## fuel capture
[35 empty] | 432012 | [19 empty] | 0
I.H.S SITE ID | SITE NAME | SBC | NAME OF TECHNICIAN | REGION | REGION MANAGER | QUALITY AUDITOR | SECURITY (YES/NO) | INDOOR / OUTDOOR | POWER TOPOLOGY | CURRENT TOPOLOGY | REASONS OF POWER TOPOLOGY CHANGE | SITE TYPE | ORDER NUMBERS | CURRENT VISIT DATE | PREVIOUS VISIT DATE | TYPE OF VISIT | DG SERIAL NUMBER | DG BRAND | AC / DC | DG KVA | DG REPLACEMENT DATE | PREVIOUS DG RUN HOURS | CURRENT DG RUN HOURS | RUNING HOURS | MAX RH | RH TEST | Last servicing | CURRENT SERVICING | NEXT SERVICE PLANED | DG serviced Hour | PREVIOUS DIESEL LEVEL | DG DIMENSION | FUEL FOUND IN CM | FUEL FOUND | FUEL ADDED | FUEL LEFT ON SITE | FUEL CONSUMED | CPH | Manufacturer CPH | CPH Test | ZESCO METER S/NO | PHASE TYPE | CURRENT GRID METER READING | PREVIOUS GRID METER READING | GRID CONSUMPTION (kWh) | N-PH1 VOLTAGE | N-PH2 VOLTAGE | N-PH3 VOLTAGE | LOAD 1 (A) | LOAD 2 (A) | LOAD 3 (A) | DC LOAD (A) | COMMENT | SUPPLIER |  | NOC CAPTURED
IHS_CBT_222A | CHAMBOLI | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-09-28 |  |  | Gen Logic |  | 30 |  | 81 | 163 | 82 | 240 | OK |  |  |  |  | 382 |  |  | 10 | 300 | 310 | 372 | 4.5366 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_075M | Ndeke Changachanga | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-02 |  |  | Gen Logic |  | 20 |  | 3528 | 3596 | 68 | 144 | OK |  |  |  |  | 380 |  |  | 29 | 300 | 329 | 351 | 5.1618 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_244A | NDEKE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-03 |  |  | Earth technology |  | 15 |  | 3758 | 3832 | 74 | 120 | OK |  |  |  |  | 266 |  |  | 5 | 300 | 305 | 261 | 3.527 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_108M | Chachacha | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-04 |  |  | perkins |  | 20 |  | 1448 | 1512 | 64 | 96 | OK |  |  |  |  | 347 |  |  | 72 | 300 | 372 | 275 | 4.2969 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_105M | Buntungwa | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-06 |  |  | Gen Logic |  | 16 |  | 5724 | 5750 | 26 | 48 | OK |  |  |  |  | 110 |  |  | 5 | 300 | 305 | 105 | 4.0385 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_243A | GEDDIS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-06 |  |  | Gen Logic |  | 15 |  | 17759 | 17776 | 17 | 48 | OK |  |  |  |  | 111 |  |  | 45 | 200 | 245 | 66 | 3.8824 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_074M | Luangwa | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-06 |  |  | Gen Logic |  | 16 |  | 4397 | 4423 | 26 | 48 | OK |  |  |  |  | 110 |  |  | 16 | 100 | 116 | 94 | 3.6154 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_305A | LUANGWA KAFUE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-06 |  |  | Yanmar |  | 16 |  | 778 | 827 | 49 | 48 | inconsitent RH |  |  |  |  | 204 |  |  | 23 | 200 | 223 | 181 | 3.6939 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_228A | MINDOLO | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-06 |  |  | Earth technology |  | 20 |  | 11014 | 11039 | 25 | 48 | OK |  |  |  |  | 120 |  |  | 37 | 300 | 337 | 83 | 3.32 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_356A | New Ndeke Village | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-06 |  |  | CK Works |  | 20 |  | 802 | 866 | 64 | 48 | inconsitent RH |  |  |  |  | 396 |  |  | 56 | 300 | 356 | 340 | 5.3125 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_083M | Nkana East | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-06 |  |  | Gen Logic |  | 16 |  | 3773 | 3785 | 12 | 48 | OK |  |  |  |  | 60 |  |  | 10 | 300 | 310 | 50 | 4.1667 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_237A | NKANA WEST | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-06 |  |  | Earth technology |  | 20 |  | 11620 | 11654 | 34 | 48 | OK |  |  |  |  | 145 |  |  | 10 | 25 | 35 | 135 | 3.9706 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_297A | KITWE POLICE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-07 |  |  | Gen Logic |  | 16 |  | 7521 | 7538 | 17 | 24 | OK |  |  |  |  | 55 |  |  | 5 | 200 | 205 | 50 | 2.9412 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_084M | Kitwe ZNS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-07 |  |  | CDP |  | 15 |  | 18110 | 18136 | 26 | 24 | inconsitent RH |  |  |  |  | 55 |  |  | 0 | 300 | 300 | 55 | 2.1154 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_334A | Miseshi Village | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-07 |  |  | Generator City |  | 16 |  | 3190 | 3206 | 16 | 24 | OK |  |  |  |  | 75 |  |  | 0 | 300 | 300 | 75 | 4.6875 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_079M | Ndeke | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-07 |  |  | CK Works |  | 20 |  | 9866 | 9875 | 9 | 24 | OK |  |  |  |  | 60 |  |  | 10 | 25 | 35 | 50 | 5.5556 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_274A | ZNS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-07 |  |  | Gen Logic |  | 16 |  | 13135 | 13154 | 19 | 24 | OK |  |  |  |  | 60 |  |  | 5 | 300 | 305 | 55 | 2.8947 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_079M | Ndeke | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-08 |  |  | CK Works |  | 20 |  | 9875 | 9880 | 5 | 0 | inconsitent RH |  |  |  |  | 35 |  |  | 5 | 300 | 305 | 30 | 6 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_237A | NKANA WEST | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-08 |  |  | Earth technology |  | 20 |  | 11654 | 11657 | 3 | 0 | inconsitent RH |  |  |  |  | 35 |  |  | 23 | 300 | 323 | 12 | 4 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_235M | KAWAMA KCC (Chimwemwe rlf | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 1925-10-07 |  |  | CK Works |  | 20 |  | 9412 | 0 | -9412 | 876624 | OK |  |  |  |  | 191 |  |  | 41 | 300 | 341 | 150 | -0.015937 | 2.5 | [5 empty] | 0 | [7 empty] | faulty controller | MERU |  | CAPTURED
IHS_CBT_120M | Garneton | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-09-24 |  |  | Gen Logic |  | 16 |  | 12626 | 12747 | 121 | 336 | OK |  |  |  |  | 345 |  |  | 41 | 200 | 241 | 304 | 2.5124 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_111M | Chimwemwe Nakadoli | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-03 |  |  | GNM |  | 15 |  | 9478 | 9533 | 55 | 120 | OK |  |  |  |  | 146 |  |  | 10 | 200 | 210 | 136 | 2.4727 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_121M | Ichipe | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-03 |  |  | IHS_CBT_121M |  | 15 |  | 14116 | 14162 | 46 | 120 | OK |  |  |  |  | 241 |  |  | 47 | 300 | 347 | 194 | 4.2174 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_242A | PARKLANDS | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-04 |  |  | Gen Logic |  | 20 |  | 9577 | 9648 | 71 | 96 | OK |  |  |  |  | 235 |  |  | 15 | 50 | 65 | 220 | 3.0986 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_089M | Valley View | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-05 |  |  | ASCOT |  | 30 |  | 2840 | 2878 | 38 | 72 | OK |  |  |  |  | 212 |  |  | 22 | 50 | 72 | 190 | 5 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_093M | Kwacha East | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-06 |  |  | Gen Logic |  | 30 |  | 125 | 142 | 17 | 48 | OK |  |  |  |  | 138 |  |  | 38 | 250 | 288 | 100 | 5.8824 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_285A | KWACHA | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-06 |  |  | CK Works |  | 20 |  | 5240 | 5265 | 25 | 48 | OK |  |  |  |  | 125 |  |  | 25 | 20 | 45 | 100 | 4 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_229A | CHIMWEMWE | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-06 |  |  | Gen Logic |  | 20 |  | 257 | 280 | 23 | 48 | OK |  |  |  |  | 188 |  |  | 38 | 400 | 438 | 150 | 6.5217 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_113M | Green Belt | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-06 |  |  | IMG |  | 20 |  | 10490 | 10516 | 26 | 48 | OK |  |  |  |  | 202 |  |  | 62 | 300 | 362 | 140 | 5.3846 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_296A | KAMUNGA | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-06 |  |  | Gen Logic |  | 16 |  | 6021 | 6045 | 24 | 48 | OK |  |  |  |  | 100 |  |  | 5 | 300 | 305 | 95 | 3.9583 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_353A | Court Barrifs | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-08 |  |  | CK Works |  | 20 |  | 10455 | 10479 | 24 | 0 | inconsitent RH |  |  |  |  | 110 |  |  | 23 | 50 | 73 | 87 | 3.625 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_285A | KWACHA | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-08 |  |  | CK Works |  | 20 |  | 5265 | 5267 | 2 | 0 | inconsitent RH |  |  |  |  | 45 |  |  | 38 | 150 | 188 | 7 | 3.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_269A | SOSOLISO | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-08 |  |  | Jiuan |  | 15 |  | 5422 | 5496 | 74 | 0 | inconsitent RH |  |  |  |  | 238 |  |  | 27 | 28 | 55 | 211 | 2.8514 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_114M | Kamatipa North | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-04 |  |  | perkins |  | 15 |  | 907 | 929 | 22 | 96 | OK |  |  |  |  | 110 |  |  | 10 | 300 | 310 | 100 | 4.5455 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_241A | BULANGILILO | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-06 |  |  | perkins |  | 20 |  | 3139 | 3153 | 14 | 48 | OK |  |  |  |  | 70 |  |  | 20 | 20 | 40 | 50 | 3.5714 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_269A | SOSOLISO | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-08 |  |  | Jiuan |  | 15 |  | 5496 | 5515 | 19 | 0 | inconsitent RH |  |  |  |  | 55 |  |  | 5 | 200 | 205 | 50 | 2.6316 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_090M | Jambo Drive | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-07 |  |  | Gen Logic |  | 16 |  | 8498 | 8506 | 8 | 24 | OK |  |  |  |  | 75 |  |  | 35 | 300 | 335 | 40 | 5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_266A | KAWAMA Copperbelt | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-06 |  |  | Gen Logic |  | 16 |  | 14493 | 14535 | 42 | 48 | OK |  |  |  |  | 170 |  |  | 57 | 200 | 257 | 113 | 2.6905 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_080M | Kalambo | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-06 |  |  | Gen Logic |  | 16 |  | 6540 | 6561 | 21 | 48 | OK |  |  |  |  | 141 |  |  | 41 | 300 | 341 | 100 | 4.7619 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_103M | Kwacha central | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-08 |  |  | Gen Logic |  | 16 |  | 672 | 692 | 20 | 0 | inconsitent RH |  |  |  |  | 120 |  |  | 27 | 20 | 47 | 93 | 4.65 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_112M | Kamtipa | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-04 |  |  | Gen Logic |  | 16 |  | 399 | 430 | 31 | 96 | OK |  |  |  |  | 130 |  |  | 5 | 300 | 305 | 125 | 4.0323 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_354A | Mufuchani | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Gen Only |  |  | Green Field |  | 2025-10-08 | 2025-10-05 |  |  | CK Works |  | 20 |  | 12979 | 13012 | 33 | 72 | OK |  |  |  |  | 129 |  |  | 13 | 200 | 213 | 116 | 3.5152 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_107M | Mindolo South | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-05 |  |  | perkins |  | 20 |  | 9373 | 9417 | 44 | 72 | OK |  |  |  |  | 210 |  |  | 10 | 300 | 310 | 200 | 4.5455 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_263A | NAKADOLI | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-06 |  |  | Gen Logic |  | 16 |  | 6747 | 6773 | 26 | 48 | OK |  |  |  |  | 105 |  |  | 26 | 200 | 226 | 79 | 3.0385 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_351A | Riverside Congo Way | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-07 |  |  | CK Works |  | 20 |  | 5821 | 5830 | 9 | 24 | OK |  |  |  |  | 84 |  |  | 34 | 300 | 334 | 50 | 5.5556 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_116M | Twatacha | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-09-29 |  |  | Gen Logic |  | 16 |  | 347 | 458 | 111 | 216 | OK |  |  |  |  | 464 |  |  | 75 | 200 | 275 | 389 | 3.5045 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_217M | KITWE MAIN SCHOOL | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-05 |  |  | Generator City |  | 16 |  | 15834 | 15868 | 34 | 72 | OK |  |  |  |  | 166 |  |  | 36 | 20 | 56 | 130 | 3.8235 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_015M | Yengwe | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-09-22 |  |  | CK Works |  | 20 |  | 5632 | 5705 | 73 | 384 | OK |  |  |  |  | 300 |  |  | 6 | 200 | 206 | 294 | 4.0274 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_037M | Minsundu | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-05 |  |  | GL Yanmar |  | 16 |  | FAULTY | FAULTY | #VALUE! | 72 | #VALUE! |  |  |  |  | 165 |  |  | 10 | 200 | 210 | 155 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | MERU |  | CAPTURED
IHS_CBT_361A | Mitengo TDRC | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-05 |  |  | CK Works |  | 20 |  | 5354 | 5404 | 50 | 72 | OK |  |  |  |  | 276 |  |  | 51 | 200 | 251 | 225 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_344A | Nkwazi 3G | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-05 |  |  | CK Works |  | 20 |  | 45723 | 45771 | 48 | 72 | OK |  |  |  |  | 210 |  |  | 10 | 200 | 210 | 200 | 4.1667 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_025M | Pamozi Extension | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-05 |  |  | GL Yanmar |  | 16 |  | 3114 | 3168 | 54 | 72 | OK |  |  |  |  | 242 |  |  | 80 | 200 | 280 | 162 | 3 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_023M | Twapia | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-05 |  |  | Gen Logic |  | 15 |  | 7494 | 7541 | 47 | 72 | OK |  |  |  |  | 310 |  |  | 160 | 200 | 360 | 150 | 3.1915 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_222M | TWAPIA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-05 |  |  | Generator City |  | 13 |  | 818 | 876 | 58 | 72 | OK |  |  |  |  | 210 |  |  | 22 | 200 | 222 | 188 | 3.2414 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_252A | CHIFUBU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-06 |  |  | Gen Logic |  | 30 |  | 4005 | 4027 | 22 | 48 | OK |  |  |  |  | 176 |  |  | 77 | 200 | 277 | 99 | 4.5 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_364A | Chifubu Sec. School | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-06 |  |  | CK Works |  | 20 |  | 753 | 774 | 21 | 48 | OK |  |  |  |  | 300 |  |  | 152 | 200 | 352 | 148 | 7.0476 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_291A | MWATAYANVWA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-06 |  |  | Gen Logic |  | 20 |  | 4286 | 4308 | 22 | 48 | OK |  |  |  |  | 150 |  |  | 51 | 80 | 131 | 99 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_264A | NDOLA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-06 |  |  | Gen Logic |  | 16 |  | 5888 | 5916 | 28 | 48 | OK |  |  |  |  | 248 |  |  | 122 | 200 | 322 | 126 | 4.5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_245A | NORTHRISE | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-06 |  |  | Lamasat |  | 20 |  | 8507 | 8529 | 22 | 48 | OK |  |  |  |  | 151 |  |  | 52 | 50 | 102 | 99 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_017M | Overspill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-06 |  |  | Falcon |  | 20 |  | 8491 | 8530 | 39 | 48 | OK |  |  |  |  | 197 |  |  | 60 | 50 | 110 | 137 | 3.5128 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_218A | PAMODZI | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-06 |  |  | Gen Logic |  | 20 |  | 13637 | 13664 | 27 | 48 | OK |  |  |  |  | 148 |  |  | 81 | 200 | 281 | 67 | 2.4815 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_226M | CHIFUBU WEST | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-07 |  |  | Generator City |  | 13 |  | 18936 | 18953 | 17 | 24 | OK |  |  |  |  | 75 |  |  | 30 | 200 | 230 | 45 | 2.6471 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_233A | CHIPULUKUSU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-07 |  |  | Earth Technology |  | 15 |  | 4788 | 4813 | 25 | 24 | inconsitent RH |  |  |  |  | 173 |  |  | 60 | 200 | 260 | 113 | 4.52 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-07 |  |  | GL Yanmar |  | 20 |  | 184 | 190 | 6 | 24 | OK |  |  |  |  | 40 |  |  | 10 | 200 | 210 | 30 | 5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_018M | Nkwanzi | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-07 |  |  | CK Works |  | 20 |  | 1255 | 1266 | 11 | 24 | OK |  |  |  |  | 158 |  |  | 108 | 50 | 158 | 50 | 4.5455 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_013M | Dola Hill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-07 |  |  | Himoinsa |  | 30 |  | 5630 | 5655 | 25 | 24 | inconsitent RH |  |  |  |  | 272 |  |  | 147 | 300 | 447 | 125 | 5 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_219M | PETAUKE CRESCENT | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-07 |  |  | CK Works |  | 20 |  | 3739 | 3763 | 24 | 24 | OK |  |  |  |  | 155 |  |  | 39 | 50 | 89 | 116 | 4.8333 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_017M | Overspill | GNM | KAMBOLE | [10 empty] | 2025-10-08 | 2025-10-08 |  |  | Falcon |  | 20 |  | 8530 | 8531 | 1 | 0 | inconsitent RH |  |  |  |  | 110 |  |  | 106 | 200 | 306 | 4 | 4 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_219M | PETAUKE CRESCENT | GNM | KAMBOLE | [10 empty] | 2025-10-08 | 2025-10-08 |  |  | CK Works |  | 20 |  | 3763 | 3769 | 6 | 0 | inconsitent RH |  |  |  |  | 89 |  |  | 60 | 200 | 260 | 29 | 4.8333 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_245A | NORTHRISE | GNM | KAMBOLE | [10 empty] | 2025-10-08 | 2025-10-08 |  |  | Lamasat |  | 20 |  | 8529 | 8539 | 10 | 0 | inconsitent RH |  |  |  |  | 102 |  |  | 57 | 200 | 257 | 45 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_344A | Nkwazi 3G | GNM | KAMBOLE | [10 empty] | 2025-10-08 | 2025-10-08 |  |  | CK Works |  | 20 |  | 45771 | 45791 | 20 | 0 | inconsitent RH |  |  |  |  | 210 |  |  | 120 | 100 | 220 | 90 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_257A | TWAPIA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-07 |  |  | CK Works |  | 20 |  | 12558 | 12568 | 10 | 24 | OK |  |  |  |  | 91 |  |  | 46 | 200 | 246 | 45 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_029M | Zafico | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-05 |  |  | Green Power |  | 15 |  | 3129 | 3228 | 99 | 72 | inconsitent RH |  |  |  |  | 386 |  |  | 49 | 200 | 249 | 337 | 3.404 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_005M | Premium Plaza | CCS | KAMBOLE | [10 empty] | 2025-10-08 | 2025-10-02 |  |  | N/A |  | N/A |  | 8548 | 8581 | 33 | 144 | OK |  |  |  |  | 151 |  |  | 38 | 20 | 58 | 113 | 3.4242 | N/A | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_306A | TUG-ARGAN | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-02 |  |  | Yanmar |  | 16 |  | 12960 | 13033 | 73 | 144 | OK |  |  |  |  | 317 |  |  | 110 | 100 | 210 | 207 | 2.8356 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_014M | Lubuto | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-05 |  |  | CK Works |  | 20 |  | 3640 | 3703 | 63 | 72 | OK |  |  |  |  | 310 |  |  | 20 | 400 | 420 | 290 | 4.6032 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_021M | Sky ways | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-05 |  |  | CK Works |  | 20 |  | 7344 | 7378 | 34 | 72 | OK |  |  |  |  | 130 |  |  | 5 | 90 | 95 | 125 | 3.6765 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_085M | Dangote | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-05 |  |  | Earth technology |  | 13 |  | 7935 | 7971 | 36 | 72 | OK |  |  |  |  | 223 |  |  | 90 | 200 | 290 | 133 | 3.6944 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_010M | Kabushi | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-06 |  |  | IMG |  | 15 |  | 7502 | 7520 | 18 | 48 | OK |  |  |  |  | 130 |  |  | 63 | 300 | 363 | 67 | 3.7222 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_035M | Kaloko | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-07 |  |  | Himoinsa |  | 30 |  | 9382 | 9408 | 26 | 24 | inconsitent RH |  |  |  |  | 139 |  |  | 29 | 300 | 329 | 110 | 4.2308 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_027M | Kantolomba | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-07 |  |  | CK Works |  | 20 |  | 5438 | 5452 | 14 | 24 | OK |  |  |  |  | 135 |  |  | 56 | 300 | 356 | 79 | 5.6429 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_022M | Kasembo | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-07 |  |  | Gen Logic |  | 20 |  | 6220 | 6237 | 17 | 24 | OK |  |  |  |  | 168 |  |  | 86 | 300 | 386 | 82 | 4.8235 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_006M | Lubuto Central | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-07 |  |  | Lamasat |  | 15 |  | 940 | 956 | 16 | 24 | OK |  |  |  |  | 106 |  |  | 30 | 300 | 330 | 76 | 4.75 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_024M | Ndeke Township | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-08 |  |  | CK Works |  | 30 |  | 11478 | 11493 | 15 | 0 | inconsitent RH |  |  |  |  | 108 |  |  | 43 | 60 | 103 | 65 | 4.3333 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_021M | Sky ways | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-08 |  |  | CK Works |  | 20 |  | 7378 | 7391 | 13 | 0 | inconsitent RH |  |  |  |  | 95 |  |  | 30 | 300 | 330 | 65 | 5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_033M | Bwana Mukubwa | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-15 |  |  | GL Yanmar |  | 16 |  | 811 | 880 | 69 | -168 | inconsitent RH |  |  |  |  | 278 |  |  | 11 | 50 | 61 | 267 | 3.8696 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_336A | Fatima Girls | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-06 |  |  | perkins |  | 15 |  | 11222 | 11248 | 26 | 48 | OK |  |  |  |  | 170 |  |  | 64 | 300 | 364 | 106 | 4.0769 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_234A | CHIWALA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-05 |  |  | Gen Logic |  | 20 |  | 21764 | 21792 | 28 | 72 | OK |  |  |  |  | 220 |  |  | 99 | 200 | 299 | 121 | 4.3214 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_253A | ITAWA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-01 |  |  | Gen Logic |  | 20 |  | 10552 | 10650 | 98 | 168 | OK |  |  |  |  | 376 |  |  | 5 | 300 | 305 | 371 | 3.7857 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_024M | Ndeke Township | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-08 |  |  | CK Works |  | 30 |  | 11493 | 11500 | 7 | 0 | inconsitent RH |  |  |  |  | 103 |  |  | 69 | 400 | 469 | 34 | 4.8571 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_016M | Itawa | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-05 |  |  | Vitalgen |  | 30 |  | 4584 | 4623 | 39 | 72 | OK |  |  |  |  | 294 |  |  | 75 | 300 | 375 | 219 | 5.6154 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_349A | Kafubu Mall | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-06 |  |  | Gen Logic |  | 16 |  | 16180 | 16200 | 20 | 48 | OK |  |  |  |  | 105 |  |  | 49 | 300 | 349 | 56 | 2.8 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_091M | Kalalangabo | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-05 |  |  | GL Yanmar |  | 16 |  | 5760 | 5850 | 90 | 72 | inconsitent RH |  |  |  |  | 461 |  |  | 129 | 300 | 429 | 332 | 3.6889 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_232A | LUBUTO | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-09-29 |  |  | Gen Logic |  | 20 |  | 10924 | 11011 | 87 | 216 | OK |  |  |  |  | 382 |  |  | 34 | 300 | 334 | 348 | 4 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_012M | Itawa West | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-05 |  |  | Lamasat |  | 20 |  | 11366 | 11417 | 51 | 72 | OK |  |  |  |  | 277 |  |  | 134 | 200 | 334 | 143 | 2.8039 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_236A | KALALANGABO | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-05 |  |  | ASCOT |  | 30 |  | 26 | 91 | 65 | 72 | OK |  |  |  |  | 363 |  |  | 55 | 200 | 255 | 308 | 4.7385 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_008M | Masala | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-05 |  |  | Generator City |  | 13 |  | 6333 | 6374 | 41 | 72 | OK |  |  |  |  | 268 |  |  | 104 | 300 | 404 | 164 | 4 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_056M | Masangano | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-05 |  |  | GL Yanmar |  | 16 |  | 23061 | 23080 | 19 | 72 | OK |  |  |  |  | 179 |  |  | 85 | 300 | 385 | 94 | 4.9474 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_293A | MUSAKASONKA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-09-29 |  |  | Gen Logic |  | 20 |  | 1220 | 1304 | 84 | 216 | OK |  |  |  |  | 373 |  |  | 70 | 300 | 370 | 303 | 3.6071 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_020M | Mushili | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-02 |  |  | CK Works |  | 30 |  | 8374 | 8433 | 59 | 144 | OK |  |  |  |  | 331 |  |  | 53 | 300 | 353 | 278 | 4.7119 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_235A | KAFULAFUTA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-09-21 |  |  | Lamasat |  | 20 |  | 7380 | 7391 | 11 | 408 | OK |  |  |  |  | 130 |  |  | 80 | 100 | 180 | 50 | 4.5455 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_288A | NDOLA BUS STATION | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-01 |  |  | CK Works |  | 20 |  | 200 | 286 | 86 | 168 | OK |  |  |  |  | 399 |  |  | 5 | 300 | 305 | 394 | 4.5814 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_346A | Nilkant Mine | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Solar-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-05 |  |  | CK Works |  | 20 |  | 11344 | 11423 | 79 | 72 | inconsitent RH |  |  |  |  | 371 |  |  | 79 | 200 | 279 | 292 | 3.6962 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_040M | Seed Of Hope | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-05 |  |  | Lamasat |  | 15 |  | 25014 | 25085 | 71 | 72 | OK |  |  |  |  | 248 |  |  | 10 | 300 | 310 | 238 | 3.3521 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_003M | Swimming Pool | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-05 |  |  | CK Works |  | 30 |  | 7130 | 7147 | 17 | 72 | OK |  |  |  |  | 223 |  |  | 143 | 300 | 443 | 80 | 4.7059 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_312A | FISENGE | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-09-22 |  |  | Yanmar |  | 16 |  | 7247 | 7377 | 130 | 384 | OK |  |  |  |  | 444 |  |  | 20 | 200 | 220 | 424 | 3.2615 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_048M | Kamirenda Extension | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-09-29 |  |  | Vitalgen |  | 20 |  | 9570 | 9667 | 97 | 216 | OK |  |  |  |  | 355 |  |  | 10 | 250 | 260 | 345 | 3.5567 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_064M | Finsansa Basic | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-03 |  |  | Yanmar |  | 16 |  | 7816 | 7847 | 31 | 120 | OK |  |  |  |  | 311 |  |  | 205 | 150 | 355 | 106 | 3.4194 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_343A | Chinese Colony | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-03 |  |  | Gen Logic |  | 20 |  | FAULTY | FAULTY | #VALUE! | 120 | #VALUE! |  |  |  |  | 276 |  |  | 150 | 200 | 350 | 126 | #VALUE! | 2.5 | [5 empty] | 0 | [7 empty] | faulty controller | MERU |  | CAPTURED
IHS_CBT_277A | ROAN | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-03 |  |  | Gen Logic |  | 16 |  | FAULTY | FAULTY | #VALUE! | 120 | #VALUE! |  |  |  |  | 250 |  |  | 162 | 150 | 312 | 88 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | MERU |  | CAPTURED
IHS_CBT_052M | Luanshya New Town | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-03 |  |  | Gen Logic |  | 16 |  | 15021 | 15071 | 50 | 120 | OK |  |  |  |  | 283 |  |  | 113 | 200 | 313 | 170 | 3.4 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_062M | Roan Township | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-03 |  |  | CK Works |  | 20 |  | 8221 | 8251 | 30 | 120 | OK |  |  |  |  | 316 |  |  | 205 | 150 | 355 | 111 | 3.7 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_058M | Mikomfwa | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-03 |  |  | Gen Logic |  | 16 |  | 7675 | 7774 | 99 | 120 | OK |  |  |  |  | 305 |  |  | 10 | 200 | 210 | 295 | 2.9798 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_049M | Mikomfwa East | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-04 |  |  | Gen Logic |  | 16 |  | 6468 | 6532 | 64 | 96 | OK |  |  |  |  | 394 |  |  | 138 | 150 | 288 | 256 | 4 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_054M | Mikomfwa Market | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-04 |  |  | Yanmar |  | 16 |  | 12356 | 12409 | 53 | 96 | OK |  |  |  |  | 322 |  |  | 115 | 150 | 265 | 207 | 3.9057 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_230A | MIKOMFWA | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-05 |  |  | Earth technology |  | 15 |  | 878 | 906 | 28 | 72 | OK |  |  |  |  | 238 |  |  | 137 | 150 | 287 | 101 | 3.6071 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_146M | Miku Mining | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-01 |  |  | Gen Logic |  | 20 |  | 20245 | 20414 | 169 | 168 | inconsitent RH |  |  |  |  | 444 |  |  | 16 | 300 | 316 | 428 | 2.5325 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_126M | Chibuluma | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-07 |  |  | Gen Logic |  | 20 |  | 3721 | 3743 | 22 | 24 | OK |  |  |  |  | 107 |  |  | 22 | 250 | 272 | 85 | 3.8636 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_301A | CHIBULUMA TOWN | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-07 |  |  | Gen Logic |  | 16 |  | 9513 | 9533 | 20 | 24 | OK |  |  |  |  | 91 |  |  | 15 | 300 | 315 | 76 | 3.8 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_088M | Geddis | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-08 |  |  | CDP |  | 13 |  | 11793 | 11825 | 32 | 0 | inconsitent RH |  |  |  |  | 105 |  |  | 25 | 20 | 45 | 80 | 2.5 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_094M | Kitwe Primary | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-05 |  |  | Gen Logic |  | 16 |  | 2471 | 2491 | 20 | 72 | OK |  |  |  |  | 115 |  |  | 39 | 30 | 69 | 76 | 3.8 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_342A | Kantanta Street | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-08 | 2025-10-05 |  |  | Gen Logic |  | 20 |  | 3758 | 3771 | 13 | 72 | OK |  |  |  |  | 60 |  |  | 15 | 30 | 45 | 45 | 3.4615 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_133M | Chibuluma Golf Club | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-05 |  |  | Powerol |  | 13 |  | 5109 | 5148 | 39 | 96 | OK |  |  |  |  | 142 |  |  | 0 | 300 | 300 | 142 | 3.641 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_261A | CHATI | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Solar-Gen |  |  | Green Field |  | 2025-10-09 | 1924-09-19 |  |  | perkins |  | 16 |  | 14926 | 14992 | 66 | 885840 | OK |  |  |  |  | 241 |  |  | 0 | 300 | 300 | 241 | 3.6515 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_300A | LUBAMBE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-05 |  |  | Jiuan |  | 30 |  | 5071 | 5105 | 34 | 96 | OK |  |  |  |  | 167 |  |  | 24 | 200 | 224 | 143 | 4.2059 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_074M | Luangwa | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-08 |  |  | Gen Logic |  | 16 |  | 4423 | 4433 | 10 | 24 | OK |  |  |  |  | 116 |  |  | 78 | 200 | 278 | 38 | 3.8 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_353A | Court Barrifs | GNM | FACKSON | [10 empty] | 2025-10-09 | 2025-10-08 |  |  | CK Works |  | 20 |  | 10479 | 10493 | 14 | 24 | OK |  |  |  |  | 73 |  |  | 20 | 200 | 220 | 53 | 3.7857 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_088M | Geddis | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-08 |  |  | CDP |  | 13 |  | 11825 | 11835 | 10 | 24 | OK |  |  |  |  | 45 |  |  | 15 | 100 | 115 | 30 | 3 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_342A | Kantanta Street | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-08 |  |  | Gen Logic |  | 20 |  | 3771 | 3779 | 8 | 24 | OK |  |  |  |  | 45 |  |  | 15 | 200 | 215 | 30 | 3.75 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_094M | Kitwe Primary | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-08 |  |  | Gen Logic |  | 16 |  | 2491 | 2500 | 9 | 24 | OK |  |  |  |  | 69 |  |  | 35 | 200 | 235 | 34 | 3.7778 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_242A | PARKLANDS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-08 |  |  | Gen Logic |  | 20 |  | 9648 | 9660 | 12 | 24 | OK |  |  |  |  | 65 |  |  | 20 | 200 | 220 | 45 | 3.75 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_073M | Cedrics Farm | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-05 |  |  | perkins |  | 15 |  | 16976 | 17083 | 107 | 96 | inconsitent RH |  |  |  |  | 310 |  |  | 10 | 200 | 210 | 300 | 2.8037 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_368A | #N/A | #N/A | FACKSON | #N/A | #N/A | #N/A |  | #N/A | #N/A |  |  | #N/A |  | 2025-10-09 | 2025-10-03 |  |  | #N/A |  | #N/A |  | 9804 | 9893 | 89 | 144 | OK |  |  |  |  | 278 |  |  | 5 | 100 | 105 | 273 | 3.0674 | #N/A | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_102M | Richmond | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-05 |  |  | Gen Logic |  | 16 |  | 2770 | 2832 | 62 | 96 | OK |  |  |  |  | 236 |  |  | 5 | 200 | 205 | 231 | 3.7258 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_218M | WUSAKILE POLICE CAMP | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-09-29 |  |  | Generator City |  | 16 |  | 7312 | 7409 | 97 | 240 | OK |  |  |  |  | 336 |  |  | 17 | 100 | 117 | 319 | 3.2887 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_089M | Valley View | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-08 |  |  | ASCOT |  | 30 |  | 2878 | 2887 | 9 | 24 | OK |  |  |  |  | 72 |  |  | 22 | 400 | 422 | 50 | 5.5556 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_241A | BULANGILILO | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-08 |  |  | perkins |  | 20 |  | 3153 | 3162 | 9 | 24 | OK |  |  |  |  | 40 |  |  | 10 | 150 | 160 | 30 | 3.3333 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_103M | Kwacha central | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-08 |  |  | Gen Logic |  | 16 |  | 692 | 696 | 4 | 24 | OK |  |  |  |  | 47 |  |  | 30 | 150 | 180 | 17 | 4.25 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_285A | KWACHA | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-08 |  |  | CK Works |  | 20 |  | 5267 | 5285 | 18 | 24 | OK |  |  |  |  | 188 |  |  | 123 | 150 | 273 | 65 | 3.6111 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_217M | KITWE MAIN SCHOOL | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-08 |  |  | Generator City |  | 16 |  | 15868 | 15883 | 15 | 24 | OK |  |  |  |  | 56 |  |  | 5 | 100 | 105 | 51 | 3.4 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_103M | Kwacha central | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-09 |  |  | Gen Logic |  | 16 |  | 692 | 711 | 19 | 0 | inconsitent RH |  |  |  |  | 180 |  |  | 110 | 150 | 260 | 70 | 3.6842 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_276A | KAKOLO I & II | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Solar-Gen |  |  | Green Field |  | 2025-10-09 | 2025-09-27 |  |  | Jiuan |  | 15 |  | 24047 | 24117 | 70 | 288 | OK |  |  |  |  | 217 |  |  | 14 | 150 | 164 | 203 | 2.9 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_123M | Mukuba University | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-04 |  |  | IMG |  | 15 |  | 11620 | 11639 | 19 | 120 | OK |  |  |  |  | 207 |  |  | 142 | 150 | 292 | 65 | 3.4211 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_115M | Mindolo | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-05 |  |  | Gen Logic |  | 16 |  | 7299 | 7384 | 85 | 96 | OK |  |  |  |  | 324 |  |  | 69 | 100 | 169 | 255 | 3 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_216M | COOL BANANAS | GNM | KAMBOLE | [10 empty] | 2025-10-09 | 2025-10-06 |  |  | Generator City |  | 13 |  | FAULTY | FAULTY | #VALUE! | 72 | #VALUE! |  |  |  |  | 205 |  |  | 26 | 200 | 226 | 179 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | MERU |  | CAPTURED
IHS_CBT_018M | Nkwanzi | GNM | KAMBOLE | [10 empty] | 2025-10-09 | 2025-10-08 |  |  | CK Works |  | 20 |  | 1266 | 1277 | 11 | 24 | OK |  |  |  |  | 158 |  |  | 108 | 200 | 308 | 50 | 4.5455 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_291A | MWATAYANVWA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-08 |  |  | Gen Logic |  | 20 |  | 4308 | 4324 | 16 | 24 | OK |  |  |  |  | 131 |  |  | 59 | 200 | 259 | 72 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_005M | Premium Plaza | CCS | KAMBOLE | [10 empty] | 2025-10-09 | 2025-10-08 |  |  | N/A |  | N/A |  | 8581 | 8583 | 2 | 24 | OK |  |  |  |  | 58 |  |  | 51 | 100 | 151 | 7 | 3.5 | N/A | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_335A | Daag Hamershold | GNM | KAMBOLE | [10 empty] | 2025-10-09 | 2025-09-29 |  |  | LAMASAT |  | 15 |  | 7728 | 7768 | 40 | 240 | OK |  |  |  |  | 242 |  |  | 142 | 100 | 242 | 100 | 2.5 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_033M | Bwana Mukubwa | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-08 |  |  | GL Yanmar |  | 16 |  | 880 | 881 | 1 | 24 | OK |  |  |  |  | 61 |  |  | 56 | 300 | 356 | 5 | 5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_233M | Zambeef Mpongwe | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-08 |  |  | Falcon |  | 16 |  | 0 | 0 | 0 | 24 | OK |  |  |  |  | 260 |  |  | 60 | 300 | 360 | 200 | #DIV/0! | 2 | [5 empty] | 0 | [7 empty] | DG SWAP | MERU |  | CAPTURED
IHS_CBT_227M | LUANSHYA EAST | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-03 |  |  | Generator City |  | 16 |  | 7545 | 7585 | 40 | 144 | OK |  |  |  |  | 398 |  |  | 234 | 150 | 384 | 164 | 4.1 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_179M | ETC Bio Energy Farm | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-09-29 |  |  | Gen Logic |  | 15 |  | 10209 | 10311 | 102 | 240 | OK |  |  |  |  | 340 |  |  | 53 | 200 | 253 | 287 | 2.8137 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_047M | Kamirenda | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-09-29 |  |  | Gen Logic |  | 16 |  | 13096 | 13153 | 57 | 240 | OK |  |  |  |  | 187 |  |  | 10 | 200 | 210 | 177 | 3.1053 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_210A | LUANSHYA | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-05 |  |  | CK Works |  | 20 |  | 7821 | 7881 | 60 | 96 | OK |  |  |  |  | 222 |  |  | 18 | 300 | 318 | 204 | 3.4 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_050M | Luanshya Town Center | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-05 |  |  | Gen Logic |  | 20 |  | 8404 | 8445 | 41 | 96 | OK |  |  |  |  | 402 |  |  | 201 | 300 | 501 | 201 | 4.9024 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_307A | TVTC | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-05 |  |  | Gen Logic |  | 16 |  | FAULTY | FAULTY | #VALUE! | 96 | #VALUE! |  |  |  |  | 115 |  |  | 56 | 150 | 206 | 59 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | MERU |  | CAPTURED
IHS_CTR_271A | MACHIYA | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-05 |  |  | RID |  | 16 |  | 0 | 7652 | 7652 | 96 | inconsitent RH |  |  |  |  | 290 |  |  | 10 | 300 | 310 | 280 | 0.036592 | 2 | [5 empty] | 0 | [7 empty] | DG SWAP | MERU |  | CAPTURED
IHS_CBT_265A | NEW TOWN | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-03 |  |  | Gen Logic |  | 16 |  | 1691 | 1742 | 51 | 144 | OK |  |  |  |  | 309 |  |  | 5 | 100 | 105 | 304 | 5.9608 | 2 | [5 empty] | 0 | [7 empty] | Take not:that Fuel has been stolen on site about 115lits the ob number has been shared, reported at New town Police station. | MERU |  | CAPTURED
IHS_CBT_172M | ST. Anthony | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-05 |  |  | CK Works |  | 20 |  | 5482 | 5573 | 91 | 96 | OK |  |  |  |  | 273 |  |  | 38 | 200 | 238 | 235 | 2.5824 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_159M | Chembe South | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-05 |  |  | Gen Logic |  | 20 |  | FAULTY | FAULTY | #VALUE! | 96 | #VALUE! |  |  |  |  | 290 |  |  | 30 | 300 | 330 | 260 | #VALUE! | 2.5 | [5 empty] | 0 | [7 empty] | faulty controller | MERU |  | CAPTURED
IHS_CBT_132M | Kalulushi West | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-05 |  |  | Gen Logic |  | 20 |  | 5712 | 5741 | 29 | 96 | OK |  |  |  |  | 207 |  |  | 47 | 400 | 447 | 160 | 5.5172 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_117M | Chibote | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-05 |  |  | Gen Logic |  | 15 |  | 5781 | 5798 | 17 | 96 | OK |  |  |  |  | 174 |  |  | 75 | 250 | 325 | 99 | 5.8235 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_134M | Kalulushi East | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-05 |  |  | CK Works |  | 20 |  | 8233 | 8265 | 32 | 96 | OK |  |  |  |  | 143 |  |  | 5 | 400 | 405 | 138 | 4.3125 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_310A | CHEMBE CHATI | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-09-29 |  |  | Gen Logic |  | 17 |  | FAULTY | FAULTY | #VALUE! | 240 | #VALUE! |  |  |  |  | 395 |  |  | 154 | 150 | 304 | 241 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_167M | Kafubu | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-05 |  |  | LISTER PETTER |  | 16 |  | FAULTY | FAULTY | #VALUE! | 96 | #VALUE! |  |  |  |  | 315 |  |  | 28 | 300 | 328 | 287 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | MERU |  | CAPTURED
IHS_CBT_119M | Lumumba | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-05 |  |  | Gen Logic |  | 16 |  | 9540 | 9572 | 32 | 96 | OK |  |  |  |  | 104 |  |  | 24 | 250 | 274 | 80 | 2.5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_206A | KALULUSHI | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-05 |  |  | IMG |  | 15 |  | 7361 | 7390 | 29 | 96 | OK |  |  |  |  | 175 |  |  | 45 | 300 | 345 | 130 | 4.4828 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_127M | Kalulushi | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-05 |  |  | Himoinsa |  | 30 |  | 10713 | 10744 | 31 | 96 | OK |  |  |  |  | 188 |  |  | 67 | 300 | 367 | 121 | 3.9032 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_267A | KALULUSHI EAST | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-05 |  |  | Gen Logic |  | 16 |  | 13617 | 13648 | 31 | 96 | OK |  |  |  |  | 191 |  |  | 57 | 300 | 357 | 134 | 4.3226 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_118M | Kamaronde | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-05 |  |  | CK Works |  | 20 |  | 3062 | 3102 | 40 | 96 | OK |  |  |  |  | 302 |  |  | 142 | 300 | 442 | 160 | 4 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_238M | NAPSA Complex | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-05 |  |  | MPMC |  | 15 |  | 8538 | 8566 | 28 | 96 | OK |  |  |  |  | 160 |  |  | 59 | 300 | 359 | 101 | 3.6071 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_155M | St. Joseph | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-05 |  |  | Gen Logic |  | 16 |  | 6485 | 6526 | 41 | 96 | OK |  |  |  |  | 125 |  |  | 15 | 300 | 315 | 110 | 2.6829 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_087M | Lulamba School | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-09 | 2025-10-05 |  |  | perkins |  | 20 |  | 166 | 177 | 11 | 96 | OK |  |  |  |  | 69 |  |  | 24 | 150 | 174 | 45 | 4.0909 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_129M | Emerald Mine Lufwanyama | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-05 |  |  | Gen Logic |  | 15 |  | 25077 | 25252 | 175 | 120 | inconsitent RH |  |  |  |  | 555 |  |  | 50 | 300 | 350 | 505 | 2.8857 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_078M | Bupe | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-09-10 |  |  | Gen Logic |  | 16 |  | 22866 | 22987 | 121 | 720 | OK |  |  |  |  | 471 |  |  | 59 | 100 | 159 | 412 | 3.405 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_352A | Parklands TBN | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-05 |  |  | CK Works |  | 20 |  | 8193 | 8280 | 87 | 120 | OK |  |  |  |  | 349 |  |  | 114 | 100 | 214 | 235 | 2.7011 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_229A | CHIMWEMWE | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-08 |  |  | Gen Logic |  | 20 |  | 280 | 316 | 36 | 48 | OK |  |  |  |  | 438 |  |  | 209 | 300 | 509 | 229 | 6.3611 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_120M | Garneton | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-08 |  |  | Gen Logic |  | 16 |  | 12747 | 12756 | 9 | 48 | OK |  |  |  |  | 241 |  |  | 222 | 200 | 422 | 19 | 2.1111 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_111M | Chimwemwe Nakadoli | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-08 |  |  | GNM |  | 15 |  | 9533 | 9577 | 44 | 48 | OK |  |  |  |  | 210 |  |  | 100 | 150 | 250 | 110 | 2.5 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_087M | Lulamba School | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-09 |  |  | perkins |  | 20 |  | 177 | 207 | 30 | 24 | inconsitent RH |  |  |  |  | 174 |  |  | 51 | 100 | 151 | 123 | 4.1 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_235M | KAWAMA KCC (Chimwemwe rlf | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-08 |  |  | CK Works |  | 20 |  | 0 | 9471 | 9471 | 48 | inconsitent RH |  |  |  |  | 341 |  |  | 144 | 300 | 444 | 197 | 0.0208 | 2.5 | [5 empty] | 0 | [7 empty] | DG SWAP | MERU |  | CAPTURED
IHS_CBT_093M | Kwacha East | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-08 |  |  | Gen Logic |  | 30 |  | 142 | 166 | 24 | 48 | OK |  |  |  |  | 288 |  |  | 112 | 300 | 412 | 176 | 7.3333 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_351A | Riverside Congo Way | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-08 |  |  | CK Works |  | 20 |  | 5830 | 5862 | 32 | 48 | OK |  |  |  |  | 334 |  |  | 176 | 300 | 476 | 158 | 4.9375 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_241A | BULANGILILO | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-09 |  |  | perkins |  | 20 |  | 3162 | 3174 | 12 | 24 | OK |  |  |  |  | 160 |  |  | 120 | 300 | 420 | 40 | 3.3333 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_276A | KAKOLO I & II | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Solar-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-09 |  |  | Jiuan |  | 15 |  | 24117 | 24122 | 5 | 24 | OK |  |  |  |  | 164 |  |  | 150 | 200 | 350 | 14 | 2.8 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_115M | Mindolo | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-09 |  |  | Gen Logic |  | 16 |  | 7384 | 7384 | 0 | 24 | OK |  |  |  |  | 169 |  |  | 169 | 200 | 369 | 0 | #DIV/0! | 2 | [5 empty] | 0 | [7 empty] | DG DIDNT RUN | MERU |  | CAPTURED
IHS_CBT_217M | KITWE MAIN SCHOOL | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-09 |  |  | Generator City |  | 16 |  | 15883 | 15899 | 16 | 24 | OK |  |  |  |  | 105 |  |  | 48 | 300 | 348 | 57 | 3.5625 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_098M | Bulangililo | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-05 |  |  | Gen Logic |  | 16 |  | 8203 | 8210 | 7 | 120 | OK |  |  |  |  | 207 |  |  | 186 | 150 | 336 | 21 | 3 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_220A | ITIMPI | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-04 |  |  | MPI |  | 20 |  | 11320 | 11439 | 119 | 144 | OK |  |  |  |  | 379 |  |  | 51 | 300 | 351 | 328 | 2.7563 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_333A | Mindolo North | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-05 |  |  | perkins |  | 15 |  | 8907 | 8990 | 83 | 120 | OK |  |  |  |  | 380 |  |  | 139 | 200 | 339 | 241 | 2.9036 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_099M | Kitwe Town Center | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-05 |  |  | CDP |  | 15 |  | 9025 | 9096 | 71 | 120 | OK |  |  |  |  | 230 |  |  | 15 | 300 | 315 | 215 | 3.0282 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_226M | CHIFUBU WEST | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-08 |  |  | Generator City |  | 13 |  | 18953 | 18990 | 37 | 48 | OK |  |  |  |  | 230 |  |  | 133 | 200 | 333 | 97 | 2.6216 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_252A | CHIFUBU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-08 |  |  | Gen Logic |  | 30 |  | 4027 | 4062 | 35 | 48 | OK |  |  |  |  | 277 |  |  | 109 | 300 | 409 | 168 | 4.8 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-08 |  |  | GL Yanmar |  | 20 |  | 190 | 222 | 32 | 48 | OK |  |  |  |  | 210 |  |  | 50 | 200 | 250 | 160 | 5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_361A | Mitengo TDRC | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-08 |  |  | CK Works |  | 20 |  | 5404 | 5447 | 43 | 48 | OK |  |  |  |  | 251 |  |  | 56 | 200 | 256 | 195 | 4.5349 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_291A | MWATAYANVWA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-09 |  |  | Gen Logic |  | 20 |  | 4324 | 4357 | 33 | 24 | inconsitent RH |  |  |  |  | 259 |  |  | 148 | 200 | 348 | 111 | 3.3636 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_264A | NDOLA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-08 |  |  | Gen Logic |  | 16 |  | 5916 | 5947 | 31 | 48 | OK |  |  |  |  | 322 |  |  | 173 | 200 | 373 | 149 | 4.8065 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_018M | Nkwanzi | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-09 |  |  | CK Works |  | 20 |  | 1277 | 1308 | 31 | 24 | inconsitent RH |  |  |  |  | 308 |  |  | 168 | 200 | 368 | 140 | 4.5161 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_025M | Pamozi Extension | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-08 |  |  | GL Yanmar |  | 16 |  | 3168 | 3206 | 38 | 48 | OK |  |  |  |  | 280 |  |  | 166 | 200 | 366 | 114 | 3 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_219M | PETAUKE CRESCENT | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-08 |  |  | CK Works |  | 20 |  | 3769 | 3811 | 42 | 48 | OK |  |  |  |  | 260 |  |  | 58 | 200 | 258 | 202 | 4.8095 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_257A | TWAPIA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-08 |  |  | CK Works |  | 20 |  | 12568 | 12598 | 30 | 48 | OK |  |  |  |  | 246 |  |  | 111 | 200 | 311 | 135 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_344A | Nkwazi 3G | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-08 |  |  | CK Works |  | 20 |  | 45791 | 45799 | 8 | 48 | OK |  |  |  |  | 220 |  |  | 184 | 200 | 384 | 36 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_245A | NORTHRISE | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-08 |  |  | Lamasat |  | 20 |  | 8539 | 8564 | 25 | 48 | OK |  |  |  |  | 257 |  |  | 144 | 300 | 444 | 113 | 4.52 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_015M | Yengwe | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-08 |  |  | CK Works |  | 20 |  | 5705 | 5734 | 29 | 48 | OK |  |  |  |  | 206 |  |  | 70 | 300 | 370 | 136 | 4.6897 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_005M | Premium Plaza | CCS | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Roof Top |  | 2025-10-10 | 2025-10-09 |  |  | N/A |  | N/A |  | 8583 | 8588 | 5 | 24 | OK |  |  |  |  | 151 |  |  | 134 | 200 | 334 | 17 | 3.4 | N/A | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_347A | Ndola International Airport | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-05 |  |  | Vitalgen |  | 20 |  | 8849 | 8970 | 121 | 120 | inconsitent RH |  |  |  |  | 192 |  |  | 192 | 100 | 292 | 0 | 0 | 2.5 | [5 empty] | 0 | [7 empty] | DG DIDNT RUN | MERU |  | CAPTURED
IHS_CBT_002M | Hillcrest | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-09-28 |  |  | GL Yanmar |  | 20 |  | 7709 | 7800 | 91 | 288 | OK |  |  |  |  | 427 |  |  | 99 | 200 | 299 | 328 | 3.6044 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_207A | KANINI | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-09-29 |  |  | Gen Logic |  | 16 |  | 9006 | 9095 | 89 | 264 | OK |  |  |  |  | 358 |  |  | 37 | 300 | 337 | 321 | 3.6067 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_009M | Tazama Building | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Roof Top |  | 2025-10-10 | 2025-10-02 |  |  | IMG |  | 16 |  | 28793 | 28928 | 135 | 192 | OK |  |  |  |  | 377 |  |  | 41 | 300 | 341 | 336 | 2.4889 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_001M | Kanini | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-04 |  |  | IMG |  | 20 |  | 7508 | 7589 | 81 | 144 | OK |  |  |  |  | 367 |  |  | 59 | 300 | 359 | 308 | 3.8025 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_360A | Hilcrest Extension | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-05 |  |  | CK Works |  | 20 |  | 10489 | 10534 | 45 | 120 | OK |  |  |  |  | 283 |  |  | 71 | 300 | 371 | 212 | 4.7111 | 5.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_004M | Ndola T. Centre | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-07 |  |  | Falcon |  | 20 |  | 176 | 210 | 34 | 72 | OK |  |  |  |  | 177 |  |  | 20 | 300 | 320 | 157 | 4.6176 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_058M | Mikomfwa | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-08 |  |  | Gen Logic |  | 16 |  | 7774 | 7793 | 19 | 48 | OK |  |  |  |  | 210 |  |  | 145 | 100 | 245 | 65 | 3.4211 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_049M | Mikomfwa East | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-08 |  |  | Gen Logic |  | 16 |  | 6532 | 6549 | 17 | 48 | OK |  |  |  |  | 288 |  |  | 209 | 100 | 309 | 79 | 4.6471 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_054M | Mikomfwa Market | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-08 |  |  | Yanmar |  | 16 |  | 12409 | 12427 | 18 | 48 | OK |  |  |  |  | 265 |  |  | 194 | 100 | 294 | 71 | 3.9444 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_043M | Fisenge | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-05 |  |  | Gen Logic |  | 16 |  | FAULTY | FAULTY | #VALUE! | 120 | #VALUE! |  |  |  |  | 200 |  |  | 51 | 300 | 351 | 149 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | MERU |  | CAPTURED
IHS_CBT_044M | Kafubu Block | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-07 |  |  | Yanmar |  | 16 |  | 17758 | 17789 | 31 | 72 | OK |  |  |  |  | 170 |  |  | 67 | 200 | 267 | 103 | 3.3226 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_314A | KAFUBU BLOCK | GNM | Royd | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-05 |  |  | CK Works |  | 20 |  | 7458 | 7501 | 43 | 120 | OK |  |  |  |  | 253 |  |  | 94 | 200 | 294 | 159 | 3.6977 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_181M | Lukanga resettlement | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Solar-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-05 |  |  | CK Works |  | 20 |  | 5062 | 5328 | 266 | 120 | inconsitent RH |  |  |  |  | 537 |  |  | 10 | 400 | 410 | 527 | 1.9812 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_265A | NEW TOWN | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-09 |  |  | Gen Logic |  | 16 |  | 1742 | 1754 | 12 | 24 | OK |  |  |  |  | 105 |  |  | 60 | 200 | 260 | 45 | 3.75 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_161M | Mikata Mpongwe | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Solar-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-05 |  |  | IMG |  | 20 |  | 9729 | 9778 | 49 | 120 | OK |  |  |  |  | 210 |  |  | 38 | 300 | 338 | 172 | 3.5102 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_215M | PHILIP FARM | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Solar-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-05 |  |  | perkins |  | 15 |  | FAULTY | 19428 | #VALUE! | 120 | #VALUE! |  |  |  |  | 310 |  |  | 38 | 300 | 338 | 272 | #VALUE! | 1.8 | [5 empty] | 0 | [7 empty] | faulty controller | MERU |  | CAPTURED
IHS_CBT_074M | Luangwa | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-09 |  |  | Gen Logic |  | 16 |  | 4433 | 4457 | 24 | 24 | OK |  |  |  |  | 278 |  |  | 186 | 200 | 386 | 92 | 3.8333 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_305A | LUANGWA KAFUE | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-08 |  |  | Yanmar |  | 16 |  | 827 | 851 | 24 | 48 | OK |  |  |  |  | 223 |  |  | 223 | 250 | 473 | 0 | 0 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_146M | Miku Mining | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-08 |  |  | Gen Logic |  | 20 |  | 20414 | 20443 | 29 | 48 | OK |  |  |  |  | 316 |  |  | 231 | 100 | 331 | 85 | 2.931 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_088M | Geddis | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-09 |  |  | CDP |  | 13 |  | 11835 | 11856 | 21 | 24 | OK |  |  |  |  | 115 |  |  | 52 | 300 | 352 | 63 | 3 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_081M | Chamboli | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-05 |  |  | Gen Logic |  | 16 |  | 13189 | 13291 | 102 | 120 | OK |  |  |  |  | 459 |  |  | 115 | 300 | 415 | 344 | 3.3725 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_086M | Minsenshi-natwange | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-05 |  |  | Gen Logic |  | 16 |  | 293 | 293 | 0 | 120 | OK |  |  |  |  | 160 |  |  | 160 | 150 | 310 | 0 | #DIV/0! | 2 | [5 empty] | 0 | [7 empty] | DG DIDNT RUN | MERU |  | CAPTURED
IHS_CBT_092M | Nkana Stadium | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-05 |  |  | Gen Logic |  | 16 |  | 5398 | 5536 | 138 | 120 | inconsitent RH |  |  |  |  | 552 |  |  | 0 | 400 | 400 | 552 | 4 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_241M | Kagem mine | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-05 |  |  | perkins |  | 20 |  | 14060 | 14195 | 135 | 120 | inconsitent RH |  |  |  |  | 493 |  |  | 15 | 300 | 315 | 478 | 3.5407 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_061M | Mwekera | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-05 |  |  | CK Works |  | 20 |  | 4648 | 4711 | 63 | 120 | OK |  |  |  |  | 200 |  |  | 10 | 250 | 260 | 190 | 3.0159 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_345A | Ndeke Changachanga south 3G | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-05 |  |  | Gen Logic |  | 20 |  | 13436 | 13552 | 116 | 120 | OK |  |  |  |  | 250 |  |  | 0 | 250 | 250 | 250 | 2.1552 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_355A | Ndeke Sub. A | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Gen Only |  |  | Green Field |  | 2025-10-10 | 2025-10-05 |  |  | CK Works |  | 20 |  | 14869 | 14895 | 26 | 120 | OK |  |  |  |  | 155 |  |  | 69 | 250 | 319 | 86 | 3.3077 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_250A | SOB | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-05 |  |  | Gen Logic |  | 15 |  | 19403 | 19403 | 0 | 120 | OK |  |  |  |  | 210 |  |  | 210 | 100 | 310 | 0 | #DIV/0! | 1.8 | [5 empty] | 0 | [7 empty] | DG DIDNT RUN | MERU |  | CAPTURED
IHS_CBT_259A | KAMAKANGA I & II | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-05 |  |  | perkins |  | 20 |  | 21383 | 21476 | 93 | 120 | OK |  |  |  |  | 387 |  |  | 127 | 300 | 427 | 260 | 2.7957 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_223M | SHOW GROUNDS | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-05 |  |  | Generator City |  | 16 |  | FAULTY | FAULTY | #VALUE! | 120 | #VALUE! |  |  |  |  | 360 |  |  | 5 | 250 | 255 | 355 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | MERU |  | CAPTURED
IHS_CBT_217A | MAPOSA | GNM | SAMUEL | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-09-29 |  |  | Gen Logic |  | 30 |  | 0 | 25 | 25 | 264 | OK |  |  |  |  | 300 |  |  | 205 | 200 | 405 | 95 | 3.8 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_218M | WUSAKILE POLICE CAMP | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-09 |  |  | Generator City |  | 16 |  | 7409 | 7416 | 7 | 24 | OK |  |  |  |  | 117 |  |  | 94 | 200 | 294 | 23 | 3.2857 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_082M | Ndeke Extension | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-10 | 2025-10-05 |  |  | Gen Logic |  | 20 |  | 7380 | 7444 | 64 | 120 | OK |  |  |  |  | 383 |  |  | 50 | 300 | 350 | 333 | 5.2031 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_113M | Green Belt | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | IMG |  | 20 |  | 10516 | 10545 | 29 | 72 | OK |  |  |  |  | 362 |  |  | 190 | 300 | 490 | 172 | 5.931 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_121M | Ichipe | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | IHS_CBT_121M |  | 15 |  | 14162 | 14170 | 8 | 72 | OK |  |  |  |  | 347 |  |  | 315 | 200 | 515 | 32 | 4 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_090M | Jambo Drive | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | Gen Logic |  | 16 |  | 8506 | 8557 | 51 | 72 | OK |  |  |  |  | 335 |  |  | 86 | 300 | 386 | 249 | 4.8824 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_080M | Kalambo | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | Gen Logic |  | 16 |  | 6561 | 6583 | 22 | 72 | OK |  |  |  |  | 341 |  |  | 247 | 300 | 547 | 94 | 4.2727 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_296A | KAMUNGA | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | Gen Logic |  | 16 |  | 6045 | 6111 | 66 | 72 | OK |  |  |  |  | 305 |  |  | 51 | 300 | 351 | 254 | 3.8485 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_354A | Mufuchani | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Gen Only |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | CK Works |  | 20 |  | 13012 | 13042 | 30 | 72 | OK |  |  |  |  | 213 |  |  | 100 | 300 | 400 | 113 | 3.7667 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_269A | SOSOLISO | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | Jiuan |  | 15 |  | 5515 | 5552 | 37 | 72 | OK |  |  |  |  | 205 |  |  | 99 | 200 | 299 | 106 | 2.8649 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_089M | Valley View | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-09 |  |  | ASCOT |  | 30 |  | 2887 | 2945 | 58 | 48 | inconsitent RH |  |  |  |  | 422 |  |  | 132 | 300 | 432 | 290 | 5 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_103M | Kwacha central | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-09 |  |  | Gen Logic |  | 16 |  | 711 | 729 | 18 | 48 | OK |  |  |  |  | 260 |  |  | 176 | 200 | 376 | 84 | 4.6667 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_087M | Lulamba School | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-10 |  |  | perkins |  | 20 |  | 207 | 234 | 27 | 24 | inconsitent RH |  |  |  |  | 151 |  |  | 41 | 100 | 141 | 110 | 4.0741 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_037M | Minsundu | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | GL Yanmar |  | 16 |  | FAULTY | FAULTY | #VALUE! | 72 | #VALUE! |  |  |  |  | 210 |  |  | 87 | 200 | 287 | 123 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | MERU |  | CAPTURED
IHS_CBT_218A | PAMODZI | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | Gen Logic |  | 20 |  | 13664 | 13715 | 51 | 72 | OK |  |  |  |  | 281 |  |  | 133 | 200 | 333 | 148 | 2.902 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_013M | Dola Hill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | Himoinsa |  | 30 |  | 5655 | 5699 | 44 | 72 | OK |  |  |  |  | 447 |  |  | 235 | 300 | 535 | 212 | 4.8182 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_023M | Twapia | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | Gen Logic |  | 15 |  | 7541 | 7586 | 45 | 72 | OK |  |  |  |  | 360 |  |  | 175 | 200 | 375 | 185 | 4.1111 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_017M | Overspill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | Falcon |  | 20 |  | 8531 | 8594 | 63 | 72 | OK |  |  |  |  | 306 |  |  | 117 | 300 | 417 | 189 | 3 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_029M | Zafico | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | Green Power |  | 15 |  | 3228 | 3274 | 46 | 72 | OK |  |  |  |  | 249 |  |  | 92 | 200 | 292 | 157 | 3.413 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_222M | TWAPIA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | Generator City |  | 13 |  | 876 | 920 | 44 | 72 | OK |  |  |  |  | 222 |  |  | 40 | 300 | 340 | 182 | 4.1364 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_216M | COOL BANANAS | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-09 |  |  | Generator City |  | 13 |  | 7827 | 7846 | 19 | 48 | OK |  |  |  |  | 226 |  |  | 184 | 200 | 384 | 42 | 2.2105 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_233A | CHIPULUKUSU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | Earth Technology |  | 15 |  | 4813 | 4846 | 33 | 72 | OK |  |  |  |  | 260 |  |  | 111 | 300 | 411 | 149 | 4.5152 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_018M | Nkwanzi | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-10 |  |  | CK Works |  | 20 |  | 1308 | 1350 | 42 | 24 | inconsitent RH |  |  |  |  | 368 |  |  | 179 | 200 | 379 | 189 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-10 |  |  | GL Yanmar |  | 20 |  | 222 | 255 | 33 | 24 | inconsitent RH |  |  |  |  | 250 |  |  | 89 | 300 | 389 | 161 | 4.8788 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_359A | Cross Crescent | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-05 |  |  | CK Works |  | 20 |  | 5620 | 5634 | 14 | 144 | OK |  |  |  |  | 303 |  |  | 217 | 200 | 417 | 86 | 6.1429 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_041M | Kaniki | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-05 |  |  | GL Yanmar |  | 16 |  | 11174 | 11196 | 22 | 144 | OK |  |  |  |  | 242 |  |  | 180 | 100 | 280 | 62 | 2.8182 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_072M | Twasekela Basic | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-05 |  |  | Ghadder |  | 20 |  | FAULTY | FAULTY | #VALUE! | 144 | #VALUE! |  |  |  |  | 151 |  |  | 51 | 200 | 251 | 100 | #VALUE! | 2.5 | [5 empty] | 0 | [7 empty] | faulty controller | MERU |  | CAPTURED
IHS_CBT_332A | Ndeke_Ndola | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Roof Top |  | 2025-10-11 | 2025-09-29 |  |  | 0 |  | 15 |  | 613 | 725 | 112 | 288 | OK |  |  |  |  | 305 |  |  | 20 | 300 | 320 | 285 | 2.5446 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_156M | Mpongwe Turnoff | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-09-30 |  |  | Himoinsa |  | 30 |  | 6763 | 6827 | 64 | 264 | OK |  |  |  |  | 394 |  |  | 160 | 300 | 460 | 234 | 3.6562 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_045M | Tuckugan | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-04 |  |  | GL Yanmar |  | 16 |  | FAULTY | FAULTY | #VALUE! | 168 | #VALUE! |  |  |  |  | 120 |  |  | 20 | 200 | 220 | 100 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | MERU |  | CAPTURED
IHS_CBT_283A | MASALA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-05 |  |  | IMG |  | 20 |  | 7609 | 7686 | 77 | 144 | OK |  |  |  |  | 305 |  |  | 41 | 300 | 341 | 264 | 3.4286 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_363A | Milemu Sec. School | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-05 |  |  | CK Works |  | 20 |  | 10051 | 10132 | 81 | 144 | OK |  |  |  |  | 313 |  |  | 21 | 300 | 321 | 292 | 3.6049 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_338A | Musa Kasonka_3_Rlf | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-05 |  |  | CK Works |  | 20 |  | 10991 | 11034 | 43 | 144 | OK |  |  |  |  | 371 |  |  | 193 | 200 | 393 | 178 | 4.1395 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_033M | Bwana Mukubwa | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-09 |  |  | GL Yanmar |  | 16 |  | 881 | 919 | 38 | 48 | OK |  |  |  |  | 356 |  |  | 177 | 200 | 377 | 179 | 4.7105 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_027M | Kantolomba | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | CK Works |  | 20 |  | 5452 | 5497 | 45 | 72 | OK |  |  |  |  | 356 |  |  | 104 | 300 | 404 | 252 | 5.6 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_010M | Kabushi | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | IMG |  | 15 |  | 7520 | 7569 | 49 | 72 | OK |  |  |  |  | 363 |  |  | 181 | 200 | 381 | 182 | 3.7143 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_014M | Lubuto | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | CK Works |  | 20 |  | 3703 | 3750 | 47 | 72 | OK |  |  |  |  | 420 |  |  | 199 | 200 | 399 | 221 | 4.7021 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_006M | Lubuto Central | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | Lamasat |  | 15 |  | 956 | 1001 | 45 | 72 | OK |  |  |  |  | 330 |  |  | 118 | 200 | 318 | 212 | 4.7111 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_024M | Ndeke Township | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | CK Works |  | 30 |  | 11500 | 11555 | 55 | 72 | OK |  |  |  |  | 469 |  |  | 166 | 300 | 466 | 303 | 5.5091 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_021M | Sky ways | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | CK Works |  | 20 |  | 7391 | 7419 | 28 | 72 | OK |  |  |  |  | 330 |  |  | 198 | 200 | 398 | 132 | 4.7143 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_306A | TUG-ARGAN | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | Yanmar |  | 16 |  | 13033 | 13063 | 30 | 72 | OK |  |  |  |  | 210 |  |  | 120 | 200 | 320 | 90 | 3 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_034M | Mushili Baracks | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-05 |  |  | GL Yanmar |  | 15 |  | 27693 | 27798 | 105 | 144 | OK |  |  |  |  | 305 |  |  | 5 | 300 | 305 | 300 | 2.8571 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_224M | SKYWAYS KAPIRI ROAD | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-05 |  |  | Generator City |  | 13 |  | 4168 | 4251 | 83 | 144 | OK |  |  |  |  | 367 |  |  | 51 | 300 | 351 | 316 | 3.8072 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_289A | BUPE | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-01 |  |  | Gen Logic |  | 15 |  | 13186 | 13238 | 52 | 240 | OK |  |  |  |  | 285 |  |  | 90 | 200 | 290 | 195 | 3.75 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_105M | Buntungwa | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | Gen Logic |  | 16 |  | 5750 | 5792 | 42 | 72 | OK |  |  |  |  | 305 |  |  | 137 | 250 | 387 | 168 | 4 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_297A | KITWE POLICE | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | Gen Logic |  | 16 |  | 7538 | 7566 | 28 | 72 | OK |  |  |  |  | 205 |  |  | 123 | 250 | 373 | 82 | 2.9286 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_075M | Ndeke Changachanga | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | Gen Logic |  | 20 |  | 3596 | 3636 | 40 | 72 | OK |  |  |  |  | 329 |  |  | 125 | 200 | 325 | 204 | 5.1 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_108M | Chachacha | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | perkins |  | 20 |  | 1512 | 1542 | 30 | 72 | OK |  |  |  |  | 372 |  |  | 246 | 200 | 446 | 126 | 4.2 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_228A | MINDOLO | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | Earth technology |  | 20 |  | 11039 | 11100 | 61 | 72 | OK |  |  |  |  | 337 |  |  | 135 | 250 | 385 | 202 | 3.3115 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_079M | Ndeke | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | CK Works |  | 20 |  | 9880 | 9930 | 50 | 72 | OK |  |  |  |  | 305 |  |  | 25 | 500 | 525 | 280 | 5.6 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_244A | NDEKE | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | Earth technology |  | 15 |  | 3832 | 3870 | 38 | 72 | OK |  |  |  |  | 305 |  |  | 156 | 250 | 406 | 149 | 3.9211 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_237A | NKANA WEST | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | Earth technology |  | 20 |  | 11657 | 11724 | 67 | 72 | OK |  |  |  |  | 323 |  |  | 55 | 250 | 305 | 268 | 4 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_222A | CHAMBOLI | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | Gen Logic |  | 30 |  | 163 | 207 | 44 | 72 | OK |  |  |  |  | 310 |  |  | 113 | 200 | 313 | 197 | 4.4773 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_243A | GEDDIS | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | Gen Logic |  | 15 |  | 17776 | 17793 | 17 | 72 | OK |  |  |  |  | 245 |  |  | 180 | 200 | 380 | 65 | 3.8235 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_334A | Miseshi Village | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | Generator City |  | 16 |  | 3206 | 3237 | 31 | 72 | OK |  |  |  |  | 300 |  |  | 157 | 300 | 457 | 143 | 4.6129 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_083M | Nkana East | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | Gen Logic |  | 16 |  | 3785 | 3855 | 70 | 72 | OK |  |  |  |  | 310 |  |  | 23 | 300 | 323 | 287 | 4.1 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_356A | New Ndeke Village | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-08 |  |  | CK Works |  | 20 |  | 866 | 890 | 24 | 72 | OK |  |  |  |  | 356 |  |  | 226 | 200 | 426 | 130 | 5.4167 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_078M | Bupe | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-11 | 2025-10-10 |  |  | Gen Logic |  | 16 |  | 22987 | 22987 | 0 | 24 | OK |  |  |  |  | 159 |  |  | 159 | 200 | 359 | 0 | #DIV/0! | 2 | [5 empty] | 0 | [7 empty] | DG DIDNT RUN | MERU |  | CAPTURED
IHS_CBT_133M | Chibuluma Golf Club | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-12 | 2025-10-09 |  |  | Powerol |  | 13 |  | 5148 | 5227 | 79 | 72 | inconsitent RH |  |  |  |  | 300 |  |  | 15 | 300 | 315 | 285 | 3.6076 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_266A | KAWAMA Copperbelt | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-12 | 2025-10-08 |  |  | Gen Logic |  | 16 |  | 14353 | 14435 | 82 | 96 | OK |  |  |  |  | 257 |  |  | 18 | 300 | 318 | 239 | 2.9146 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_263A | NAKADOLI | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-12 | 2025-10-08 |  |  | Gen Logic |  | 16 |  | 6773 | 6841 | 68 | 96 | OK |  |  |  |  | 226 |  |  | 22 | 300 | 322 | 204 | 3 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_111M | Chimwemwe Nakadoli | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-12 | 2025-10-10 |  |  | GNM |  | 15 |  | 9577 | 9625 | 48 | 48 | OK |  |  |  |  | 250 |  |  | 130 | 300 | 430 | 120 | 2.5 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_087M | Lulamba School | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-12 | 2025-10-11 |  |  | perkins |  | 20 |  | 234 | 259 | 25 | 24 | inconsitent RH |  |  |  |  | 141 |  |  | 38 | 200 | 238 | 103 | 4.12 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_114M | Kamatipa North | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-12 | 2025-10-08 |  |  | perkins |  | 15 |  | 929 | 978 | 49 | 96 | OK |  |  |  |  | 310 |  |  | 88 | 300 | 388 | 222 | 4.5306 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_251A | Kitwe Railways | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-12 | 2025-09-29 |  |  | MPI |  | 20 |  | 5557 | 5661 | 104 | 312 | OK |  |  |  |  | 376 |  |  | 22 | 100 | 122 | 354 | 3.4038 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_112M | Kamtipa | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-12 | 2025-10-08 |  |  | Gen Logic |  | 16 |  | 430 | 481 | 51 | 96 | OK |  |  |  |  | 305 |  |  | 82 | 300 | 382 | 223 | 4.3725 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_335A | Daag Hamershold | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-12 | 2025-10-09 |  |  | LAMASAT |  | 15 |  | 7768 | 7846 | 78 | 72 | inconsitent RH |  |  |  |  | 242 |  |  | 47 | 100 | 147 | 195 | 2.5 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_257A | TWAPIA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-12 | 2025-10-10 |  |  | CK Works |  | 20 |  | 12598 | 12627 | 29 | 48 | OK |  |  |  |  | 311 |  |  | 180 | 200 | 380 | 131 | 4.5172 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_219M | PETAUKE CRESCENT | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-12 | 2025-10-10 |  |  | CK Works |  | 20 |  | 3811 | 3843 | 32 | 48 | OK |  |  |  |  | 258 |  |  | 104 | 300 | 404 | 154 | 4.8125 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_361A | Mitengo TDRC | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-12 | 2025-10-10 |  |  | CK Works |  | 20 |  | 5447 | 5492 | 45 | 48 | OK |  |  |  |  | 256 |  |  | 34 | 200 | 234 | 222 | 4.9333 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_347A | Ndola International Airport | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-12 | 2025-10-10 |  |  | Vitalgen |  | 20 |  | 8970 | 9046 | 76 | 48 | inconsitent RH |  |  |  |  | 292 |  |  | 86 | 200 | 286 | 206 | 2.7105 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_291A | MWATAYANVWA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-12 | 2025-10-10 |  |  | Gen Logic |  | 20 |  | 4357 | 4411 | 54 | 48 | inconsitent RH |  |  |  |  | 348 |  |  | 104 | 300 | 404 | 244 | 4.5185 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_301A | CHIBULUMA TOWN | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-12 | 2025-10-08 |  |  | Gen Logic |  | 16 |  | 9533 | 9612 | 79 | 96 | OK |  |  |  |  | 315 |  |  | 14 | 300 | 314 | 301 | 3.8101 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_126M | Chibuluma | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-12 | 2025-10-08 |  |  | Gen Logic |  | 20 |  | 3743 | 3799 | 56 | 96 | OK |  |  |  |  | 272 |  |  | 55 | 250 | 305 | 217 | 3.875 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_073M | Cedrics Farm | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-12 | 2025-10-09 |  |  | perkins |  | 15 |  | 17083 | 17144 | 61 | 72 | OK |  |  |  |  | 210 |  |  | 39 | 300 | 339 | 171 | 2.8033 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_368A | #N/A | #N/A | SAMUEL | #N/A | #N/A | #N/A |  | #N/A | #N/A |  |  | #N/A |  | 2025-10-12 | 2025-10-09 |  |  | #N/A |  | #N/A |  | 9893 | 9922 | 29 | 72 | OK |  |  |  |  | 105 |  |  | 12 | 250 | 262 | 93 | 3.2069 | #N/A | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_238M | NAPSA Complex | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-12 | 2025-10-09 |  |  | MPMC |  | 15 |  | 8566 | 8624 | 58 | 72 | OK |  |  |  |  | 359 |  |  | 147 | 100 | 247 | 212 | 3.6552 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_300A | LUBAMBE | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-12 | 2025-10-09 |  |  | Jiuan |  | 30 |  | 5105 | 5123 | 18 | 72 | OK |  |  |  |  | 224 |  |  | 148 | 250 | 398 | 76 | 4.2222 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_117M | Chibote | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-12 | 2025-10-09 |  |  | Gen Logic |  | 15 |  | 5798 | 5852 | 54 | 72 | OK |  |  |  |  | 325 |  |  | 119 | 200 | 319 | 206 | 3.8148 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_132M | Kalulushi West | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-12 | 2025-10-09 |  |  | Gen Logic |  | 20 |  | 5741 | 5788 | 47 | 72 | OK |  |  |  |  | 447 |  |  | 188 | 200 | 388 | 259 | 5.5106 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_134M | Kalulushi East | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-12 | 2025-10-09 |  |  | CK Works |  | 20 |  | 8265 | 8318 | 53 | 72 | OK |  |  |  |  | 405 |  |  | 177 | 200 | 377 | 228 | 4.3019 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_242A | PARKLANDS | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-12 | 2025-10-09 |  |  | Gen Logic |  | 20 |  | 9660 | 9696 | 36 | 72 | OK |  |  |  |  | 220 |  |  | 86 | 250 | 336 | 134 | 3.7222 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_094M | Kitwe Primary | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-12 | 2025-10-09 |  |  | Gen Logic |  | 16 |  | 2500 | 2556 | 56 | 72 | OK |  |  |  |  | 235 |  |  | 28 | 50 | 78 | 207 | 3.6964 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_267A | KALULUSHI EAST | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-12 | 2025-10-09 |  |  | Gen Logic |  | 16 |  | 13648 | 13705 | 57 | 72 | OK |  |  |  |  | 357 |  |  | 113 | 250 | 363 | 244 | 4.2807 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_119M | Lumumba | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-12 | 2025-10-09 |  |  | Gen Logic |  | 16 |  | 9572 | 9658 | 86 | 72 | inconsitent RH |  |  |  |  | 274 |  |  | 59 | 250 | 309 | 215 | 2.5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_127M | Kalulushi | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-12 | 2025-10-09 |  |  | Himoinsa |  | 30 |  | 10744 | 10818 | 74 | 72 | inconsitent RH |  |  |  |  | 367 |  |  | 71 | 300 | 371 | 296 | 4 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_102M | Richmond | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-12 | 2025-10-09 |  |  | Gen Logic |  | 16 |  | 2832 | 2865 | 33 | 72 | OK |  |  |  |  | 205 |  |  | 82 | 250 | 332 | 123 | 3.7273 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_206A | KALULUSHI | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-12 | 2025-10-09 |  |  | IMG |  | 15 |  | 7390 | 7435 | 45 | 72 | OK |  |  |  |  | 345 |  |  | 142 | 200 | 342 | 203 | 4.5111 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_107M | Mindolo South | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-08 |  |  | perkins |  | 20 |  | 9417 | 9455 | 38 | 120 | OK |  |  |  |  | 310 |  |  | 151 | 200 | 351 | 159 | 4.1842 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_116M | Twatacha | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-13 |  |  | Gen Logic |  | 16 |  | 458 | 497 | 39 | 0 | inconsitent RH |  |  |  |  | 275 |  |  | 143 | 300 | 443 | 132 | 3.3846 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_285A | KWACHA | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-17 |  |  | CK Works |  | 20 |  | 5285 | 5364 | 79 | -96 | inconsitent RH |  |  |  |  | 273 |  |  | 10 | 300 | 310 | 263 | 3.3291 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_123M | Mukuba University | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-28 |  |  | IMG |  | 15 |  | 11639 | 11679 | 40 | -360 | inconsitent RH |  |  |  |  | 292 |  |  | 152 | 300 | 452 | 140 | 3.5 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_005M | Premium Plaza | CCS | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Roof Top |  | 2025-10-13 | 2025-10-10 |  |  | N/A |  | N/A |  | 8588 | 8666 | 78 | 72 | inconsitent RH |  |  |  |  | 334 |  |  | 68 | 200 | 268 | 266 | 3.4103 | N/A | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_245A | NORTHRISE | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-10 |  |  | Lamasat |  | 20 |  | 8564 | 8640 | 76 | 72 | inconsitent RH |  |  |  |  | 444 |  |  | 102 | 300 | 402 | 342 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_226M | CHIFUBU WEST | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-10 |  |  | Generator City |  | 13 |  | 18990 | 19064 | 74 | 72 | inconsitent RH |  |  |  |  | 333 |  |  | 140 | 200 | 340 | 193 | 2.6081 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_364A | Chifubu Sec. School | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-08 |  |  | CK Works |  | 20 |  | 774 | 808 | 34 | 120 | OK |  |  |  |  | 352 |  |  | 128 | 100 | 228 | 224 | 6.5882 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_264A | NDOLA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-10 |  |  | Gen Logic |  | 16 |  | 5947 | 5992 | 45 | 72 | OK |  |  |  |  | 373 |  |  | 170 | 200 | 370 | 203 | 4.5111 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_252A | CHIFUBU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-10 |  |  | Gen Logic |  | 30 |  | 4062 | 4134 | 72 | 72 | OK |  |  |  |  | 409 |  |  | 85 | 300 | 385 | 324 | 4.5 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_041M | Kaniki | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-11 |  |  | GL Yanmar |  | 16 |  | 11196 | 11249 | 53 | 48 | inconsitent RH |  |  |  |  | 280 |  |  | 137 | 100 | 237 | 143 | 2.6981 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_025M | Pamozi Extension | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-10 |  |  | GL Yanmar |  | 16 |  | 3206 | 3285 | 79 | 72 | inconsitent RH |  |  |  |  | 366 |  |  | 136 | 300 | 436 | 230 | 2.9114 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_015M | Yengwe | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-10 |  |  | CK Works |  | 20 |  | 5734 | 5802 | 68 | 72 | OK |  |  |  |  | 370 |  |  | 64 | 300 | 364 | 306 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_016M | Itawa | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-08 |  |  | Vitalgen |  | 30 |  | 4623 | 4688 | 65 | 120 | OK |  |  |  |  | 375 |  |  | 10 | 400 | 410 | 365 | 5.6154 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_253A | ITAWA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-08 |  |  | Gen Logic |  | 20 |  | 10650 | 10730 | 80 | 120 | OK |  |  |  |  | 305 |  |  | 10 | 300 | 310 | 295 | 3.6875 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_234A | CHIWALA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-08 |  |  | Gen Logic |  | 20 |  | 21792 | 21831 | 39 | 120 | OK |  |  |  |  | 299 |  |  | 65 | 100 | 165 | 234 | 6 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_012M | Itawa West | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-08 |  |  | Lamasat |  | 20 |  | 11417 | 11522 | 105 | 120 | OK |  |  |  |  | 334 |  |  | 40 | 300 | 340 | 294 | 2.8 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_085M | Dangote | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-08 |  |  | Earth technology |  | 13 |  | 7971 | 8018 | 47 | 120 | OK |  |  |  |  | 290 |  |  | 155 | 100 | 255 | 135 | 2.8723 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_232A | LUBUTO | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-08 |  |  | Gen Logic |  | 20 |  | 11011 | 11068 | 57 | 120 | OK |  |  |  |  | 334 |  |  | 106 | 300 | 406 | 228 | 4 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_020M | Mushili | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-08 |  |  | CK Works |  | 30 |  | 8433 | 8488 | 55 | 120 | OK |  |  |  |  | 353 |  |  | 94 | 300 | 394 | 259 | 4.7091 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_336A | Fatima Girls | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-08 |  |  | perkins |  | 15 |  | 11248 | 11313 | 65 | 120 | OK |  |  |  |  | 364 |  |  | 121 | 100 | 221 | 243 | 3.7385 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_288A | NDOLA BUS STATION | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-08 |  |  | CK Works |  | 20 |  | 286 | 342 | 56 | 120 | OK |  |  |  |  | 305 |  |  | 38 | 400 | 438 | 267 | 4.7679 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_003M | Swimming Pool | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-08 |  |  | CK Works |  | 30 |  | 7147 | 7219 | 72 | 120 | OK |  |  |  |  | 443 |  |  | 97 | 400 | 497 | 346 | 4.8056 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_346A | Nilkant Mine | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Solar-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-08 |  |  | CK Works |  | 20 |  | 11423 | 11463 | 40 | 120 | OK |  |  |  |  | 279 |  |  | 124 | 300 | 424 | 155 | 3.875 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_032M | Cleveland | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-05 |  |  | CK Works |  | 20 |  | 6271 | 6299 | 28 | 192 | OK |  |  |  |  | 294 |  |  | 192 | 200 | 392 | 102 | 3.6429 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_214A | NDOLA FRA SILOS | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Roof Top |  | 2025-10-13 | 2025-10-05 |  |  | Lamasat |  | 20 |  | 12812 | 12885 | 73 | 192 | OK |  |  |  |  | 259 |  |  | 69 | 400 | 469 | 190 | 2.6027 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_309A | NDOLA LIME | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-05 |  |  | Gen Logic |  | 15 |  | 8851 | 8886 | 35 | 192 | OK |  |  |  |  | 237 |  |  | 116 | 200 | 316 | 121 | 3.4571 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_004M | Ndola T. Centre | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-10 |  |  | Falcon |  | 20 |  | 210 | 259 | 49 | 72 | OK |  |  |  |  | 320 |  |  | 94 | 300 | 394 | 226 | 4.6122 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_040M | Seed Of Hope | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-08 |  |  | Lamasat |  | 15 |  | 25085 | 25154 | 69 | 120 | OK |  |  |  |  | 310 |  |  | 68 | 200 | 268 | 242 | 3.5072 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_047M | Kamirenda | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-09 |  |  | Gen Logic |  | 16 |  | 13153 | 13181 | 28 | 96 | OK |  |  |  |  | 210 |  |  | 112 | 150 | 262 | 98 | 3.5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_227M | LUANSHYA EAST | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-09 |  |  | Generator City |  | 16 |  | 7585 | 7612 | 27 | 96 | OK |  |  |  |  | 384 |  |  | 265 | 100 | 365 | 119 | 4.4074 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_210A | LUANSHYA | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-09 |  |  | CK Works |  | 20 |  | 7881 | 7942 | 61 | 96 | OK |  |  |  |  | 318 |  |  | 92 | 300 | 392 | 226 | 3.7049 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_307A | TVTC | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-09 |  |  | Gen Logic |  | 16 |  | FAULTY | FAULTY | #VALUE! | 96 | #VALUE! |  |  |  |  | 206 |  |  | 81 | 200 | 281 | 125 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_054M | Mikomfwa Market | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-10 |  |  | Yanmar |  | 16 |  | 12427 | 12459 | 32 | 72 | OK |  |  |  |  | 294 |  |  | 10 | 150 | 160 | 284 | 8.875 | 2 | [5 empty] | 0 | [7 empty] | Stolen fuel abiut 145 ltrs mattered reported at mabungo police ob number 6762/25 | SAHARA |  | CAPTURED
IHS_CBT_043M | Fisenge | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-10 |  |  | Gen Logic |  | 16 |  | FAULTY | FAULTY | #VALUE! | 72 | #VALUE! |  |  |  |  | 351 |  |  | 223 | 100 | 323 | 128 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_048M | Kamirenda Extension | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-08 |  |  | Vitalgen |  | 20 |  | 9667 | 9725 | 58 | 120 | OK |  |  |  |  | 260 |  |  | 20 | 300 | 320 | 240 | 4.1379 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_312A | FISENGE | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-08 |  |  | Yanmar |  | 16 |  | 7377 | 7408 | 31 | 120 | OK |  |  |  |  | 220 |  |  | 105 | 200 | 305 | 115 | 3.7097 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_052M | Luanshya New Town | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-08 |  |  | Gen Logic |  | 16 |  | 15071 | 15118 | 47 | 120 | OK |  |  |  |  | 313 |  |  | 153 | 200 | 353 | 160 | 3.4043 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_230A | MIKOMFWA | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-08 |  |  | Earth technology |  | 15 |  | 906 | 942 | 36 | 120 | OK |  |  |  |  | 287 |  |  | 164 | 200 | 364 | 123 | 3.4167 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_155M | St. Joseph | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-09 |  |  | Gen Logic |  | 16 |  | 6526 | 6587 | 61 | 96 | OK |  |  |  |  | 315 |  |  | 145 | 200 | 345 | 170 | 2.7869 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_342A | Kantanta Street | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-09 |  |  | Gen Logic |  | 20 |  | 3779 | 3834 | 55 | 96 | OK |  |  |  |  | 215 |  |  | 11 | 300 | 311 | 204 | 3.7091 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_088M | Geddis | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-10 |  |  | CDP |  | 13 |  | 11856 | 11933 | 77 | 72 | inconsitent RH |  |  |  |  | 352 |  |  | 121 | 300 | 421 | 231 | 3 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_094M | Kitwe Primary | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-12 |  |  | Gen Logic |  | 16 |  | 2556 | 2571 | 15 | 24 | OK |  |  |  |  | 78 |  |  | 24 | 300 | 324 | 54 | 3.6 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_353A | Court Barrifs | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-09 |  |  | CK Works |  | 20 |  | 10493 | 10543 | 50 | 96 | OK |  |  |  |  | 220 |  |  | 31 | 300 | 331 | 189 | 3.78 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_237A | NKANA WEST | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-11 |  |  | Earth technology |  | 20 |  | 11724 | 11773 | 49 | 48 | inconsitent RH |  |  |  |  | 305 |  |  | 109 | 250 | 359 | 196 | 4 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_167M | Kafubu | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-09 |  |  | LISTER PETTER |  | 16 |  | FAULTY | FAULTY | #VALUE! | 96 | #VALUE! |  |  |  |  | 328 |  |  | 80 | 200 | 280 | 248 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_203M | Lufwanyama | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-04 |  |  | Gen Logic |  | 13 |  | FAULTY | FAULTY | #VALUE! | 216 | #VALUE! |  |  |  |  | 12 |  |  | 5 | 200 | 205 | 7 | #VALUE! | 1.5 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_104M | Twibukishe | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-05 |  |  | Gen Logic |  | 16 |  | 24350 | 10543 | -13807 | 192 | OK |  |  |  |  | 110 |  |  | 110 | 150 | 260 | 0 | 0 | 2 | [5 empty] | 0 | [7 empty] | DG DIDNT RUN | SAHARA |  | CAPTURED
IHS_CBT_355A | Ndeke Sub. A | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Gen Only |  |  | Green Field |  | 2025-10-13 | 2025-10-10 |  |  | CK Works |  | 20 |  | 14895 | 14963 | 68 | 72 | OK |  |  |  |  | 319 |  |  | 94 | 400 | 494 | 225 | 3.3088 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_223A | LUFWANYAMA | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-05 |  |  | Gen Logic |  | 20 |  | 6448 | 6540 | 92 | 192 | OK |  |  |  |  | 274 |  |  | 25 | 200 | 225 | 249 | 2.7065 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_223M | SHOW GROUNDS | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-10 |  |  | Generator City |  | 16 |  | FAULTY | FAULTY | #VALUE! | 72 | #VALUE! |  |  |  |  | 255 |  |  | 74 | 200 | 274 | 181 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_251A | Kitwe Railways | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-12 |  |  | MPI |  | 20 |  | 5661 | 5679 | 18 | 24 | OK |  |  |  |  | 122 |  |  | 60 | 300 | 360 | 62 | 3.4444 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_352A | Parklands TBN | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-10 |  |  | CK Works |  | 20 |  | 8280 | 8315 | 35 | 72 | OK |  |  |  |  | 214 |  |  | 119 | 200 | 319 | 95 | 2.7143 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_218M | WUSAKILE POLICE CAMP | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-13 | 2025-10-10 |  |  | Generator City |  | 16 |  | 7416 | 7437 | 21 | 72 | OK |  |  |  |  | 294 |  |  | 226 | 200 | 426 | 68 | 3.2381 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_074M | Luangwa | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-10 |  |  | Gen Logic |  | 16 |  | 4457 | 4521 | 64 | 96 | OK |  |  |  |  | 386 |  |  | 125 | 200 | 325 | 261 | 4.0781 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_242A | PARKLANDS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-12 |  |  | Gen Logic |  | 20 |  | 9696 | 9733 | 37 | 48 | OK |  |  |  |  | 336 |  |  | 185 | 150 | 335 | 151 | 4.0811 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_105M | Buntungwa | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-11 |  |  | Gen Logic |  | 16 |  | 5792 | 5840 | 48 | 72 | OK |  |  |  |  | 387 |  |  | 189 | 200 | 389 | 198 | 4.125 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_108M | Chachacha | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-11 |  |  | perkins |  | 20 |  | 1542 | 1598 | 56 | 72 | OK |  |  |  |  | 446 |  |  | 191 | 200 | 391 | 255 | 4.5536 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_243A | GEDDIS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-11 |  |  | Gen Logic |  | 15 |  | 17793 | 17871 | 78 | 72 | inconsitent RH |  |  |  |  | 380 |  |  | 98 | 200 | 298 | 282 | 3.6154 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_084M | Kitwe ZNS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-08 |  |  | CDP |  | 15 |  | 18136 | 18227 | 91 | 144 | OK |  |  |  |  | 300 |  |  | 66 | 300 | 366 | 234 | 2.5714 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_305A | LUANGWA KAFUE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-10 |  |  | Yanmar |  | 16 |  | 851 | 916 | 65 | 96 | OK |  |  |  |  | 386 |  |  | 386 | 150 | 536 | 0 | 0 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_228A | MINDOLO | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-11 |  |  | Earth technology |  | 20 |  | 11100 | 11178 | 78 | 72 | inconsitent RH |  |  |  |  | 385 |  |  | 153 | 200 | 353 | 232 | 2.9744 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_083M | Nkana East | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-11 |  |  | Gen Logic |  | 16 |  | 3855 | 3933 | 78 | 72 | inconsitent RH |  |  |  |  | 323 |  |  | 5 | 300 | 305 | 318 | 4.0769 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_102M | Richmond | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-12 |  |  | Gen Logic |  | 16 |  | 2865 | 2903 | 38 | 48 | OK |  |  |  |  | 332 |  |  | 179 | 150 | 329 | 153 | 4.0263 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_274A | ZNS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-08 |  |  | Gen Logic |  | 16 |  | 13154 | 13248 | 94 | 144 | OK |  |  |  |  | 305 |  |  | 43 | 300 | 343 | 262 | 2.7872 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_229A | CHIMWEMWE | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-10 |  |  | Gen Logic |  | 20 |  | 316 | 374 | 58 | 96 | OK |  |  |  |  | 509 |  |  | 161 | 300 | 461 | 348 | 6 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_090M | Jambo Drive | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-11 |  |  | Gen Logic |  | 16 |  | 8557 | 8610 | 53 | 72 | OK |  |  |  |  | 386 |  |  | 144 | 300 | 444 | 242 | 4.566 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_089M | Valley View | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-11 |  |  | ASCOT |  | 30 |  | 2945 | 3007 | 62 | 72 | OK |  |  |  |  | 432 |  |  | 114 | 300 | 414 | 318 | 5.129 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_113M | Green Belt | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-11 |  |  | IMG |  | 20 |  | 10545 | 10583 | 38 | 72 | OK |  |  |  |  | 490 |  |  | 265 | 300 | 565 | 225 | 5.9211 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_296A | KAMUNGA | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-11 |  |  | Gen Logic |  | 16 |  | 6111 | 6189 | 78 | 72 | inconsitent RH |  |  |  |  | 351 |  |  | 45 | 300 | 345 | 306 | 3.9231 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_018M | Nkwanzi | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-11 |  |  | CK Works |  | 20 |  | 1350 | 1400 | 50 | 72 | OK |  |  |  |  | 379 |  |  | 154 | 300 | 454 | 225 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_029M | Zafico | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-11 |  |  | Green Power |  | 15 |  | 3274 | 3324 | 50 | 72 | OK |  |  |  |  | 292 |  |  | 122 | 200 | 322 | 170 | 3.4 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_359A | Cross Crescent | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-11 |  |  | CK Works |  | 20 |  | 5634 | 5707 | 73 | 72 | inconsitent RH |  |  |  |  | 417 |  |  | 101 | 100 | 201 | 316 | 4.3288 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_013M | Dola Hill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-11 |  |  | Himoinsa |  | 30 |  | 5699 | 5751 | 52 | 72 | OK |  |  |  |  | 535 |  |  | 285 | 300 | 585 | 250 | 4.8077 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_361A | Mitengo TDRC | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-12 |  |  | CK Works |  | 20 |  | 5492 | 5539 | 47 | 48 | OK |  |  |  |  | 234 |  |  | 44 | 300 | 344 | 190 | 4.0426 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_022M | Kasembo | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-08 |  |  | Gen Logic |  | 20 |  | 6237 | 6278 | 41 | 144 | OK |  |  |  |  | 386 |  |  | 193 | 300 | 493 | 193 | 4.7073 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_035M | Kaloko | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-08 |  |  | Himoinsa |  | 30 |  | 9408 | 9485 | 77 | 144 | OK |  |  |  |  | 329 |  |  | 18 | 200 | 218 | 311 | 4.039 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_008M | Masala | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-08 |  |  | Generator City |  | 13 |  | 6374 | 6466 | 92 | 144 | OK |  |  |  |  | 404 |  |  | 36 | 100 | 136 | 368 | 4 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_024M | Ndeke Township | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-11 |  |  | CK Works |  | 30 |  | 11555 | 11608 | 53 | 72 | OK |  |  |  |  | 466 |  |  | 174 | 300 | 474 | 292 | 5.5094 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_360A | Hilcrest Extension | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-10 |  |  | CK Works |  | 20 |  | 10534 | 10595 | 61 | 96 | OK |  |  |  |  | 371 |  |  | 84 | 200 | 284 | 287 | 4.7049 | 5.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_027M | Kantolomba | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-11 |  |  | CK Works |  | 20 |  | 5491 | 5552 | 61 | 72 | OK |  |  |  |  | 404 |  |  | 96 | 300 | 396 | 308 | 5.0492 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_343A | Chinese Colony | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-08 |  |  | Gen Logic |  | 20 |  | FAULTY | FAULTY | #VALUE! | 144 | #VALUE! |  |  |  |  | 350 |  |  | 237 | 200 | 437 | 113 | #VALUE! | 2.5 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_064M | Finsansa Basic | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-08 |  |  | Yanmar |  | 16 |  | 7847 | 7884 | 37 | 144 | OK |  |  |  |  | 355 |  |  | 225 | 200 | 425 | 130 | 3.5135 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_058M | Mikomfwa | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-10 |  |  | Gen Logic |  | 16 |  | 7793 | 7823 | 30 | 96 | OK |  |  |  |  | 245 |  |  | 143 | 200 | 343 | 102 | 3.4 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_049M | Mikomfwa East | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-10 |  |  | Gen Logic |  | 16 |  | 6549 | 6593 | 44 | 96 | OK |  |  |  |  | 309 |  |  | 111 | 200 | 311 | 198 | 4.5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_277A | ROAN | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-08 |  |  | Gen Logic |  | 16 |  | FAULTY | FAULTY | #VALUE! | 144 | #VALUE! |  |  |  |  | 312 |  |  | 158 | 200 | 358 | 154 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_062M | Roan Township | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-08 |  |  | CK Works |  | 20 |  | 8251 | 8365 | 114 | 144 | OK |  |  |  |  | 355 |  |  | 5 | 200 | 205 | 350 | 3.0702 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_118M | Kamaronde | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-09 |  |  | CK Works |  | 20 |  | 3102 | 3158 | 56 | 120 | OK |  |  |  |  | 442 |  |  | 218 | 300 | 518 | 224 | 4 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_238M | NAPSA Complex | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-14 | 2025-10-12 |  |  | MPMC |  | 15 |  | 8624 | 8636 | 12 | 48 | OK |  |  |  |  | 247 |  |  | 201 | 200 | 401 | 46 | 3.8333 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_133M | Chibuluma Golf Club | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-12 |  |  | Powerol |  | 13 |  | 5227 | 5296 | 69 | 72 | OK |  |  |  |  | 315 |  |  | 66 | 300 | 366 | 249 | 3.6087 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_073M | Cedrics Farm | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-12 |  |  | perkins |  | 15 |  | 17144 | 17221 | 77 | 72 | inconsitent RH |  |  |  |  | 339 |  |  | 82 | 400 | 482 | 257 | 3.3377 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_368A | #N/A | #N/A | FACKSON | #N/A | #N/A | #N/A |  | #N/A | #N/A |  |  | #N/A |  | 2025-10-15 | 2025-10-12 |  |  | #N/A |  | #N/A |  | 9922 | 9965 | 43 | 72 | OK |  |  |  |  | 262 |  |  | 117 | 300 | 417 | 145 | 3.3721 | #N/A | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_300A | LUBAMBE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-12 |  |  | Jiuan |  | 30 |  | 5123 | 5179 | 56 | 72 | OK |  |  |  |  | 398 |  |  | 141 | 300 | 441 | 257 | 4.5893 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_222A | CHAMBOLI | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-11 |  |  | Gen Logic |  | 30 |  | 207 | 249 | 42 | 96 | OK |  |  |  |  | 313 |  |  | 123 | 300 | 423 | 190 | 4.5238 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_297A | KITWE POLICE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-11 |  |  | Gen Logic |  | 16 |  | 7566 | 7641 | 75 | 96 | OK |  |  |  |  | 373 |  |  | 128 | 300 | 428 | 245 | 3.2667 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_262A | MISESHI NATWANGE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-05 |  |  | perkins |  | 20 |  | 3961 | 3992 | 31 | 240 | OK |  |  |  |  | 423 |  |  | 346 | 100 | 446 | 77 | 2.4839 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_334A | Miseshi Village | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-11 |  |  | Generator City |  | 16 |  | 3237 | 3302 | 65 | 96 | OK |  |  |  |  | 457 |  |  | 105 | 400 | 505 | 352 | 5.4154 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_075M | Ndeke Changachanga | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-11 |  |  | Gen Logic |  | 20 |  | 3636 | 3696 | 60 | 96 | OK |  |  |  |  | 325 |  |  | 22 | 400 | 422 | 303 | 5.05 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_082M | Ndeke Extension | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-10 |  |  | Gen Logic |  | 20 |  | 7444 | 7502 | 58 | 120 | OK |  |  |  |  | 350 |  |  | 34 | 350 | 384 | 316 | 5.4483 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_356A | New Ndeke Village | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-11 |  |  | CK Works |  | 20 |  | 890 | 930 | 40 | 96 | OK |  |  |  |  | 426 |  |  | 210 | 300 | 510 | 216 | 5.4 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_235M | KAWAMA KCC (Chimwemwe rlf | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-10 |  |  | CK Works |  | 20 |  | 9471 | 9547 | 76 | 120 | OK |  |  |  |  | 444 |  |  | 41 | 200 | 241 | 403 | 5.3026 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_217M | KITWE MAIN SCHOOL | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-10 |  |  | Generator City |  | 16 |  | 15899 | 15994 | 95 | 120 | OK |  |  |  |  | 348 |  |  | 44 | 300 | 344 | 304 | 3.2 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_099M | Kitwe Town Center | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-10 |  |  | CDP |  | 15 |  | 9096 | 9164 | 68 | 120 | OK |  |  |  |  | 315 |  |  | 117 | 300 | 417 | 198 | 2.9118 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_351A | Riverside Congo Way | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-10 |  |  | CK Works |  | 20 |  | 5862 | 5944 | 82 | 120 | OK |  |  |  |  | 476 |  |  | 73 | 200 | 273 | 403 | 4.9146 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_080M | Kalambo | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-11 |  |  | Gen Logic |  | 16 |  | 6583 | 6629 | 46 | 96 | OK |  |  |  |  | 547 |  |  | 353 | 200 | 553 | 194 | 4.2174 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_098M | Bulangililo | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-10 |  |  | Gen Logic |  | 16 |  | 8210 | 8255 | 45 | 120 | OK |  |  |  |  | 336 |  |  | 201 | 200 | 401 | 135 | 3 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_103M | Kwacha central | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-11 |  |  | Gen Logic |  | 16 |  | 729 | 804 | 75 | 96 | OK |  |  |  |  | 376 |  |  | 31 | 300 | 331 | 345 | 4.6 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_344A | Nkwazi 3G | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-10 |  |  | CK Works |  | 20 |  | 45799 | 45837 | 38 | 120 | OK |  |  |  |  | 384 |  |  | 213 | 300 | 513 | 171 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_216M | COOL BANANAS | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-11 |  |  | Generator City |  | 13 |  | 7846 | 7905 | 59 | 96 | OK |  |  |  |  | 384 |  |  | 236 | 300 | 536 | 148 | 2.5085 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_017M | Overspill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-11 |  |  | Falcon |  | 20 |  | 8594 | 8715 | 121 | 96 | inconsitent RH |  |  |  |  | 417 |  |  | 54 | 300 | 354 | 363 | 3 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_219M | PETAUKE CRESCENT | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-12 |  |  | CK Works |  | 20 |  | 3843 | 3903 | 60 | 72 | OK |  |  |  |  | 404 |  |  | 116 | 300 | 416 | 288 | 4.8 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_257A | TWAPIA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-12 |  |  | CK Works |  | 20 |  | 12627 | 12675 | 48 | 72 | OK |  |  |  |  | 380 |  |  | 164 | 300 | 464 | 216 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_364A | Chifubu Sec. School | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-13 |  |  | CK Works |  | 20 |  | 806 | 821 | 15 | 48 | OK |  |  |  |  | 228 |  |  | 123 | 200 | 323 | 105 | 7 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_233A | CHIPULUKUSU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-11 |  |  | Earth Technology |  | 15 |  | 4846 | 4906 | 60 | 96 | OK |  |  |  |  | 411 |  |  | 141 | 300 | 441 | 270 | 4.5 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_041M | Kaniki | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-13 |  |  | GL Yanmar |  | 16 |  | 11247 | 11341 | 94 | 48 | inconsitent RH |  |  |  |  | 237 |  |  | 29 | 300 | 329 | 208 | 2.2128 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_037M | Minsundu | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-11 |  |  | GL Yanmar |  | 16 |  | FAULTY | FAULTY | #VALUE! | 96 | #VALUE! |  |  |  |  | 287 |  |  | 54 | 300 | 354 | 233 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_023M | Twapia | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-11 |  |  | Gen Logic |  | 15 |  | 7586 | 7636 | 50 | 96 | OK |  |  |  |  | 375 |  |  | 175 | 200 | 375 | 200 | 4 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_291A | MWATAYANVWA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-12 |  |  | Gen Logic |  | 20 |  | 4411 | 4479 | 68 | 72 | OK |  |  |  |  | 404 |  |  | 98 | 300 | 398 | 306 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-11 |  |  | GL Yanmar |  | 20 |  | 255 | 325 | 70 | 96 | OK |  |  |  |  | 389 |  |  | 35 | 100 | 135 | 354 | 5.0571 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_218A | PAMODZI | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-11 |  |  | Gen Logic |  | 20 |  | 13715 | 13787 | 72 | 96 | OK |  |  |  |  | 333 |  |  | 124 | 100 | 224 | 209 | 2.9028 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_226A | SAKANIA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-05 |  |  | Gen Logic |  | 16 |  | 1771 | 1849 | 78 | 240 | OK |  |  |  |  | 347 |  |  | 144 | 300 | 444 | 203 | 2.6026 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_222M | TWAPIA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-11 |  |  | Generator City |  | 13 |  | 920 | 990 | 70 | 96 | OK |  |  |  |  | 340 |  |  | 66 | 300 | 366 | 274 | 3.9143 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_207A | KANINI | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-10 |  |  | Gen Logic |  | 16 |  | 9095 | 9159 | 64 | 120 | OK |  |  |  |  | 337 |  |  | 110 | 300 | 410 | 227 | 3.5469 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_001M | Kanini | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-10 |  |  | IMG |  | 20 |  | 7589 | 7662 | 73 | 120 | OK |  |  |  |  | 359 |  |  | 88 | 200 | 288 | 271 | 3.7123 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_033M | Bwana Mukubwa | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-11 |  |  | GL Yanmar |  | 16 |  | 919 | 978 | 59 | 96 | OK |  |  |  |  | 377 |  |  | 99 | 300 | 399 | 278 | 4.7119 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_283A | MASALA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-11 |  |  | IMG |  | 20 |  | 7686 | 7752 | 66 | 96 | OK |  |  |  |  | 341 |  |  | 110 | 200 | 310 | 231 | 3.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_021M | Sky ways | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-11 |  |  | CK Works |  | 20 |  | 7419 | 7484 | 65 | 96 | OK |  |  |  |  | 398 |  |  | 92 | 300 | 392 | 306 | 4.7077 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_207A | KANINI | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-15 |  |  | Gen Logic |  | 16 |  | 9095 | 9159 | 64 | 0 | inconsitent RH |  |  |  |  | 410 |  |  | 113 | 150 | 263 | 297 | 4.6406 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_014M | Lubuto | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-11 |  |  | CK Works |  | 20 |  | 3750 | 3824 | 74 | 96 | OK |  |  |  |  | 399 |  |  | 51 | 300 | 351 | 348 | 4.7027 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_006M | Lubuto Central | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-11 |  |  | Lamasat |  | 15 |  | 1001 | 1072 | 71 | 96 | OK |  |  |  |  | 318 |  |  | 5 | 300 | 305 | 313 | 4.4085 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_009M | Tazama Building | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Roof Top |  | 2025-10-15 | 2025-10-10 |  |  | IMG |  | 16 |  | 28928 | 28987 | 59 | 120 | OK |  |  |  |  | 341 |  |  | 193 | 200 | 393 | 148 | 2.5085 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_010M | Kabushi | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-11 |  |  | IMG |  | 15 |  | 7569 | 7641 | 72 | 96 | OK |  |  |  |  | 381 |  |  | 114 | 150 | 264 | 267 | 3.7083 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_054M | Mikomfwa Market | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-13 |  |  | Yanmar |  | 16 |  | 12459 | 12480 | 21 | 48 | OK |  |  |  |  | 160 |  |  | 76 | 200 | 276 | 84 | 4 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_193M | Chambatata | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-05 |  |  | Yanmar |  | 16 |  | 12667 | 12744 | 77 | 240 | OK |  |  |  |  | 267 |  |  | 50 | 200 | 250 | 217 | 2.8182 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_044M | Kafubu Block | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-10 |  |  | Yanmar |  | 16 |  | 17788 | 17865 | 77 | 120 | OK |  |  |  |  | 267 |  |  | 22 | 300 | 322 | 245 | 3.1818 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_314A | KAFUBU BLOCK | GNM | Royd | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-10 |  |  | CK Works |  | 20 |  | 7501 | 7558 | 57 | 120 | OK |  |  |  |  | 294 |  |  | 100 | 300 | 400 | 194 | 3.4035 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_339A | Katuni Eden Institute | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-05 |  |  | Gen Logic |  | 10 |  | 15784 | 15851 | 67 | 240 | OK |  |  |  |  | 225 |  |  | 20 | 300 | 320 | 205 | 3.0597 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_168M | Mpongwe | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-09-09 |  |  | GL Yanmar |  | 16 |  | 11310 | 11340 | 30 | 864 | OK |  |  |  |  | 208 |  |  | 120 | 100 | 220 | 88 | 2.9333 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_265A | NEW TOWN | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-10 |  |  | Gen Logic |  | 16 |  | 1754 | 1798 | 44 | 120 | OK |  |  |  |  | 260 |  |  | 114 | 200 | 314 | 146 | 3.3182 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_319A | Nkanga Hill (Mumena_1) | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-03 |  |  | GL Yanmar |  | 15 |  | FAULTY | FAULTY | #VALUE! | 288 | #VALUE! |  |  |  |  | 302 |  |  | 36 | 300 | 336 | 266 | #VALUE! | 1.8 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_137M | Nkanga Hills | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-05 |  |  | GL Yanmar |  | 16 |  | 5649 | 5735 | 86 | 240 | OK |  |  |  |  | 281 |  |  | 25 | 300 | 325 | 256 | 2.9767 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_159M | Chembe South | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-09 |  |  | Gen Logic |  | 20 |  | FAULTY | FAULTY | #VALUE! | 144 | #VALUE! |  |  |  |  | 330 |  |  | 75 | 300 | 375 | 255 | #VALUE! | 2.5 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_117M | Chibote | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-12 |  |  | Gen Logic |  | 15 |  | 5852 | 5901 | 49 | 72 | OK |  |  |  |  | 319 |  |  | 132 | 200 | 332 | 187 | 3.8163 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_132M | Kalulushi West | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-12 |  |  | Gen Logic |  | 20 |  | 5788 | 5832 | 44 | 72 | OK |  |  |  |  | 388 |  |  | 146 | 300 | 446 | 242 | 5.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_301A | CHIBULUMA TOWN | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-12 |  |  | Gen Logic |  | 16 |  | 9612 | 9674 | 62 | 72 | OK |  |  |  |  | 314 |  |  | 78 | 300 | 378 | 236 | 3.8065 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_330A | Funda Junction (Mumena_5) | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-10 |  |  | METCO |  | 15 |  | FAULTY | FAULTY | #VALUE! | 120 | #VALUE! |  |  |  |  | 120 |  |  | 15 | 300 | 315 | 105 | #VALUE! | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_119M | Lumumba | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-12 |  |  | Gen Logic |  | 16 |  | 9658 | 9694 | 36 | 72 | OK |  |  |  |  | 309 |  |  | 214 | 200 | 414 | 95 | 2.6389 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_126M | Chibuluma | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-12 |  |  | Gen Logic |  | 20 |  | 3799 | 3843 | 44 | 72 | OK |  |  |  |  | 305 |  |  | 137 | 200 | 337 | 168 | 3.8182 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_206A | KALULUSHI | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-12 |  |  | IMG |  | 15 |  | 7435 | 7493 | 58 | 72 | OK |  |  |  |  | 342 |  |  | 78 | 300 | 378 | 264 | 4.5517 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_267A | KALULUSHI EAST | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-12 |  |  | Gen Logic |  | 16 |  | 13705 | 13764 | 59 | 72 | OK |  |  |  |  | 363 |  |  | 114 | 300 | 414 | 249 | 4.2203 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_329A | St. Marys Mission (MUTENDA ST. MARYS_1) | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-12 |  |  | METCO |  | 15 |  | FAULTY | FAULTY | #VALUE! | 72 | #VALUE! |  |  |  |  | 235 |  |  | 65 | 300 | 365 | 170 | #VALUE! | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_213M | St. Marys Mission | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-12 |  |  | Pramac |  | 10 |  | FAULTY | FAULTY | #VALUE! | 72 | #VALUE! |  |  |  |  | 245 |  |  | 5 | 300 | 305 | 240 | #VALUE! | 1.5 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_008M | Masala | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-14 |  |  | Generator City |  | 13 |  | 6466 | 6482 | 16 | 24 | OK |  |  |  |  | 136 |  |  | 72 | 200 | 272 | 64 | 4 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH |  |  | CAPTURED
IHS_CBT_349A | Kafubu Mall | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-15 | 2025-10-08 |  |  | Gen Logic |  | 16 |  | 16200 | 16280 | 80 | 168 | OK |  |  |  |  | 349 |  |  | 110 | 300 | 410 | 239 | 2.9875 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_129M | Emerald Mine Lufwanyama | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-16 | 2025-10-10 |  |  | Gen Logic |  | 15 |  | 25252 | 25363 | 111 | 144 | OK |  |  |  |  | 350 |  |  | 40 | 200 | 240 | 310 | 2.7928 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_094M | Kitwe Primary | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-16 | 2025-10-13 |  |  | Gen Logic |  | 16 |  | 2571 | 2626 | 55 | 72 | OK |  |  |  |  | 324 |  |  | 86 | 200 | 286 | 238 | 4.3273 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_081M | Chamboli | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-16 | 2025-10-10 |  |  | Gen Logic |  | 16 |  | 13291 | 13389 | 98 | 144 | OK |  |  |  |  | 415 |  |  | 111 | 200 | 311 | 304 | 3.102 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_244A | NDEKE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-16 | 2025-10-11 |  |  | Earth technology |  | 15 |  | 3870 | 3950 | 80 | 120 | OK |  |  |  |  | 406 |  |  | 81 | 200 | 281 | 325 | 4.0625 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_079M | Ndeke | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-16 | 2025-10-11 |  |  | CK Works |  | 20 |  | 9930 | 10044 | 114 | 120 | OK |  |  |  |  | 525 |  |  | 5 | 300 | 305 | 520 | 4.5614 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_299A | KITWE POST OFFICE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Roof Top |  | 2025-10-16 | 2025-10-10 |  |  | Gen Logic |  | 17 |  | 11289 | 11395 | 106 | 144 | OK |  |  |  |  | 214 |  |  | 0 | 200 | 200 | 214 | 2.0189 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_269A | SOSOLISO | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-16 | 2025-10-11 |  |  | Jiuan |  | 15 |  | 5552 | 5633 | 81 | 120 | OK |  |  |  |  | 299 |  |  | 54 | 300 | 354 | 245 | 3.0247 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_266A | KAWAMA Copperbelt | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-16 | 2025-10-12 |  |  | Gen Logic |  | 16 |  | 14435 | 14504 | 69 | 96 | OK |  |  |  |  | 318 |  |  | 117 | 200 | 317 | 201 | 2.913 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_285A | KWACHA | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-16 | 2025-10-13 |  |  | CK Works |  | 20 |  | 5364 | 5418 | 54 | 72 | OK |  |  |  |  | 310 |  |  | 121 | 300 | 421 | 189 | 3.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_235M | KAWAMA KCC (Chimwemwe rlf | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-16 | 2025-10-15 |  |  | CK Works |  | 20 |  | 9547 | 9561 | 14 | 24 | OK |  |  |  |  | 241 |  |  | 168 | 100 | 268 | 73 | 5.2143 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_114M | Kamatipa North | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-16 | 2025-10-12 |  |  | perkins |  | 15 |  | 978 | 1050 | 72 | 96 | OK |  |  |  |  | 388 |  |  | 64 | 200 | 264 | 324 | 4.5 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_112M | Kamtipa | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-16 | 2025-10-12 |  |  | Gen Logic |  | 16 |  | 481 | 519 | 38 | 96 | OK |  |  |  |  | 382 |  |  | 222 | 200 | 422 | 160 | 4.2105 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_359A | Cross Crescent | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-16 | 2025-10-14 |  |  | CK Works |  | 20 |  | 5707 | 5731 | 24 | 48 | OK |  |  |  |  | 201 |  |  | 95 | 200 | 295 | 106 | 4.4167 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_264A | NDOLA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-16 | 2025-10-13 |  |  | Gen Logic |  | 16 |  | 5992 | 6045 | 53 | 72 | OK |  |  |  |  | 370 |  |  | 135 | 200 | 335 | 235 | 4.434 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-16 | 2025-10-15 |  |  | GL Yanmar |  | 20 |  | 325 | 341 | 16 | 24 | OK |  |  |  |  | 135 |  |  | 55 | 200 | 255 | 80 | 5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_252A | CHIFUBU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-16 | 2025-10-13 |  |  | Gen Logic |  | 30 |  | 4134 | 4204 | 70 | 72 | OK |  |  |  |  | 385 |  |  | 70 | 300 | 370 | 315 | 4.5 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_025M | Pamozi Extension | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-16 | 2025-10-13 |  |  | GL Yanmar |  | 16 |  | 3285 | 3355 | 70 | 72 | OK |  |  |  |  | 436 |  |  | 253 | 300 | 553 | 183 | 2.6143 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_288A | NDOLA BUS STATION | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-16 | 2025-10-13 |  |  | CK Works |  | 20 |  | 342 | 389 | 47 | 72 | OK |  |  |  |  | 438 |  |  | 212 | 300 | 512 | 226 | 4.8085 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_085M | Dangote | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-16 | 2025-10-13 |  |  | Earth technology |  | 13 |  | 8018 | 8051 | 33 | 72 | OK |  |  |  |  | 255 |  |  | 163 | 150 | 313 | 92 | 2.7879 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_234A | CHIWALA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-16 | 2025-10-13 |  |  | Gen Logic |  | 20 |  | 21831 | 21846 | 15 | 72 | OK |  |  |  |  | 165 |  |  | 100 | 300 | 400 | 65 | 4.3333 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_325A | KALOKO KAFULAFUTA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-16 | 2025-10-14 |  |  | GL Yanmar |  | 15 |  | 7613 | 7629 | 16 | 48 | OK |  |  |  |  | 220 |  |  | 10 | 250 | 260 | 210 | 13.125 | 1.8 | [5 empty] | 0 | [7 empty] | STOLEN FUEL OB TO BE SHARED SOON | SAHARA |  | CAPTURED
IHS_CBT_004M | Ndola T. Centre | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-16 | 2025-10-13 |  |  | Falcon |  | 20 |  | 259 | 324 | 65 | 72 | OK |  |  |  |  | 394 |  |  | 85 | 300 | 385 | 309 | 4.7538 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_224M | SKYWAYS KAPIRI ROAD | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-16 | 2025-10-11 |  |  | Generator City |  | 13 |  | 4251 | 4324 | 73 | 120 | OK |  |  |  |  | 351 |  |  | 80 | 200 | 280 | 271 | 3.7123 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_362A | Ndola Central Police | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-16 | 2025-10-10 |  |  | CK Works |  | 20 |  | FAULTY | 12082 | #VALUE! | 144 | #VALUE! |  |  |  |  | 190 |  |  | 5 | 200 | 205 | 185 | #VALUE! | 4.5 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_331A | Mushili Baracks | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-16 | 2025-10-03 |  |  | GL Isuzu |  | 10 |  | 10535 | 10645 | 110 | 312 | OK |  |  |  |  | 405 |  |  | 17 | 200 | 217 | 388 | 3.5273 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_065M | Mpatamato East | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-16 | 2025-10-10 |  |  | Yanmar |  | 16 |  | 8450 | 8550 | 100 | 144 | OK |  |  |  |  | 325 |  |  | 21 | 200 | 221 | 304 | 3.04 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_134M | Kalulushi East | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-16 | 2025-10-12 |  |  | CK Works |  | 20 |  | 8318 | 8389 | 71 | 96 | OK |  |  |  |  | 377 |  |  | 71 | 300 | 371 | 306 | 4.3099 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_127M | Kalulushi | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-16 | 2025-10-12 |  |  | Himoinsa |  | 30 |  | 10818 | 10874 | 56 | 96 | OK |  |  |  |  | 371 |  |  | 147 | 300 | 447 | 224 | 4 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_146M | Miku Mining | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-16 | 2025-10-10 |  |  | Gen Logic |  | 20 |  | 20443 | 20569 | 126 | 144 | OK |  |  |  |  | 331 |  |  | 5 | 300 | 305 | 326 | 2.5873 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_259A | KAMAKANGA I & II | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-16 | 2025-10-10 |  |  | perkins |  | 20 |  | 21476 | 21549 | 73 | 144 | OK |  |  |  |  | 427 |  |  | 222 | 300 | 522 | 205 | 2.8082 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_088M | Geddis | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-13 |  |  | CDP |  | 13 |  | 11933 | 12032 | 99 | 96 | inconsitent RH |  |  |  |  | 421 |  |  | 107 | 300 | 407 | 314 | 3.1717 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_342A | Kantanta Street | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-13 |  |  | Gen Logic |  | 20 |  | 3834 | 3902 | 68 | 96 | OK |  |  |  |  | 311 |  |  | 20 | 300 | 320 | 291 | 4.2794 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_074M | Luangwa | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-14 |  |  | Gen Logic |  | 16 |  | 4521 | 4577 | 56 | 72 | OK |  |  |  |  | 325 |  |  | 93 | 300 | 393 | 232 | 4.1429 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_305A | LUANGWA KAFUE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-14 |  |  | Yanmar |  | 16 |  | 916 | 972 | 56 | 72 | OK |  |  |  |  | 292 |  |  | 292 | 100 | 392 | 0 | 0 | 2 | [5 empty] | 0 | [8 empty] | IHS PUMA |  | CAPTURED
IHS_CBT_237A | NKANA WEST | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-13 |  |  | Earth technology |  | 20 |  | 11773 | 11869 | 96 | 96 | OK |  |  |  |  | 359 |  |  | 5 | 300 | 305 | 354 | 3.6875 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_228A | MINDOLO | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-14 |  |  | Earth technology |  | 20 |  | 11178 | 11246 | 68 | 72 | OK |  |  |  |  | 353 |  |  | 151 | 200 | 351 | 202 | 2.9706 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_105M | Buntungwa | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-14 |  |  | Gen Logic |  | 16 |  | 5840 | 5879 | 39 | 72 | OK |  |  |  |  | 389 |  |  | 226 | 300 | 526 | 163 | 4.1795 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_243A | GEDDIS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-14 |  |  | Gen Logic |  | 15 |  | 17871 | 17941 | 70 | 72 | OK |  |  |  |  | 298 |  |  | 46 | 300 | 346 | 252 | 3.6 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_083M | Nkana East | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-14 |  |  | Gen Logic |  | 16 |  | 3933 | 3992 | 59 | 72 | OK |  |  |  |  | 305 |  |  | 60 | 400 | 460 | 245 | 4.1525 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_115M | Mindolo | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-10 |  |  | Gen Logic |  | 16 |  | 7384 | 7496 | 112 | 168 | OK |  |  |  |  | 369 |  |  | 13 | 100 | 113 | 356 | 3.1786 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_276A | KAKOLO I & II | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Solar-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-10 |  |  | Jiuan |  | 15 |  | 24122 | 24187 | 65 | 168 | OK |  |  |  |  | 360 |  |  | 160 | 300 | 460 | 200 | 3.0769 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_263A | NAKADOLI | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-12 |  |  | Gen Logic |  | 16 |  | 6841 | 6906 | 65 | 120 | OK |  |  |  |  | 322 |  |  | 133 | 200 | 333 | 189 | 2.9077 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_111M | Chimwemwe Nakadoli | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-12 |  |  | GNM |  | 15 |  | 9625 | 9688 | 63 | 120 | OK |  |  |  |  | 430 |  |  | 272 | 200 | 472 | 158 | 2.5079 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_107M | Mindolo South | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-13 |  |  | perkins |  | 20 |  | 9455 | 9494 | 39 | 96 | OK |  |  |  |  | 351 |  |  | 187 | 200 | 387 | 164 | 4.2051 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_333A | Mindolo North | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-10 |  |  | perkins |  | 15 |  | 8990 | 9075 | 85 | 168 | OK |  |  |  |  | 339 |  |  | 101 | 200 | 301 | 238 | 2.8 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_296A | KAMUNGA | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-14 |  |  | Gen Logic |  | 16 |  | 6189 | 6257 | 68 | 72 | OK |  |  |  |  | 345 |  |  | 86 | 100 | 186 | 259 | 3.8088 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_361A | Mitengo TDRC | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-14 |  |  | CK Works |  | 20 |  | 5539 | 5610 | 71 | 72 | OK |  |  |  |  | 344 |  |  | 24 | 200 | 224 | 320 | 4.507 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_005M | Premium Plaza | CCS | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Roof Top |  | 2025-10-17 | 2025-10-13 |  |  | N/A |  | N/A |  | 8666 | 8734 | 68 | 96 | OK |  |  |  |  | 268 |  |  | 36 | 300 | 336 | 232 | 3.4118 | N/A | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_091M | Kalalangabo | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-08 |  |  | GL Yanmar |  | 16 |  | 5850 | 5898 | 48 | 216 | OK |  |  |  |  | 429 |  |  | 261 | 200 | 461 | 168 | 3.5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_236A | KALALANGABO | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-08 |  |  | ASCOT |  | 30 |  | 91 | 131 | 40 | 216 | OK |  |  |  |  | 255 |  |  | 60 | 300 | 360 | 195 | 4.875 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_232A | LUBUTO | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-13 |  |  | Gen Logic |  | 20 |  | 11068 | 11107 | 39 | 96 | OK |  |  |  |  | 406 |  |  | 250 | 200 | 450 | 156 | 4 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_336A | Fatima Girls | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-13 |  |  | perkins |  | 15 |  | 11313 | 11371 | 58 | 96 | OK |  |  |  |  | 221 |  |  | 18 | 300 | 318 | 203 | 3.5 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_016M | Itawa | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-13 |  |  | Vitalgen |  | 30 |  | 4688 | 4745 | 57 | 96 | OK |  |  |  |  | 410 |  |  | 90 | 200 | 290 | 320 | 5.614 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_253A | ITAWA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-13 |  |  | Gen Logic |  | 20 |  | 10730 | 10803 | 73 | 96 | OK |  |  |  |  | 310 |  |  | 32 | 300 | 332 | 278 | 3.8082 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_024M | Ndeke Township | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-14 |  |  | CK Works |  | 30 |  | 11608 | 11661 | 53 | 72 | OK |  |  |  |  | 474 |  |  | 182 | 300 | 482 | 292 | 5.5094 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_035M | Kaloko | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-14 |  |  | Himoinsa |  | 30 |  | 9485 | 9514 | 29 | 72 | OK |  |  |  |  | 218 |  |  | 98 | 200 | 298 | 120 | 4.1379 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_027M | Kantolomba | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-14 |  |  | CK Works |  | 20 |  | 5552 | 5601 | 49 | 72 | OK |  |  |  |  | 396 |  |  | 121 | 300 | 421 | 275 | 5.6122 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_338A | Musa Kasonka_3_Rlf | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-11 |  |  | CK Works |  | 20 |  | 11034 | 11121 | 87 | 144 | OK |  |  |  |  | 393 |  |  | 62 | 300 | 362 | 331 | 3.8046 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_360A | Hilcrest Extension | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-14 |  |  | CK Works |  | 20 |  | 10595 | 10645 | 50 | 72 | OK |  |  |  |  | 284 |  |  | 49 | 200 | 249 | 235 | 4.7 | 5.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_050M | Luanshya Town Center | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-09 |  |  | Gen Logic |  | 20 |  | 8445 | 8527 | 82 | 192 | OK |  |  |  |  | 501 |  |  | 94 | 200 | 294 | 407 | 4.9634 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_227M | LUANSHYA EAST | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-13 |  |  | Generator City |  | 16 |  | 7612 | 7663 | 51 | 96 | OK |  |  |  |  | 365 |  |  | 145 | 200 | 345 | 220 | 4.3137 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_210A | LUANSHYA | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-13 |  |  | CK Works |  | 20 |  | 7942 | 7993 | 51 | 96 | OK |  |  |  |  | 392 |  |  | 208 | 200 | 408 | 184 | 3.6078 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_181M | Lukanga resettlement | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Solar-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-10 |  |  | CK Works |  | 20 |  | 5328 | 5490 | 162 | 168 | OK |  |  |  |  | 410 |  |  | 10 | 300 | 310 | 400 | 2.4691 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_215M | PHILIP FARM | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Solar-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-17 |  |  | perkins |  | 15 |  | 19428 | 19531 | 103 | 0 | inconsitent RH |  |  |  |  | 338 |  |  | 70 | 200 | 270 | 268 | 2.6019 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_161M | Mikata Mpongwe | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Solar-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-26 |  |  | IMG |  | 20 |  | 9778 | 9871 | 93 | -216 | inconsitent RH |  |  |  |  | 338 |  |  | 30 | 200 | 230 | 308 | 3.3118 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_052M | Luanshya New Town | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-13 |  |  | Gen Logic |  | 16 |  | 15118 | 15150 | 32 | 96 | OK |  |  |  |  | 353 |  |  | 241 | 200 | 441 | 112 | 3.5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_067M | Mpatamato | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-09-09 |  |  | Gen Logic |  | 16 |  | 6878 | 6950 | 72 | 912 | OK |  |  |  |  | 255 |  |  | 25 | 200 | 225 | 230 | 3.1944 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_230A | MIKOMFWA | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-13 |  |  | Earth technology |  | 15 |  | 942 | 996 | 54 | 96 | OK |  |  |  |  | 364 |  |  | 169 | 200 | 369 | 195 | 3.6111 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_048M | Kamirenda Extension | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-13 |  |  | Vitalgen |  | 20 |  | 9725 | 9766 | 41 | 96 | OK |  |  |  |  | 320 |  |  | 160 | 200 | 360 | 160 | 3.9024 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_312A | FISENGE | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-13 |  |  | Yanmar |  | 16 |  | 7408 | 7427 | 19 | 96 | OK |  |  |  |  | 305 |  |  | 232 | 200 | 432 | 73 | 3.8421 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_043M | Fisenge | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-13 |  |  | Gen Logic |  | 16 |  | FAULTY | FAULTY | #VALUE! | 96 | #VALUE! |  |  |  |  | 323 |  |  | 127 | 200 | 327 | 196 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | MERU |  | CAPTURED
IHS_CBT_241M | Kagem mine | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-17 | 2025-10-10 |  |  | perkins |  | 20 |  | 14195 | 14285 | 90 | 168 | OK |  |  |  |  | 315 |  |  | 10 | 100 | 110 | 305 | 3.3889 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_108M | Chachacha | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-14 |  |  | perkins |  | 20 |  | 1598 | 1635 | 37 | 96 | OK |  |  |  |  | 391 |  |  | 221 | 300 | 521 | 170 | 4.5946 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_353A | Court Barrifs | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-13 |  |  | CK Works |  | 20 |  | 10543 | 10600 | 57 | 120 | OK |  |  |  |  | 331 |  |  | 96 | 200 | 296 | 235 | 4.1228 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_251A | Kitwe Railways | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-13 |  |  | MPI |  | 20 |  | 5679 | 5765 | 86 | 120 | OK |  |  |  |  | 360 |  |  | 30 | 50 | 80 | 330 | 3.8372 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_092M | Nkana Stadium | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-10 |  |  | Gen Logic |  | 16 |  | 5536 | 5630 | 94 | 192 | OK |  |  |  |  | 400 |  |  | 20 | 50 | 70 | 380 | 4.0426 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_092M | Nkana Stadium | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-18 |  |  | Gen Logic |  | 16 |  | 5630 | 5643 | 13 | 0 | inconsitent RH |  |  |  |  | 70 |  |  | 20 | 150 | 170 | 50 | 3.8462 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_251A | Kitwe Railways | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-18 |  |  | MPI |  | 20 |  | 5765 | 5785 | 20 | 0 | inconsitent RH |  |  |  |  | 80 |  |  | 20 | 150 | 170 | 60 | 3 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_089M | Valley View | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-14 |  |  | ASCOT |  | 30 |  | 3007 | 3083 | 76 | 96 | OK |  |  |  |  | 414 |  |  | 22 | 150 | 172 | 392 | 5.1579 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_229A | CHIMWEMWE | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-14 |  |  | Gen Logic |  | 20 |  | 374 | 448 | 74 | 96 | OK |  |  |  |  | 461 |  |  | 38 | 300 | 338 | 423 | 5.7162 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_351A | Riverside Congo Way | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-15 |  |  | CK Works |  | 20 |  | 5944 | 5990 | 46 | 72 | OK |  |  |  |  | 273 |  |  | 41 | 200 | 241 | 232 | 5.0435 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_235M | KAWAMA KCC (Chimwemwe rlf | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-16 |  |  | CK Works |  | 20 |  | 9561 | 9601 | 40 | 48 | OK |  |  |  |  | 268 |  |  | 45 | 100 | 145 | 223 | 5.575 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_115M | Mindolo | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-17 |  |  | Gen Logic |  | 16 |  | 7496 | 7525 | 29 | 24 | inconsitent RH |  |  |  |  | 113 |  |  | 29 | 200 | 229 | 84 | 2.8966 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_296A | KAMUNGA | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-17 |  |  | Gen Logic |  | 16 |  | 6257 | 6286 | 29 | 24 | inconsitent RH |  |  |  |  | 186 |  |  | 73 | 200 | 273 | 113 | 3.8966 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_245A | NORTHRISE | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-13 |  |  | Lamasat |  | 20 |  | 8640 | 8714 | 74 | 120 | OK |  |  |  |  | 402 |  |  | 69 | 250 | 319 | 333 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_029M | Zafico | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-14 |  |  | Green Power |  | 15 |  | 3324 | 3404 | 80 | 96 | OK |  |  |  |  | 322 |  |  | 50 | 200 | 250 | 272 | 3.4 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_018M | Nkwanzi | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-14 |  |  | CK Works |  | 20 |  | 1400 | 1488 | 88 | 96 | OK |  |  |  |  | 454 |  |  | 58 | 300 | 358 | 396 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_013M | Dola Hill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-14 |  |  | Himoinsa |  | 30 |  | 5751 | 5827 | 76 | 96 | OK |  |  |  |  | 585 |  |  | 205 | 300 | 505 | 380 | 5 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_364A | Chifubu Sec. School | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-15 |  |  | CK Works |  | 20 |  | 821 | 848 | 27 | 72 | OK |  |  |  |  | 323 |  |  | 134 | 200 | 334 | 189 | 7 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_023M | Twapia | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-15 |  |  | Gen Logic |  | 15 |  | 7636 | 7701 | 65 | 72 | OK |  |  |  |  | 375 |  |  | 115 | 200 | 315 | 260 | 4 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-16 |  |  | GL Yanmar |  | 20 |  | 341 | 374 | 33 | 48 | OK |  |  |  |  | 255 |  |  | 90 | 200 | 290 | 165 | 5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_347A | Ndola International Airport | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-12 |  |  | Vitalgen |  | 20 |  | 9046 | 9120 | 74 | 144 | OK |  |  |  |  | 286 |  |  | 78 | 200 | 278 | 208 | 2.8108 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_226M | CHIFUBU WEST | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-13 |  |  | Generator City |  | 13 |  | 19064 | 19159 | 95 | 120 | OK |  |  |  |  | 340 |  |  | 86 | 300 | 386 | 254 | 2.6737 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_218A | PAMODZI | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-15 |  |  | Gen Logic |  | 20 |  | 13787 | 13855 | 68 | 72 | OK |  |  |  |  | 224 |  |  | 26 | 300 | 326 | 198 | 2.9118 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_015M | Yengwe | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-13 |  |  | CK Works |  | 20 |  | 5802 | 5868 | 66 | 120 | OK |  |  |  |  | 364 |  |  | 67 | 300 | 367 | 297 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_361A | Mitengo TDRC | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-17 |  |  | CK Works |  | 20 |  | 5610 | 5629 | 19 | 24 | OK |  |  |  |  | 224 |  |  | 138 | 300 | 438 | 86 | 4.5263 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_072M | Twasekela Basic | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-11 |  |  | Ghadder |  | 20 |  | FAULTY | 9414 | #VALUE! | 168 | #VALUE! |  |  |  |  | 251 |  |  | 111 | 300 | 411 | 140 | #VALUE! | 2.5 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_012M | Itawa West | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-13 |  |  | Lamasat |  | 20 |  | 11522 | 11611 | 89 | 120 | OK |  |  |  |  | 340 |  |  | 90 | 300 | 390 | 250 | 2.809 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_003M | Swimming Pool | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-13 |  |  | CK Works |  | 30 |  | 7219 | 7314 | 95 | 120 | OK |  |  |  |  | 497 |  |  | 45 | 400 | 445 | 452 | 4.7579 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_363A | Milemu Sec. School | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-11 |  |  | CK Works |  | 20 |  | 10132 | 10191 | 59 | 168 | OK |  |  |  |  | 321 |  |  | 102 | 300 | 402 | 219 | 3.7119 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_006M | Lubuto Central | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-15 |  |  | Lamasat |  | 15 |  | 1072 | 1127 | 55 | 72 | OK |  |  |  |  | 305 |  |  | 52 | 100 | 152 | 253 | 4.6 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_014M | Lubuto | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-15 |  |  | CK Works |  | 20 |  | 3824 | 3874 | 50 | 72 | OK |  |  |  |  | 351 |  |  | 116 | 200 | 316 | 235 | 4.7 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_010M | Kabushi | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-15 |  |  | IMG |  | 15 |  | 7641 | 7694 | 53 | 72 | OK |  |  |  |  | 264 |  |  | 68 | 200 | 268 | 196 | 3.6981 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_002M | Hillcrest | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-10 |  |  | GL Yanmar |  | 20 |  | 7800 | 7864 | 64 | 192 | OK |  |  |  |  | 299 |  |  | 75 | 300 | 375 | 224 | 3.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_306A | TUG-ARGAN | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-11 |  |  | Yanmar |  | 16 |  | 13063 | 13114 | 51 | 168 | OK |  |  |  |  | 320 |  |  | 111 | 100 | 211 | 209 | 4.098 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_362A | Ndola Central Police | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-16 |  |  | CK Works |  | 20 |  | 12085 | 12120 | 35 | 48 | OK |  |  |  |  | 205 |  |  | 5 | 200 | 205 | 200 | 5.7143 | 4.5 | [5 empty] | 0 | [7 empty] | faulty controller | MERU |  | CAPTURED
IHS_CBT_360A | Hilcrest Extension | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-17 |  |  | CK Works |  | 20 |  | 10645 | 10680 | 35 | 24 | inconsitent RH |  |  |  |  | 249 |  |  | 84 | 100 | 184 | 165 | 4.7143 | 5.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_036M | Lubendo | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-18 | 2025-10-13 |  |  | GL Yanmar |  | 16 |  | 673 | 784 | 111 | 120 | OK |  |  |  |  | 347 |  |  | 5 | 300 | 305 | 342 | 3.0811 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_133M | Chibuluma Golf Club | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-15 |  |  | Powerol |  | 13 |  | 5297 | 5380 | 83 | 96 | OK |  |  |  |  | 366 |  |  | 67 | 100 | 167 | 299 | 3.6024 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_242A | PARKLANDS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-14 |  |  | Gen Logic |  | 20 |  | 9733 | 9803 | 70 | 120 | OK |  |  |  |  | 335 |  |  | 72 | 200 | 272 | 263 | 3.7571 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_244A | NDEKE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-16 |  |  | Earth technology |  | 15 |  | 3950 | 4000 | 50 | 72 | OK |  |  |  |  | 281 |  |  | 76 | 200 | 276 | 205 | 4.1 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_075M | Ndeke Changachanga | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-15 |  |  | Gen Logic |  | 20 |  | 3696 | 3761 | 65 | 96 | OK |  |  |  |  | 422 |  |  | 86 | 200 | 286 | 336 | 5.1692 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_079M | Ndeke | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-16 |  |  | CK Works |  | 20 |  | 10044 | 10093 | 49 | 72 | OK |  |  |  |  | 305 |  |  | 58 | 200 | 258 | 247 | 5.0408 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_356A | New Ndeke Village | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-15 |  |  | CK Works |  | 20 |  | 930 | 996 | 66 | 96 | OK |  |  |  |  | 510 |  |  | 185 | 100 | 285 | 325 | 4.9242 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_334A | Miseshi Village | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-15 |  |  | Generator City |  | 16 |  | 3302 | 3367 | 65 | 96 | OK |  |  |  |  | 505 |  |  | 151 | 400 | 551 | 354 | 5.4462 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_082M | Ndeke Extension | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-15 |  |  | Gen Logic |  | 20 |  | 7502 | 7556 | 54 | 96 | OK |  |  |  |  | 384 |  |  | 101 | 200 | 301 | 283 | 5.2407 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_223M | SHOW GROUNDS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-13 |  |  | Generator City |  | 16 |  | FAULTY | FAULTY | #VALUE! | 144 | #VALUE! |  |  |  |  | 274 |  |  | 5 | 200 | 205 | 269 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | MERU |  | CAPTURED
IHS_CBT_222A | CHAMBOLI | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-15 |  |  | Gen Logic |  | 30 |  | 249 | 308 | 59 | 96 | OK |  |  |  |  | 423 |  |  | 147 | 100 | 247 | 276 | 4.678 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_345A | Ndeke Changachanga south 3G | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-10 |  |  | Gen Logic |  | 20 |  | 13552 | 13637 | 85 | 216 | OK |  |  |  |  | 250 |  |  | 5 | 200 | 205 | 245 | 2.8824 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_305A | LUANGWA KAFUE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-17 |  |  | Yanmar |  | 16 |  | 972 | 1008 | 36 | 48 | OK |  |  |  |  | 185 |  |  | 185 | 300 | 485 | 0 | 0 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_352A | Parklands TBN | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-13 |  |  | CK Works |  | 20 |  | 8315 | 8437 | 122 | 144 | OK |  |  |  |  | 319 |  |  | 5 | 300 | 305 | 314 | 2.5738 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_102M | Richmond | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-14 |  |  | Gen Logic |  | 16 |  | 2903 | 2962 | 59 | 120 | OK |  |  |  |  | 329 |  |  | 103 | 200 | 303 | 226 | 3.8305 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_250A | SOB | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-10 |  |  | Gen Logic |  | 15 |  | 19403 | 19533 | 130 | 216 | OK |  |  |  |  | 310 |  |  | 10 | 200 | 210 | 300 | 2.3077 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_225M | MUSHIPI | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-10 |  |  | Generator City |  | 16 |  | 8855 | 8973 | 118 | 216 | OK |  |  |  |  | 307 |  |  | 36 | 100 | 136 | 271 | 2.2966 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_120M | Garneton | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-10 |  |  | Gen Logic |  | 16 |  | 12756 | 12790 | 34 | 216 | OK |  |  |  |  | 422 |  |  | 337 | 200 | 537 | 85 | 2.5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_354A | Mufuchani | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Gen Only |  |  | Green Field |  | 2025-10-19 | 2025-10-11 |  |  | CK Works |  | 20 |  | 13042 | 13154 | 112 | 192 | OK |  |  |  |  | 400 |  |  | 13 | 200 | 213 | 387 | 3.4554 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_090M | Jambo Drive | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-14 |  |  | Gen Logic |  | 16 |  | 8610 | 8704 | 94 | 120 | OK |  |  |  |  | 444 |  |  | 12 | 200 | 212 | 432 | 4.5957 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_285A | KWACHA | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-16 |  |  | CK Works |  | 20 |  | 5418 | 5473 | 55 | 72 | OK |  |  |  |  | 421 |  |  | 228 | 100 | 328 | 193 | 3.5091 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_089M | Valley View | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-18 |  |  | ASCOT |  | 30 |  | 3083 | 3108 | 25 | 24 | inconsitent RH |  |  |  |  | 172 |  |  | 52 | 200 | 252 | 120 | 4.8 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_235M | KAWAMA KCC (Chimwemwe rlf | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-18 |  |  | CK Works |  | 20 |  | 9601 | 9615 | 14 | 24 | OK |  |  |  |  | 145 |  |  | 68 | 200 | 268 | 77 | 5.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_114M | Kamatipa North | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-16 |  |  | perkins |  | 15 |  | 1050 | 1107 | 57 | 72 | OK |  |  |  |  | 264 |  |  | 10 | 200 | 210 | 254 | 4.4561 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_103M | Kwacha central | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-15 |  |  | Gen Logic |  | 16 |  | 804 | 874 | 70 | 96 | OK |  |  |  |  | 331 |  |  | 20 | 200 | 220 | 311 | 4.4429 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_113M | Green Belt | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-14 |  |  | IMG |  | 20 |  | 10583 | 10673 | 90 | 120 | OK |  |  |  |  | 565 |  |  | 41 | 100 | 141 | 524 | 5.8222 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_123M | Mukuba University | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-13 |  |  | IMG |  | 15 |  | 11679 | 11755 | 76 | 144 | OK |  |  |  |  | 452 |  |  | 186 | 100 | 286 | 266 | 3.5 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_220A | ITIMPI | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-10 |  |  | MPI |  | 20 |  | 11439 | 11470 | 31 | 216 | OK |  |  |  |  | 351 |  |  | 262 | 100 | 362 | 89 | 2.871 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_017M | Overspill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-15 |  |  | Falcon |  | 20 |  | 8715 | 8805 | 90 | 96 | OK |  |  |  |  | 354 |  |  | 84 | 300 | 384 | 270 | 3 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_219M | PETAUKE CRESCENT | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-15 |  |  | CK Works |  | 20 |  | 3903 | 3986 | 83 | 96 | OK |  |  |  |  | 416 |  |  | 17 | 300 | 317 | 399 | 4.8072 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_257A | TWAPIA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-15 |  |  | CK Works |  | 20 |  | 12675 | 12756 | 81 | 96 | OK |  |  |  |  | 464 |  |  | 99 | 200 | 299 | 365 | 4.5062 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_291A | MWATAYANVWA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-15 |  |  | Gen Logic |  | 20 |  | 4479 | 4553 | 74 | 96 | OK |  |  |  |  | 398 |  |  | 65 | 300 | 365 | 333 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_233A | CHIPULUKUSU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-15 |  |  | Earth Technology |  | 15 |  | 4906 | 4965 | 59 | 96 | OK |  |  |  |  | 441 |  |  | 157 | 200 | 357 | 284 | 4.8136 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_222M | TWAPIA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-15 |  |  | Generator City |  | 13 |  | 990 | 1061 | 71 | 96 | OK |  |  |  |  | 366 |  |  | 82 | 100 | 182 | 284 | 4 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_041M | Kaniki | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-15 |  |  | GL Yanmar |  | 16 |  | 11321 | 11379 | 58 | 96 | OK |  |  |  |  | 329 |  |  | 166 | 100 | 266 | 163 | 2.8103 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_056M | Masangano | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-08 |  |  | GL Yanmar |  | 16 |  | 23080 | 23101 | 21 | 264 | OK |  |  |  |  | 385 |  |  | 290 | 300 | 590 | 95 | 4.5238 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_293A | MUSAKASONKA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-08 |  |  | Gen Logic |  | 20 |  | 1304 | 1405 | 101 | 264 | OK |  |  |  |  | 370 |  |  | 20 | 200 | 220 | 350 | 3.4653 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_001M | Kanini | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-15 |  |  | IMG |  | 20 |  | 7662 | 7724 | 62 | 96 | OK |  |  |  |  | 288 |  |  | 58 | 200 | 258 | 230 | 3.7097 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_207A | KANINI | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-15 |  |  | Gen Logic |  | 16 |  | 9159 | 9220 | 61 | 96 | OK |  |  |  |  | 263 |  |  | 49 | 150 | 199 | 214 | 3.5082 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_283A | MASALA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-15 |  |  | IMG |  | 20 |  | 7752 | 7821 | 69 | 96 | OK |  |  |  |  | 310 |  |  | 68 | 200 | 268 | 242 | 3.5072 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_148M | Kaloko Trust | GNM | Kasoma | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-13 |  |  | Yanmar |  | 16 |  | 7167 | 7229 | 62 | 144 | OK |  |  |  |  | 217 |  |  | 10 | 200 | 210 | 207 | 3.3387 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_156M | Mpongwe Turnoff | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-11 |  |  | Himoinsa |  | 30 |  | 6827 | 6865 | 38 | 192 | OK |  |  |  |  | 460 |  |  | 327 | 100 | 427 | 133 | 3.5 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_054M | Mikomfwa Market | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-15 |  |  | Yanmar |  | 16 |  | 12480 | 12506 | 26 | 96 | OK |  |  |  |  | 276 |  |  | 60 | 150 | 210 | 216 | 8.3077 | 2 | [5 empty] | 0 | [7 empty] | STOLEN FUEL REPORTED AT MIKOMFWA OB NUMBER 6909/25 | MERU |  | CAPTURED
IHS_CBT_210A | LUANSHYA | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-17 |  |  | CK Works |  | 20 |  | 7993 | 8013 | 20 | 48 | OK |  |  |  |  | 408 |  |  | 68 | 200 | 268 | 340 | 17 | 2.5 | [5 empty] | 0 | [7 empty] | STOLEN FUEL ABOUT 258 LITRES REPORTED AT LUANSHSYA POLICE OB NUMBER 10035/25 | MERU |  | CAPTURED
IHS_CBT_049M | Mikomfwa East | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-14 |  |  | Gen Logic |  | 16 |  | 6593 | 6625 | 32 | 120 | OK |  |  |  |  | 311 |  |  | 163 | 150 | 313 | 148 | 4.625 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_132M | Kalulushi West | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-15 |  |  | Gen Logic |  | 20 |  | 5832 | 5888 | 56 | 96 | OK |  |  |  |  | 446 |  |  | 138 | 300 | 438 | 308 | 5.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_117M | Chibote | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-15 |  |  | Gen Logic |  | 15 |  | 5901 | 5956 | 55 | 96 | OK |  |  |  |  | 332 |  |  | 123 | 200 | 323 | 209 | 3.8 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_206A | KALULUSHI | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-15 |  |  | IMG |  | 15 |  | 7493 | 7553 | 60 | 96 | OK |  |  |  |  | 378 |  |  | 105 | 200 | 305 | 273 | 4.55 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_267A | KALULUSHI EAST | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-15 |  |  | Gen Logic |  | 16 |  | 13764 | 13834 | 70 | 96 | OK |  |  |  |  | 414 |  |  | 125 | 200 | 325 | 289 | 4.1286 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_126M | Chibuluma | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-15 |  |  | Gen Logic |  | 20 |  | 3843 | 3922 | 79 | 96 | OK |  |  |  |  | 337 |  |  | 36 | 200 | 236 | 301 | 3.8101 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_301A | CHIBULUMA TOWN | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-15 |  |  | Gen Logic |  | 16 |  | 9674 | 9758 | 84 | 96 | OK |  |  |  |  | 378 |  |  | 58 | 300 | 358 | 320 | 3.8095 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_008M | Masala | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-15 |  |  | Generator City |  | 13 |  | 6482 | 6540 | 58 | 96 | OK |  |  |  |  | 272 |  |  | 51 | 200 | 251 | 221 | 3.8103 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_033M | Bwana Mukubwa | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-19 | 2025-10-15 |  |  | GL Yanmar |  | 16 |  | 978 | 1031 | 53 | 96 | OK |  |  |  |  | 399 |  |  | 155 | 150 | 305 | 244 | 4.6038 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_129M | Emerald Mine Lufwanyama | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-16 |  |  | Gen Logic |  | 15 |  | 25363 | 25400 | 37 | 96 | OK |  |  |  |  | 240 |  |  | 130 | 200 | 330 | 110 | 2.973 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_133M | Chibuluma Golf Club | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-19 |  |  | Powerol |  | 13 |  | 5380 | 5406 | 26 | 24 | inconsitent RH |  |  |  |  | 167 |  |  | 73 | 100 | 173 | 94 | 3.6154 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_021M | Sky ways | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-15 |  |  | CK Works |  | 20 |  | 7484 | 7551 | 67 | 120 | OK |  |  |  |  | 392 |  |  | 77 | 200 | 277 | 315 | 4.7015 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_251A | Kitwe Railways | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-18 |  |  | MPI |  | 20 |  | 5785 | 5822 | 37 | 48 | OK |  |  |  |  | 170 |  |  | 20 | 200 | 220 | 150 | 4.0541 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_237A | NKANA WEST | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-17 |  |  | Earth technology |  | 20 |  | 11869 | 11945 | 76 | 72 | inconsitent RH |  |  |  |  | 305 |  |  | 15 | 50 | 65 | 290 | 3.8158 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_094M | Kitwe Primary | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-16 |  |  | Gen Logic |  | 16 |  | 2626 | 2692 | 66 | 96 | OK |  |  |  |  | 286 |  |  | 38 | 150 | 188 | 248 | 3.7576 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_342A | Kantanta Street | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-17 |  |  | Gen Logic |  | 20 |  | 3902 | 3954 | 52 | 72 | OK |  |  |  |  | 320 |  |  | 109 | 50 | 159 | 211 | 4.0577 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_092M | Nkana Stadium | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-18 |  |  | Gen Logic |  | 16 |  | 5643 | 5664 | 21 | 48 | OK |  |  |  |  | 170 |  |  | 85 | 200 | 285 | 85 | 4.0476 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_074M | Luangwa | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-17 |  |  | Gen Logic |  | 16 |  | 4577 | 4637 | 60 | 72 | OK |  |  |  |  | 393 |  |  | 151 | 100 | 251 | 242 | 4.0333 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_355A | Ndeke Sub. A | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Gen Only |  |  | Green Field |  | 2025-10-20 | 2025-10-13 |  |  | CK Works |  | 20 |  | 14963 | 15043 | 80 | 168 | OK |  |  |  |  | 494 |  |  | 203 | 200 | 403 | 291 | 3.6375 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_218M | WUSAKILE POLICE CAMP | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-13 |  |  | Generator City |  | 16 |  | 7437 | 7507 | 70 | 168 | OK |  |  |  |  | 426 |  |  | 189 | 200 | 389 | 237 | 3.3857 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_094M | Kitwe Primary | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-20 |  |  | Gen Logic |  | 16 |  | 2692 | 2741 | 49 | 0 | inconsitent RH |  |  |  |  | 188 |  |  | 20 | 50 | 70 | 168 | 3.4286 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_078M | Bupe | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-11 |  |  | Gen Logic |  | 16 |  | 22987 | 23108 | 121 | 216 | OK |  |  |  |  | 359 |  |  | 20 | 100 | 120 | 339 | 2.8017 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_099M | Kitwe Town Center | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-15 |  |  | CDP |  | 15 |  | 9164 | 9226 | 62 | 120 | OK |  |  |  |  | 417 |  |  | 237 | 200 | 437 | 180 | 2.9032 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_217M | KITWE MAIN SCHOOL | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-15 |  |  | Generator City |  | 16 |  | 15994 | 16094 | 100 | 120 | OK |  |  |  |  | 344 |  |  | 16 | 200 | 216 | 328 | 3.28 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_113M | Green Belt | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-19 |  |  | IMG |  | 20 |  | 10673 | 10687 | 14 | 24 | OK |  |  |  |  | 141 |  |  | 59 | 300 | 359 | 82 | 5.8571 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_112M | Kamtipa | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-16 |  |  | Gen Logic |  | 16 |  | 519 | 569 | 50 | 96 | OK |  |  |  |  | 422 |  |  | 207 | 200 | 407 | 215 | 4.3 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_116M | Twatacha | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-13 |  |  | Gen Logic |  | 16 |  | 493 | 517 | 24 | 168 | OK |  |  |  |  | 443 |  |  | 349 | 200 | 549 | 94 | 3.9167 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_121M | Ichipe | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-11 |  |  | IHS_CBT_121M |  | 15 |  | 14170 | 14276 | 106 | 216 | OK |  |  |  |  | 515 |  |  | 101 | 200 | 301 | 414 | 3.9057 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_098M | Bulangililo | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-15 |  |  | Gen Logic |  | 16 |  | 8255 | 8362 | 107 | 120 | OK |  |  |  |  | 401 |  |  | 75 | 200 | 275 | 326 | 3.0467 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_241A | BULANGILILO | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-10 |  |  | perkins |  | 20 |  | 3174 | 3217 | 43 | 240 | OK |  |  |  |  | 420 |  |  | 269 | 200 | 469 | 151 | 3.5116 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_093M | Kwacha East | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-10 |  |  | Gen Logic |  | 30 |  | 166 | 190 | 24 | 240 | OK |  |  |  |  | 412 |  |  | 235 | 200 | 435 | 177 | 7.375 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_351A | Riverside Congo Way | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-18 |  |  | CK Works |  | 20 |  | 5990 | 6028 | 38 | 48 | OK |  |  |  |  | 241 |  |  | 41 | 200 | 241 | 200 | 5.2632 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_080M | Kalambo | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-15 |  |  | Gen Logic |  | 16 |  | 6629 | 6691 | 62 | 120 | OK |  |  |  |  | 553 |  |  | 283 | 200 | 483 | 270 | 4.3548 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_269A | SOSOLISO | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-16 |  |  | Jiuan |  | 15 |  | 5633 | 5701 | 68 | 96 | OK |  |  |  |  | 354 |  |  | 129 | 50 | 179 | 225 | 3.3088 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_087M | Lulamba School | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-12 |  |  | perkins |  | 20 |  | 259 | 280 | 21 | 192 | OK |  |  |  |  | 238 |  |  | 154 | 200 | 354 | 84 | 4 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-18 |  |  | GL Yanmar |  | 20 |  | 374 | 419 | 45 | 48 | OK |  |  |  |  | 290 |  |  | 65 | 200 | 265 | 225 | 5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_025M | Pamozi Extension | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-16 |  |  | GL Yanmar |  | 16 |  | 3355 | 3480 | 125 | 96 | inconsitent RH |  |  |  |  | 553 |  |  | 200 | 200 | 400 | 353 | 2.824 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_037M | Minsundu | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-15 |  |  | GL Yanmar |  | 16 |  | FAULTY | FAULTY | #VALUE! | 120 | #VALUE! |  |  |  |  | 354 |  |  | 84 | 300 | 384 | 270 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | IHS PUMA |  | CAPTURED
IHS_CBT_011M | Monkey Mountain | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-09-02 |  |  | Green Power |  | 16 |  | FAULTY | FAULTY | #VALUE! | 1152 | #VALUE! |  |  |  |  | 100 |  |  | 0 | 200 | 200 | 100 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | IHS PUMA |  | CAPTURED
IHS_CBT_344A | Nkwazi 3G | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-15 |  |  | CK Works |  | 20 |  | 45837 | 45908 | 71 | 120 | OK |  |  |  |  | 513 |  |  | 193 | 300 | 493 | 320 | 4.507 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_017M | Overspill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-19 |  |  | Falcon |  | 20 |  | 8805 | 8841 | 36 | 24 | inconsitent RH |  |  |  |  | 384 |  |  | 0 | 50 | 50 | 384 | 10.6667 | 2.5 | [5 empty] | 0 | [7 empty] | Stolen fuel OB number will be shared soon | IHS PUMA |  | CAPTURED
IHS_CBT_252A | CHIFUBU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-16 |  |  | Gen Logic |  | 30 |  | 4204 | 4266 | 62 | 96 | OK |  |  |  |  | 370 |  |  | 72 | 300 | 372 | 298 | 4.8065 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_226A | SAKANIA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-15 |  |  | Gen Logic |  | 16 |  | 1849 | 1889 | 40 | 120 | OK |  |  |  |  | 444 |  |  | 340 | 100 | 440 | 104 | 2.6 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_216M | COOL BANANAS | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-15 |  |  | Generator City |  | 13 |  | 7905 | 7989 | 84 | 120 | OK |  |  |  |  | 536 |  |  | 330 | 200 | 530 | 206 | 2.4524 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_264A | NDOLA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-16 |  |  | Gen Logic |  | 16 |  | 6045 | 6105 | 60 | 96 | OK |  |  |  |  | 335 |  |  | 31 | 200 | 231 | 304 | 5.0667 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_361A | Mitengo TDRC | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-18 |  |  | CK Works |  | 20 |  | 5629 | 5683 | 54 | 48 | inconsitent RH |  |  |  |  | 438 |  |  | 195 | 200 | 395 | 243 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_252A | CHIFUBU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-20 |  |  | Gen Logic |  | 30 |  | 4266 | 4290 | 24 | 0 | inconsitent RH |  |  |  |  | 372 |  |  | 0 | 50 | 50 | 372 | 15.5 | 4.5 | [5 empty] | 0 | [7 empty] | Stolen fuel abiut 145 ltrs mattered reported at chifubu police ob number 6837/25 | IHS PUMA |  | CAPTURED
IHS_CBT_024M | Ndeke Township | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-17 |  |  | CK Works |  | 30 |  | 11661 | 11717 | 56 | 72 | OK |  |  |  |  | 482 |  |  | 174 | 300 | 474 | 308 | 5.5 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_006M | Lubuto Central | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-18 |  |  | Lamasat |  | 15 |  | 1127 | 1166 | 39 | 48 | OK |  |  |  |  | 152 |  |  | 5 | 200 | 205 | 147 | 3.7692 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_332A | Ndeke_Ndola | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Roof Top |  | 2025-10-20 | 2025-10-11 |  |  | 0 |  | 15 |  | 725 | 826 | 101 | 216 | OK |  |  |  |  | 320 |  |  | 31 | 300 | 331 | 289 | 2.8614 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_004M | Ndola T. Centre | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-16 |  |  | Falcon |  | 20 |  | 324 | 393 | 69 | 96 | OK |  |  |  |  | 385 |  |  | 53 | 100 | 153 | 332 | 4.8116 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_214A | NDOLA FRA SILOS | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Roof Top |  | 2025-10-20 | 2025-10-13 |  |  | Lamasat |  | 20 |  | 12885 | 12990 | 105 | 168 | OK |  |  |  |  | 469 |  |  | 154 | 300 | 454 | 315 | 3 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_022M | Kasembo | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-14 |  |  | Gen Logic |  | 20 |  | 6278 | 6339 | 61 | 144 | OK |  |  |  |  | 493 |  |  | 206 | 100 | 306 | 287 | 4.7049 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_034M | Mushili Baracks | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-11 |  |  | GL Yanmar |  | 15 |  | 27798 | 27896 | 98 | 216 | OK |  |  |  |  | 305 |  |  | 30 | 200 | 230 | 275 | 2.8061 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_027M | Kantolomba | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-17 |  |  | CK Works |  | 20 |  | 5601 | 5656 | 55 | 72 | OK |  |  |  |  | 421 |  |  | 113 | 300 | 413 | 308 | 5.6 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_020M | Mushili | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-14 |  |  | CK Works |  | 30 |  | 8488 | 8548 | 60 | 144 | OK |  |  |  |  | 353 |  |  | 112 | 200 | 312 | 241 | 4.0167 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_014M | Lubuto | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-18 |  |  | CK Works |  | 20 |  | 3874 | 3907 | 33 | 48 | OK |  |  |  |  | 316 |  |  | 160 | 200 | 360 | 156 | 4.7273 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_009M | Tazama Building | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Roof Top |  | 2025-10-20 | 2025-10-15 |  |  | IMG |  | 16 |  | 28987 | 29087 | 100 | 120 | OK |  |  |  |  | 393 |  |  | 124 | 300 | 424 | 269 | 2.69 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_220M | RAILWAY STATION | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-03 |  |  | CK Works |  | 20 |  | 7123 | 7207 | 84 | 408 | OK |  |  |  |  | 284 |  |  | 24 | 200 | 224 | 260 | 3.0952 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_224M | SKYWAYS KAPIRI ROAD | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-16 |  |  | Generator City |  | 13 |  | 4324 | 4396 | 72 | 96 | OK |  |  |  |  | 280 |  |  | 13 | 200 | 213 | 267 | 3.7083 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_360A | Hilcrest Extension | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-18 |  |  | CK Works |  | 20 |  | 10680 | 10708 | 28 | 48 | OK |  |  |  |  | 184 |  |  | 52 | 200 | 252 | 132 | 4.7143 | 5.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_232A | LUBUTO | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-17 |  |  | Gen Logic |  | 20 |  | 11107 | 11193 | 86 | 72 | inconsitent RH |  |  |  |  | 450 |  |  | 110 | 200 | 310 | 340 | 3.9535 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_010M | Kabushi | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-18 |  |  | IMG |  | 15 |  | 7694 | 7739 | 45 | 48 | OK |  |  |  |  | 268 |  |  | 98 | 200 | 298 | 170 | 3.7778 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_206A | KALULUSHI | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-19 |  |  | IMG |  | 15 |  | 7553 | 7569 | 16 | 24 | OK |  |  |  |  | 305 |  |  | 233 | 150 | 383 | 72 | 4.5 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_267A | KALULUSHI EAST | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-19 |  |  | Gen Logic |  | 16 |  | 13834 | 13854 | 20 | 24 | OK |  |  |  |  | 325 |  |  | 243 | 250 | 493 | 82 | 4.1 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_132M | Kalulushi West | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-19 |  |  | Gen Logic |  | 20 |  | 5888 | 5892 | 4 | 24 | OK |  |  |  |  | 438 |  |  | 416 | 100 | 516 | 22 | 5.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_134M | Kalulushi East | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-16 |  |  | CK Works |  | 20 |  | 8389 | 8458 | 69 | 96 | OK |  |  |  |  | 371 |  |  | 74 | 200 | 274 | 297 | 4.3043 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_126M | Chibuluma | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-19 |  |  | Gen Logic |  | 20 |  | 3922 | 3938 | 16 | 24 | OK |  |  |  |  | 236 |  |  | 175 | 100 | 275 | 61 | 3.8125 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_301A | CHIBULUMA TOWN | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-19 |  |  | Gen Logic |  | 16 |  | 9758 | 9784 | 26 | 24 | inconsitent RH |  |  |  |  | 358 |  |  | 259 | 150 | 409 | 99 | 3.8077 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_117M | Chibote | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-19 |  |  | Gen Logic |  | 15 |  | 5956 | 5974 | 18 | 24 | OK |  |  |  |  | 323 |  |  | 254 | 100 | 354 | 69 | 3.8333 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_146M | Miku Mining | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-16 |  |  | Gen Logic |  | 20 |  | 20569 | 20662 | 93 | 96 | OK |  |  |  |  | 305 |  |  | 15 | 200 | 215 | 290 | 3.1183 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_241M | Kagem mine | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-17 |  |  | perkins |  | 20 |  | 14285 | 14314 | 29 | 72 | OK |  |  |  |  | 110 |  |  | 15 | 200 | 215 | 95 | 3.2759 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_167M | Kafubu | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-13 |  |  | LISTER PETTER |  | 16 |  | FAULTY | FAULTY | #VALUE! | 168 | #VALUE! |  |  |  |  | 280 |  |  | 5 | 100 | 105 | 275 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | MERU |  | CAPTURED
IHS_CBT_155M | St. Joseph | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-13 |  |  | Gen Logic |  | 16 |  | 6587 | 6698 | 111 | 168 | OK |  |  |  |  | 345 |  |  | 35 | 200 | 235 | 310 | 2.7928 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_008M | Masala | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-19 |  |  | Generator City |  | 13 |  | 6540 | 6562 | 22 | 24 | OK |  |  |  |  | 251 |  |  | 167 | 200 | 367 | 84 | 3.8182 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_289A | BUPE | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-10-11 |  |  | Gen Logic |  | 15 |  | 13238 | 13315 | 77 | 216 | OK |  |  |  |  | 290 |  |  | 20 | 150 | 170 | 270 | 3.5065 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_070M | Kauanga Basic | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-20 | 2025-09-20 |  |  | Earth technology |  | 20 |  | 12630 | 12636 | 6 | 720 | OK |  |  |  |  | 260 |  |  | 245 | 100 | 345 | 15 | 2.5 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_320A | Silangwa (Ndola Rural_1) | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-21 | 2025-09-03 |  |  | GNM |  | 15 |  | 2302 | 2423 | 121 | 1152 | OK |  |  |  |  | 533 |  |  | 30 | 200 | 230 | 503 | 4.157 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_234A | CHIWALA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-21 | 2025-10-16 |  |  | Gen Logic |  | 20 |  | 21847 | 21887 | 40 | 120 | OK |  |  |  |  | 400 |  |  | 246 | 200 | 446 | 154 | 3.85 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_306A | TUG-ARGAN | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-21 | 2025-10-18 |  |  | Yanmar |  | 16 |  | 13114 | 13149 | 35 | 72 | OK |  |  |  |  | 211 |  |  | 103 | 200 | 303 | 108 | 3.0857 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_085M | Dangote | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-21 | 2025-10-16 |  |  | Earth technology |  | 13 |  | 8052 | 8108 | 56 | 120 | OK |  |  |  |  | 313 |  |  | 142 | 200 | 342 | 171 | 3.0536 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_045M | Tuckugan | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-21 | 2025-10-11 |  |  | GL Yanmar |  | 16 |  | FAULTY | FAULTY | #VALUE! | 240 | #VALUE! |  |  |  |  | 220 |  |  | 10 | 200 | 210 | 210 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | MERU |  | CAPTURED
IHS_CBT_346A | Nilkant Mine | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Solar-Gen |  |  | Green Field |  | 2025-10-21 | 2025-10-13 |  |  | CK Works |  | 20 |  | 11463 | 11527 | 64 | 192 | OK |  |  |  |  | 424 |  |  | 180 | 100 | 280 | 244 | 3.8125 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_253A | ITAWA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-21 | 2025-10-17 |  |  | Gen Logic |  | 20 |  | 10803 | 10866 | 63 | 96 | OK |  |  |  |  | 332 |  |  | 92 | 200 | 292 | 240 | 3.8095 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_040M | Seed Of Hope | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-21 | 2025-10-13 |  |  | Lamasat |  | 15 |  | 25154 | 25195 | 41 | 192 | OK |  |  |  |  | 268 |  |  | 10 | 200 | 210 | 258 | 6.2927 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_362A | Ndola Central Police | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-21 | 2025-10-18 |  |  | CK Works |  | 20 |  | FAULTY | FAULTY | #VALUE! | 72 | #VALUE! |  |  |  |  | 205 |  |  | 5 | 70 | 75 | 200 | #VALUE! | 4.5 | [5 empty] | 0 | [7 empty] | faulty controller | MERU |  | CAPTURED
IHS_CBT_017M | Overspill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-21 | 2025-10-20 |  |  | Falcon |  | 20 |  | 8841 | 8853 | 12 | 24 | OK |  |  |  |  | 50 |  |  | 14 | 50 | 64 | 36 | 3 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_335A | Daag Hamershold | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-21 | 2025-10-12 |  |  | LAMASAT |  | 15 |  | 7846 | 7875 | 29 | 216 | OK |  |  |  |  | 147 |  |  | 74 | 200 | 274 | 73 | 2.5172 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_018M | Nkwanzi | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-21 | 2025-10-18 |  |  | CK Works |  | 20 |  | 1488 | 1563 | 75 | 72 | inconsitent RH |  |  |  |  | 358 |  |  | 20 | 50 | 70 | 338 | 4.5067 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_222M | TWAPIA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-21 | 2025-10-19 |  |  | Generator City |  | 13 |  | 1061 | 1101 | 40 | 48 | OK |  |  |  |  | 182 |  |  | 22 | 20 | 42 | 160 | 4 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_245A | NORTHRISE | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-21 | 2025-10-18 |  |  | Lamasat |  | 20 |  | 8714 | 8770 | 56 | 72 | OK |  |  |  |  | 319 |  |  | 67 | 20 | 87 | 252 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_025M | Pamozi Extension | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-21 | 2025-10-20 |  |  | GL Yanmar |  | 16 |  | 3450 | 3472 | 22 | 24 | OK |  |  |  |  | 400 |  |  | 0 | 22 | 22 | 400 | 18.1818 | 2 | [5 empty] | 0 | [7 empty] | STOLEN FUEL | TOTAL |  | CAPTURED
IHS_CBT_005M | Premium Plaza | CCS | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Roof Top |  | 2025-10-21 | 2025-10-17 |  |  | N/A |  | N/A |  | 8734 | 8832 | 98 | 96 | inconsitent RH |  |  |  |  | 336 |  |  | 2 | 20 | 22 | 334 | 3.4082 | N/A | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_359A | Cross Crescent | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-21 | 2025-10-16 |  |  | CK Works |  | 20 |  | 5731 | 5781 | 50 | 120 | OK |  |  |  |  | 295 |  |  | 70 | 20 | 90 | 225 | 4.5 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_229A | CHIMWEMWE | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-21 | 2025-10-18 |  |  | Gen Logic |  | 20 |  | 448 | 500 | 52 | 72 | OK |  |  |  |  | 338 |  |  | 38 | 50 | 88 | 300 | 5.7692 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_090M | Jambo Drive | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-21 | 2025-10-19 |  |  | Gen Logic |  | 16 |  | 8704 | 8743 | 39 | 48 | OK |  |  |  |  | 212 |  |  | 25 | 50 | 75 | 187 | 4.7949 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_237A | NKANA WEST | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-21 | 2025-10-20 |  |  | Earth technology |  | 20 |  | 11945 | 11957 | 12 | 24 | OK |  |  |  |  | 65 |  |  | 19 | 150 | 169 | 46 | 3.8333 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_044M | Kafubu Block | GNM | SAMUEL | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-15 |  |  | Yanmar |  | 16 |  | 17865 | 17975 | 110 | 168 | OK |  |  |  |  | 322 |  |  | 20 | 100 | 120 | 302 | 2.7455 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_314A | KAFUBU BLOCK | GNM | Royd | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-15 |  |  | CK Works |  | 20 |  | 7558 | 7652 | 94 | 168 | OK |  |  |  |  | 400 |  |  | 71 | 200 | 271 | 329 | 3.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_058M | Mikomfwa | GNM | SAMUEL | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-14 |  |  | Gen Logic |  | 16 |  | 7823 | 7953 | 130 | 192 | OK |  |  |  |  | 343 |  |  | 0 | 100 | 100 | 343 | 2.6385 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_235M | KAWAMA KCC (Chimwemwe rlf | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-19 |  |  | CK Works |  | 20 |  | 9615 | 9659 | 44 | 72 | OK |  |  |  |  | 268 |  |  | 41 | 100 | 141 | 227 | 5.1591 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_114M | Kamatipa North | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-19 |  |  | perkins |  | 15 |  | 1107 | 1149 | 42 | 72 | OK |  |  |  |  | 210 |  |  | 10 | 100 | 110 | 200 | 4.7619 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_241A | BULANGILILO | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-20 |  |  | perkins |  | 20 |  | 3217 | 3228 | 11 | 48 | OK |  |  |  |  | 469 |  |  | 5 | 100 | 105 | 464 | 42.1818 | 2.5 | [5 empty] | 0 | [7 empty] | STOLEN FUEL REPORTED AT BULANGILILO ABOUT 425 LTRS OB NUMBER 7308/25 | TOTAL |  | CAPTURED
IHS_CBT_090M | Jambo Drive | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-21 |  |  | Gen Logic |  | 16 |  | 8743 | 8755 | 12 | 24 | OK |  |  |  |  | 75 |  |  | 25 | 100 | 125 | 50 | 4.1667 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_089M | Valley View | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-19 |  |  | ASCOT |  | 30 |  | 3108 | 3163 | 55 | 72 | OK |  |  |  |  | 252 |  |  | 22 | 100 | 122 | 230 | 4.1818 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_229A | CHIMWEMWE | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-21 |  |  | Gen Logic |  | 20 |  | 500 | 513 | 13 | 24 | OK |  |  |  |  | 88 |  |  | 19 | 100 | 119 | 69 | 5.3077 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_296A | KAMUNGA | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-18 |  |  | Gen Logic |  | 16 |  | 6287 | 6357 | 70 | 96 | OK |  |  |  |  | 273 |  |  | 5 | 50 | 55 | 268 | 3.8286 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_222A | CHAMBOLI | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-19 |  |  | Gen Logic |  | 30 |  | 308 | 346 | 38 | 72 | OK |  |  |  |  | 247 |  |  | 68 | 150 | 218 | 179 | 4.7105 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_300A | LUBAMBE | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-15 |  |  | Jiuan |  | 30 |  | 5179 | 5276 | 97 | 168 | OK |  |  |  |  | 441 |  |  | 20 | 50 | 70 | 421 | 4.3402 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_084M | Kitwe ZNS | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-14 |  |  | CDP |  | 15 |  | 18227 | 18366 | 139 | 192 | OK |  |  |  |  | 366 |  |  | 10 | 50 | 60 | 356 | 2.5612 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_217M | KITWE MAIN SCHOOL | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-20 |  |  | Generator City |  | 16 |  | 16094 | 16127 | 33 | 48 | OK |  |  |  |  | 216 |  |  | 101 | 50 | 151 | 115 | 3.4848 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_103M | Kwacha central | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-19 |  |  | Gen Logic |  | 16 |  | 874 | 925 | 51 | 72 | OK |  |  |  |  | 220 |  |  | 13 | 100 | 113 | 207 | 4.0588 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_285A | KWACHA | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-19 |  |  | CK Works |  | 20 |  | 5473 | 5530 | 57 | 72 | OK |  |  |  |  | 328 |  |  | 177 | 50 | 227 | 151 | 2.6491 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_351A | Riverside Congo Way | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-20 |  |  | CK Works |  | 20 |  | 6028 | 6065 | 37 | 48 | OK |  |  |  |  | 241 |  |  | 57 | 100 | 157 | 184 | 4.973 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_269A | SOSOLISO | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-20 |  |  | Jiuan |  | 15 |  | 5701 | 5728 | 27 | 48 | OK |  |  |  |  | 179 |  |  | 98 | 100 | 198 | 81 | 3 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_354A | Mufuchani | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Gen Only |  |  | Green Field |  | 2025-10-22 | 2025-10-19 |  |  | CK Works |  | 20 |  | 13144 | 13220 | 76 | 72 | inconsitent RH |  |  |  |  | 213 |  |  | 13 | 150 | 163 | 200 | 2.6316 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_283A | MASALA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-19 |  |  | IMG |  | 20 |  | 7821 | 7876 | 55 | 72 | OK |  |  |  |  | 268 |  |  | 75 | 200 | 275 | 193 | 3.5091 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_016M | Itawa | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-17 |  |  | Vitalgen |  | 30 |  | 4745 | 4798 | 53 | 120 | OK |  |  |  |  | 290 |  |  | 93 | 200 | 293 | 197 | 3.717 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_362A | Ndola Central Police | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-21 |  |  | CK Works |  | 20 |  | FAULTY | 12189 | #VALUE! | 24 | #VALUE! |  |  |  |  | 75 |  |  | 75 | 100 | 175 | 0 | #VALUE! | 4.5 | [5 empty] | 0 | [7 empty] | faulty controller | TOTAL |  | CAPTURED
IHS_CBT_349A | Kafubu Mall | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-15 |  |  | Gen Logic |  | 16 |  | 16280 | 16363 | 83 | 168 | OK |  |  |  |  | 410 |  |  | 120 | 200 | 320 | 290 | 3.494 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_004M | Ndola T. Centre | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-20 |  |  | Falcon |  | 20 |  | 393 | 422 | 29 | 48 | OK |  |  |  |  | 153 |  |  | 16 | 200 | 216 | 137 | 4.7241 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_338A | Musa Kasonka_3_Rlf | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-16 |  |  | CK Works |  | 20 |  | 11121 | 11197 | 76 | 144 | OK |  |  |  |  | 362 |  |  | 80 | 100 | 180 | 282 | 3.7105 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_035M | Kaloko | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-17 |  |  | Himoinsa |  | 30 |  | 9514 | 9583 | 69 | 120 | OK |  |  |  |  | 298 |  |  | 10 | 100 | 110 | 288 | 4.1739 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_127M | Kalulushi | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-16 |  |  | Himoinsa |  | 30 |  | 10874 | 10968 | 94 | 144 | OK |  |  |  |  | 447 |  |  | 71 | 100 | 171 | 376 | 4 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_134M | Kalulushi East | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-20 |  |  | CK Works |  | 20 |  | 8458 | 8505 | 47 | 48 | OK |  |  |  |  | 274 |  |  | 71 | 100 | 171 | 203 | 4.3191 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_118M | Kamaronde | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-14 |  |  | CK Works |  | 20 |  | 3158 | 3246 | 88 | 192 | OK |  |  |  |  | 518 |  |  | 166 | 100 | 266 | 352 | 4 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_238M | NAPSA Complex | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-14 |  |  | MPMC |  | 15 |  | 8636 | 8755 | 119 | 192 | OK |  |  |  |  | 401 |  |  | 7 | 100 | 107 | 394 | 3.3109 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_345A | Ndeke Changachanga south 3G | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-19 |  |  | Gen Logic |  | 20 |  | 13637 | 13679 | 42 | 72 | OK |  |  |  |  | 205 |  |  | 68 | 50 | 118 | 137 | 3.2619 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_305A | LUANGWA KAFUE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-19 |  |  | Yanmar |  | 16 |  | 1008 | 1061 | 53 | 72 | OK |  |  |  |  | 347 |  |  | 347 | 50 | 397 | 0 | 0 | 2 | [5 empty] | 0 | [8 empty] | TOTAL |  | CAPTURED
IHS_CBT_074M | Luangwa | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-20 |  |  | Gen Logic |  | 16 |  | 4637 | 4669 | 32 | 48 | OK |  |  |  |  | 251 |  |  | 126 | 50 | 176 | 125 | 3.9062 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_075M | Ndeke Changachanga | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-19 |  |  | Gen Logic |  | 20 |  | 3761 | 3809 | 48 | 72 | OK |  |  |  |  | 286 |  |  | 47 | 100 | 147 | 239 | 4.9792 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_244A | NDEKE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-19 |  |  | Earth technology |  | 15 |  | 4000 | 4048 | 48 | 72 | OK |  |  |  |  | 276 |  |  | 85 | 100 | 185 | 191 | 3.9792 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_079M | Ndeke | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-19 |  |  | CK Works |  | 20 |  | 10093 | 10133 | 40 | 72 | OK |  |  |  |  | 258 |  |  | 54 | 150 | 204 | 204 | 5.1 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_356A | New Ndeke Village | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-19 |  |  | CK Works |  | 20 |  | 996 | 1044 | 48 | 72 | OK |  |  |  |  | 285 |  |  | 52 | 200 | 252 | 233 | 4.8542 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_082M | Ndeke Extension | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-19 |  |  | Gen Logic |  | 20 |  | 7556 | 7593 | 37 | 72 | OK |  |  |  |  | 301 |  |  | 105 | 150 | 255 | 196 | 5.2973 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_083M | Nkana East | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-17 |  |  | Gen Logic |  | 16 |  | 3992 | 4073 | 81 | 120 | OK |  |  |  |  | 460 |  |  | 123 | 150 | 273 | 337 | 4.1605 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_353A | Court Barrifs | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-18 |  |  | CK Works |  | 20 |  | 10600 | 10658 | 58 | 96 | OK |  |  |  |  | 296 |  |  | 63 | 100 | 163 | 233 | 4.0172 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_228A | MINDOLO | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-17 |  |  | Earth technology |  | 20 |  | 11246 | 11365 | 119 | 120 | OK |  |  |  |  | 351 |  |  | 28 | 100 | 128 | 323 | 2.7143 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_297A | KITWE POLICE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-15 |  |  | Gen Logic |  | 16 |  | 7641 | 7772 | 131 | 168 | OK |  |  |  |  | 428 |  |  | 61 | 100 | 161 | 367 | 2.8015 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_299A | KITWE POST OFFICE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Roof Top |  | 2025-10-22 | 2025-10-16 |  |  | Gen Logic |  | 17 |  | 11395 | 11457 | 62 | 144 | OK |  |  |  |  | 200 |  |  | 61 | 100 | 161 | 139 | 2.2419 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_081M | Chamboli | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-16 |  |  | Gen Logic |  | 16 |  | 13389 | 13499 | 110 | 144 | OK |  |  |  |  | 311 |  |  | 29 | 100 | 129 | 282 | 2.5636 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_225M | MUSHIPI | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-19 |  |  | Generator City |  | 16 |  | 8973 | 9017 | 44 | 72 | OK |  |  |  |  | 136 |  |  | 33 | 100 | 133 | 103 | 2.3409 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_250A | SOB | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-19 |  |  | Gen Logic |  | 15 |  | 19533 | 19617 | 84 | 72 | inconsitent RH |  |  |  |  | 210 |  |  | 29 | 100 | 129 | 181 | 2.1548 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_251A | Kitwe Railways | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-20 |  |  | MPI |  | 20 |  | 5822 | 5867 | 45 | 48 | OK |  |  |  |  | 220 |  |  | 41 | 150 | 191 | 179 | 3.9778 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_088M | Geddis | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-17 |  |  | CDP |  | 13 |  | 12032 | 12157 | 125 | 120 | inconsitent RH |  |  |  |  | 407 |  |  | 87 | 50 | 137 | 320 | 2.56 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_243A | GEDDIS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-17 |  |  | Gen Logic |  | 15 |  | 17941 | 18015 | 74 | 120 | OK |  |  |  |  | 346 |  |  | 75 | 100 | 175 | 271 | 3.6622 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_017M | Overspill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-21 |  |  | Falcon |  | 20 |  | 8853 | 8868 | 15 | 24 | OK |  |  |  |  | 64 |  |  | 19 | 100 | 119 | 45 | 3 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_025M | Pamozi Extension | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-21 |  |  | GL Yanmar |  | 16 |  | 3472 | 3477 | 5 | 24 | OK |  |  |  |  | 22 |  |  | 7 | 50 | 57 | 15 | 3 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-20 |  |  | GL Yanmar |  | 20 |  | 419 | 462 | 43 | 48 | OK |  |  |  |  | 265 |  |  | 50 | 100 | 150 | 215 | 5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_245A | NORTHRISE | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-21 |  |  | Lamasat |  | 20 |  | 8770 | 8772 | 2 | 24 | OK |  |  |  |  | 87 |  |  | 78 | 100 | 178 | 9 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_252A | CHIFUBU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-20 |  |  | Gen Logic |  | 30 |  | 4290 | 4300 | 10 | 48 | OK |  |  |  |  | 50 |  |  | 2 | 100 | 102 | 48 | 4.8 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_013M | Dola Hill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-18 |  |  | Himoinsa |  | 30 |  | 5827 | 5883 | 56 | 96 | OK |  |  |  |  | 505 |  |  | 169 | 200 | 369 | 336 | 6 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_029M | Zafico | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-18 |  |  | Green Power |  | 15 |  | 3404 | 3456 | 52 | 96 | OK |  |  |  |  | 250 |  |  | 73 | 50 | 123 | 177 | 3.4038 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_018M | Nkwanzi | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-21 |  |  | CK Works |  | 20 |  | 1563 | 1575 | 12 | 24 | OK |  |  |  |  | 70 |  |  | 16 | 100 | 116 | 54 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_264A | NDOLA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-20 |  |  | Gen Logic |  | 16 |  | 6105 | 6152 | 47 | 48 | OK |  |  |  |  | 231 |  |  | 21 | 50 | 71 | 210 | 4.4681 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_025M | Pamozi Extension | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-22 |  |  | GL Yanmar |  | 16 |  | 3477 | 3497 | 20 | 0 | inconsitent RH |  |  |  |  | 57 |  |  | 3 | 50 | 53 | 54 | 2.7 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_005M | Premium Plaza | CCS | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Roof Top |  | 2025-10-22 | 2025-10-21 |  |  | N/A |  | N/A |  | 8832 | 8839 | 7 | 24 | OK |  |  |  |  | 22 |  |  | 1 | 150 | 151 | 21 | 3 | N/A | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_359A | Cross Crescent | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-21 |  |  | CK Works |  | 20 |  | 5781 | 5783 | 2 | 24 | OK |  |  |  |  | 90 |  |  | 80 | 150 | 230 | 10 | 5 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_219M | PETAUKE CRESCENT | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-19 |  |  | CK Works |  | 20 |  | 3986 | 4041 | 55 | 72 | OK |  |  |  |  | 317 |  |  | 53 | 200 | 253 | 264 | 4.8 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_291A | MWATAYANVWA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-19 |  |  | Gen Logic |  | 20 |  | 4553 | 4601 | 48 | 72 | OK |  |  |  |  | 365 |  |  | 134 | 100 | 234 | 231 | 4.8125 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_233A | CHIPULUKUSU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-19 |  |  | Earth Technology |  | 15 |  | 4965 | 5017 | 52 | 72 | OK |  |  |  |  | 357 |  |  | 101 | 150 | 251 | 256 | 4.9231 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-22 |  |  | GL Yanmar |  | 20 |  | 462 | 473 | 11 | 0 | inconsitent RH |  |  |  |  | 150 |  |  | 0 | 50 | 50 | 150 | 13.6364 | 2 | [5 empty] | 0 | [7 empty] | Stolen fuel about 100 litres and a generator starter battery the matter has been reported at kawama police post OB number #2255/25 | SAHARA |  | CAPTURED
IHS_CBT_252A | CHIFUBU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-22 |  |  | Gen Logic |  | 30 |  | 4300 | 4304 | 4 | 0 | inconsitent RH |  |  |  |  | 102 |  |  | 0 | 50 | 50 | 102 | 25.5 | 4.5 | [5 empty] | 0 | [7 empty] | Stolen fuel abiut 145 ltrs mattered reported at chifubu police ob number 6837/25 | SAHARA |  | CAPTURED
IHS_CBT_264A | NDOLA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-22 |  |  | Gen Logic |  | 16 |  | 6152 | 6162 | 10 | 0 | inconsitent RH |  |  |  |  | 71 |  |  | 19 | 50 | 69 | 52 | 5.2 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_222M | TWAPIA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-21 |  |  | Generator City |  | 13 |  | 1101 | 1109 | 8 | 24 | OK |  |  |  |  | 42 |  |  | 10 | 50 | 60 | 32 | 4 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_226M | CHIFUBU WEST | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-18 |  |  | Generator City |  | 13 |  | 19159 | 19255 | 96 | 96 | OK |  |  |  |  | 386 |  |  | 0 | 100 | 100 | 386 | 4.0208 | 2 | [5 empty] | 0 | [7 empty] | STOLEN FUEL OB NUMBER 7066/25 | SAHARA |  | CAPTURED
IHS_CBT_338A | Musa Kasonka_3_Rlf | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-22 | 2025-10-17 |  |  | CK Works |  | 20 |  | 11121 | 11197 | 76 | 120 | OK |  |  |  |  | 362 |  |  | 80 | 100 | 180 | 282 | 3.7105 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_021M | Sky ways | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-20 |  |  | CK Works |  | 20 |  | 7551 | 7599 | 48 | 72 | OK |  |  |  |  | 277 |  |  | 55 | 100 | 155 | 222 | 4.625 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_265A | NEW TOWN | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-15 |  |  | Gen Logic |  | 16 |  | 1798 | 1866 | 68 | 192 | OK |  |  |  |  | 314 |  |  | 89 | 100 | 189 | 225 | 3.3088 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_043M | Fisenge | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-17 |  |  | Gen Logic |  | 16 |  | FAULTY | FAULTY | #VALUE! | 144 | #VALUE! |  |  |  |  | 327 |  |  | 153 | 100 | 253 | 174 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | IHS PUMA |  | CAPTURED
IHS_CBT_048M | Kamirenda Extension | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-17 |  |  | Vitalgen |  | 20 |  | 9766 | 9835 | 69 | 144 | OK |  |  |  |  | 360 |  |  | 84 | 100 | 184 | 276 | 4 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_050M | Luanshya Town Center | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-17 |  |  | Gen Logic |  | 20 |  | 8527 | 8581 | 54 | 144 | OK |  |  |  |  | 294 |  |  | 45 | 150 | 195 | 249 | 4.6111 | [6 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_227M | LUANSHYA EAST | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-17 |  |  | Generator City |  | 16 |  | 7663 | 7712 | 49 | 144 | OK |  |  |  |  | 345 |  |  | 129 | 100 | 229 | 216 | 4.4082 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_211A | MPATAMATU | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-15 |  |  | IMG |  | 20 |  | 7896 | 7949 | 53 | 192 | OK |  |  |  | 383 | 383 |  |  | 10 | 50 | 60 | 373 | 7.0377 | 2.5 | [5 empty] | 0 | [7 empty] | STOLEN FUEL REPORTED AT MPATAMATU OB NUMBER 4829/2025 | IHS PUMA |  | CAPTURED
IHS_CBT_054M | Mikomfwa Market | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-19 |  |  | Yanmar |  | 16 |  | 12506 | 12563 | 57 | 96 | OK |  |  |  |  | 210 |  |  | 21 | 100 | 121 | 189 | 3.3158 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_065M | Mpatamato East | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-16 |  |  | Yanmar |  | 16 |  | 8550 | 8626 | 76 | 168 | OK |  |  |  |  | 221 |  |  | 0 | 50 | 50 | 221 | 2.9079 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_161M | Mikata Mpongwe | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Solar-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-17 |  |  | IMG |  | 20 |  | 9871 | 9936 | 65 | 144 | OK |  |  |  |  | 230 |  |  | 10 | 150 | 160 | 220 | 3.3846 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_041M | Kaniki | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-19 |  |  | GL Yanmar |  | 16 |  | 11379 | 11460 | 81 | 96 | OK |  |  |  |  | 266 |  |  | 39 | 100 | 139 | 227 | 2.8025 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_257A | TWAPIA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-19 |  |  | CK Works |  | 20 |  | 12756 | 12828 | 72 | 96 | OK |  |  |  |  | 299 |  |  | 4 | 100 | 104 | 295 | 4.0972 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_018M | Nkwanzi | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-22 |  |  | CK Works |  | 20 |  | 1575 | 1592 | 17 | 24 | OK |  |  |  |  | 116 |  |  | 39 | 100 | 139 | 77 | 4.5294 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_222M | TWAPIA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-22 |  |  | Generator City |  | 13 |  | 1109 | 1120 | 11 | 24 | OK |  |  |  |  | 60 |  |  | 16 | 100 | 116 | 44 | 4 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_252A | CHIFUBU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-22 |  |  | Gen Logic |  | 30 |  | 4304 | 4322 | 18 | 24 | OK |  |  |  |  | 50 |  |  | 2 | 100 | 102 | 48 | 2.6667 | 4.5 | [5 empty] | 0 | [7 empty] | Stolen fuel abiut 145 ltrs mattered reported at chifubu police ob number 6837/25 | TOTAL |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-22 |  |  | GL Yanmar |  | 20 |  | 473 | 483 | 10 | 24 | OK |  |  |  |  | 50 |  |  | 1 | 50 | 51 | 49 | 4.9 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_029M | Zafico | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-22 |  |  | Green Power |  | 15 |  | 3456 | 3469 | 13 | 24 | OK |  |  |  |  | 123 |  |  | 78 | 50 | 128 | 45 | 3.4615 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_025M | Pamozi Extension | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-22 |  |  | GL Yanmar |  | 16 |  | 3497 | 3506 | 9 | 24 | OK |  |  |  |  | 53 |  |  | 27 | 50 | 77 | 26 | 2.8889 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_017M | Overspill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-22 |  |  | Falcon |  | 20 |  | 8868 | 8892 | 24 | 24 | OK |  |  |  |  | 119 |  |  | 47 | 100 | 147 | 72 | 3 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-23 |  |  | GL Yanmar |  | 20 |  | 483 | 490 | 7 | 0 | inconsitent RH |  |  |  |  | 51 |  |  | 16 | 100 | 116 | 35 | 5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_226M | CHIFUBU WEST | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-22 |  |  | Generator City |  | 13 |  | 19255 | 19287 | 32 | 24 | inconsitent RH |  |  |  |  | 100 |  |  | 16 | 100 | 116 | 84 | 2.625 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_089M | Valley View | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-22 |  |  | ASCOT |  | 30 |  | 3163 | 3179 | 16 | 24 | OK |  |  |  |  | 122 |  |  | 41 | 200 | 241 | 81 | 5.0625 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_235M | KAWAMA KCC (Chimwemwe rlf | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-22 |  |  | CK Works |  | 20 |  | 9659 | 9677 | 18 | 24 | OK |  |  |  |  | 141 |  |  | 41 | 100 | 141 | 100 | 5.5556 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_296A | KAMUNGA | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-22 |  |  | Gen Logic |  | 16 |  | 6357 | 6372 | 15 | 24 | OK |  |  |  |  | 55 |  |  | 5 | 100 | 105 | 50 | 3.3333 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_300A | LUBAMBE | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-22 |  |  | Jiuan |  | 30 |  | 5275 | 5284 | 9 | 24 | OK |  |  |  |  | 70 |  |  | 25 | 100 | 125 | 45 | 5 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_115M | Mindolo | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-18 |  |  | Gen Logic |  | 16 |  | 7525 | 7599 | 74 | 120 | OK |  |  |  |  | 229 |  |  | 10 | 150 | 160 | 219 | 2.9595 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_229A | CHIMWEMWE | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-22 |  |  | Gen Logic |  | 20 |  | 513 | 528 | 15 | 24 | OK |  |  |  |  | 119 |  |  | 38 | 200 | 238 | 81 | 5.4 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_113M | Green Belt | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-20 |  |  | IMG |  | 20 |  | 10687 | 10726 | 39 | 72 | OK |  |  |  |  | 359 |  |  | 126 | 100 | 226 | 233 | 5.9744 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_241A | BULANGILILO | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-22 |  |  | perkins |  | 20 |  | 3228 | 3256 | 28 | 24 | inconsitent RH |  |  |  |  | 105 |  |  | 5 | 50 | 55 | 100 | 3.5714 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_103M | Kwacha central | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-22 |  |  | Gen Logic |  | 16 |  | 925 | 949 | 24 | 24 | OK |  |  |  |  | 113 |  |  | 13 | 50 | 63 | 100 | 4.1667 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_114M | Kamatipa North | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-22 |  |  | perkins |  | 15 |  | 1149 | 1174 | 25 | 24 | inconsitent RH |  |  |  |  | 110 |  |  | 10 | 100 | 110 | 100 | 4 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_090M | Jambo Drive | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-22 |  |  | Gen Logic |  | 16 |  | 8755 | 8779 | 24 | 24 | OK |  |  |  |  | 125 |  |  | 25 | 100 | 125 | 100 | 4.1667 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_351A | Riverside Congo Way | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-22 |  |  | CK Works |  | 20 |  | 6065 | 6082 | 17 | 24 | OK |  |  |  |  | 157 |  |  | 73 | 50 | 123 | 84 | 4.9412 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_266A | KAWAMA Copperbelt | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-16 |  |  | Gen Logic |  | 16 |  | 14504 | 14648 | 144 | 168 | OK |  |  |  |  | 317 |  |  | 0 | 50 | 50 | 317 | 2.2014 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_217M | KITWE MAIN SCHOOL | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-22 |  |  | Generator City |  | 16 |  | 16127 | 16163 | 36 | 24 | inconsitent RH |  |  |  |  | 151 |  |  | 16 | 100 | 116 | 135 | 3.75 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_311A | KAMPOYO | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-09-02 |  |  | GL Yanmar |  | 15 |  | FAULTY | FAULTY | #VALUE! | 1224 | #VALUE! |  |  |  |  | 210 |  |  | 30 | 100 | 130 | 180 | #VALUE! | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_056M | Masangano | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-19 |  |  | GL Yanmar |  | 16 |  | 23101 | 23131 | 30 | 96 | OK |  |  |  |  | 590 |  |  | 10 | 150 | 160 | 580 | 19.3333 | 2 | [5 empty] | 0 | [7 empty] | Suspected fuel theft oB number 4404/25 reported at kafulafuta police. | IHS PUMA |  | CAPTURED
IHS_CBT_091M | Kalalangabo | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-17 |  |  | GL Yanmar |  | 16 |  | 5898 | 5964 | 66 | 144 | OK |  |  |  |  | 461 |  |  | 220 | 100 | 320 | 241 | 3.6515 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_236A | KALALANGABO | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-17 |  |  | ASCOT |  | 30 |  | 131 | 207 | 76 | 144 | OK |  |  |  |  | 360 |  |  | 20 | 200 | 220 | 340 | 4.4737 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_012M | Itawa West | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-18 |  |  | Lamasat |  | 20 |  | 11611 | 11716 | 105 | 120 | OK |  |  |  |  | 390 |  |  | 75 | 100 | 175 | 315 | 3 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_002M | Hillcrest | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-18 |  |  | GL Yanmar |  | 20 |  | 7864 | 7947 | 83 | 120 | OK |  |  |  |  | 375 |  |  | 84 | 100 | 184 | 291 | 3.506 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_224M | SKYWAYS KAPIRI ROAD | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-20 |  |  | Generator City |  | 13 |  | 4393 | 4443 | 50 | 72 | OK |  |  |  |  | 213 |  |  | 39 | 50 | 89 | 174 | 3.48 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_022M | Kasembo | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-20 |  |  | Gen Logic |  | 20 |  | 6339 | 6381 | 42 | 72 | OK |  |  |  |  | 306 |  |  | 104 | 100 | 204 | 202 | 4.8095 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_027M | Kantolomba | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-20 |  |  | CK Works |  | 20 |  | 5656 | 5698 | 42 | 72 | OK |  |  |  |  | 413 |  |  | 177 | 100 | 277 | 236 | 5.619 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_006M | Lubuto Central | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-20 |  |  | Lamasat |  | 15 |  | 1166 | 1206 | 40 | 72 | OK |  |  |  |  | 205 |  |  | 17 | 100 | 117 | 188 | 4.7 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_024M | Ndeke Township | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-20 |  |  | CK Works |  | 30 |  | 11717 | 11776 | 59 | 72 | OK |  |  |  |  | 474 |  |  | 149 | 100 | 249 | 325 | 5.5085 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_033M | Bwana Mukubwa | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-19 |  |  | GL Yanmar |  | 16 |  | 1031 | 1105 | 74 | 96 | OK |  |  |  |  | 305 |  |  | 5 | 200 | 205 | 300 | 4.0541 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_336A | Fatima Girls | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-17 |  |  | perkins |  | 15 |  | 11371 | 11461 | 90 | 144 | OK |  |  |  |  | 318 |  |  | 30 | 100 | 130 | 288 | 3.2 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_035M | Kaloko | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-22 |  |  | Himoinsa |  | 30 |  | 9583 | 9607 | 24 | 24 | OK |  |  |  |  | 110 |  |  | 10 | 150 | 160 | 100 | 4.1667 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_020M | Mushili | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-20 |  |  | CK Works |  | 30 |  | 8548 | 8586 | 38 | 72 | OK |  |  |  |  | 312 |  |  | 133 | 200 | 333 | 179 | 4.7105 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_237A | NKANA WEST | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-21 |  |  | Earth technology |  | 20 |  | 11957 | 12002 | 45 | 48 | OK |  |  |  |  | 169 |  |  | 5 | 200 | 205 | 164 | 3.6444 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_274A | ZNS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-14 |  |  | Gen Logic |  | 16 |  | 13248 | 13359 | 111 | 216 | OK |  |  |  |  | 343 |  |  | 62 | 50 | 112 | 281 | 2.5315 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_084M | Kitwe ZNS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-22 |  |  | CDP |  | 15 |  | 18366 | 18381 | 15 | 24 | OK |  |  |  |  | 60 |  |  | 24 | 100 | 124 | 36 | 2.4 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_073M | Cedrics Farm | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-15 |  |  | perkins |  | 15 |  | 17221 | 17385 | 164 | 192 | OK |  |  |  |  | 482 |  |  | 20 | 50 | 70 | 462 | 2.8171 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_073M | Cedrics Farm | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-23 |  |  | perkins |  | 15 |  | 17385 | 17399 | 14 | 0 | inconsitent RH |  |  |  |  | 70 |  |  | 25 | 100 | 125 | 45 | 3.2143 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_345A | Ndeke Changachanga south 3G | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-22 |  |  | Gen Logic |  | 20 |  | 13679 | 13706 | 27 | 24 | inconsitent RH |  |  |  |  | 118 |  |  | 32 | 100 | 132 | 86 | 3.1852 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_075M | Ndeke Changachanga | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-22 |  |  | Gen Logic |  | 20 |  | 3809 | 3834 | 25 | 24 | inconsitent RH |  |  |  |  | 147 |  |  | 15 | 150 | 165 | 132 | 5.28 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_244A | NDEKE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-22 |  |  | Earth technology |  | 15 |  | 4048 | 4073 | 25 | 24 | inconsitent RH |  |  |  |  | 185 |  |  | 87 | 100 | 187 | 98 | 3.92 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_079M | Ndeke | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-22 |  |  | CK Works |  | 20 |  | 10133 | 10156 | 23 | 24 | OK |  |  |  |  | 204 |  |  | 82 | 100 | 182 | 122 | 5.3043 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_242A | PARKLANDS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-19 |  |  | Gen Logic |  | 20 |  | 9803 | 9882 | 79 | 96 | OK |  |  |  |  | 272 |  |  | 5 | 100 | 105 | 267 | 3.3797 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_228A | MINDOLO | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-22 |  |  | Earth technology |  | 20 |  | 11365 | 11393 | 28 | 24 | inconsitent RH |  |  |  |  | 128 |  |  | 34 | 100 | 134 | 94 | 3.3571 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_342A | Kantanta Street | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-20 |  |  | Gen Logic |  | 20 |  | 3954 | 3989 | 35 | 72 | OK |  |  |  |  | 159 |  |  | 20 | 100 | 120 | 139 | 3.9714 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_094M | Kitwe Primary | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-23 | 2025-10-20 |  |  | Gen Logic |  | 16 |  | 2741 | 2756 | 15 | 72 | OK |  |  |  |  | 70 |  |  | 10 | 50 | 60 | 60 | 4 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_133M | Chibuluma Golf Club | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-20 |  |  | Powerol |  | 13 |  | 5406 | 5500 | 94 | 96 | OK |  |  |  |  | 173 |  |  | 0 | 250 | 250 | 173 | 1.8404 | 1.5 | [5 empty] | 0 | [8 empty] | TOTAL |  | CAPTURED
IHS_CBT_238M | NAPSA Complex | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-22 |  |  | MPMC |  | 15 |  | 8755 | 8776 | 21 | 48 | OK |  |  |  |  | 107 |  |  | 31 | 100 | 131 | 76 | 3.619 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_118M | Kamaronde | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-22 |  |  | CK Works |  | 20 |  | 3246 | 3260 | 14 | 48 | OK |  |  |  |  | 266 |  |  | 210 | 100 | 310 | 56 | 4 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_301A | CHIBULUMA TOWN | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-20 |  |  | Gen Logic |  | 16 |  | 9784 | 9870 | 86 | 96 | OK |  |  |  |  | 409 |  |  | 87 | 100 | 187 | 322 | 3.7442 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_117M | Chibote | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-20 |  |  | Gen Logic |  | 15 |  | 5974 | 6038 | 64 | 96 | OK |  |  |  |  | 354 |  |  | 110 | 150 | 260 | 244 | 3.8125 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_134M | Kalulushi East | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-22 |  |  | CK Works |  | 20 |  | 8505 | 8540 | 35 | 48 | OK |  |  |  |  | 171 |  |  | 5 | 200 | 205 | 166 | 4.7429 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_310A | CHEMBE CHATI | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-09 |  |  | Gen Logic |  | 17 |  | FAULTY | FAULTY | #VALUE! | 360 | #VALUE! |  |  |  |  | 304 |  |  | 121 | 200 | 321 | 183 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_159M | Chembe South | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-15 |  |  | Gen Logic |  | 20 |  | FAULTY | FAULTY | #VALUE! | 216 | #VALUE! |  |  |  |  | 375 |  |  | 5 | 250 | 255 | 370 | #VALUE! | 2.5 | [5 empty] | 0 | [7 empty] | faulty controller | TOTAL |  | CAPTURED
IHS_CBT_167M | Kafubu | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-20 |  |  | LISTER PETTER |  | 16 |  | FAULTY | FAULTY | #VALUE! | 96 | #VALUE! |  |  |  |  | 105 |  |  | 20 | 100 | 120 | 85 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | TOTAL |  | CAPTURED
IHS_CBT_146M | Miku Mining | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-20 |  |  | Gen Logic |  | 20 |  | 20662 | 20739 | 77 | 96 | OK |  |  |  |  | 215 |  |  | 5 | 100 | 105 | 210 | 2.7273 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_068M | Mpatamato Central | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-13 |  |  | perkins |  | 15 |  | 11286 | 11414 | 128 | 264 | OK | [7 empty] | 35 | 100 | 135 | -35 | -0.27344 | 1.8 | [5 empty] | 0 | [8 empty] | TOTAL |  | CAPTURED
IHS_CBT_065M | Mpatamato East | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-23 |  |  | Yanmar |  | 16 |  | 8626 | 8626 | 0 | 24 | OK |  |  |  |  | 50 |  |  | 50 | 50 | 100 | 0 | #DIV/0! | 2 | [5 empty] | 0 | [7 empty] | DG DIDNT RUN | TOTAL |  | CAPTURED
IHS_CBT_062M | Roan Township | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-14 |  |  | CK Works |  | 20 |  | 8365 | 8414 | 49 | 240 | OK |  |  |  |  | 205 |  |  | 40 | 100 | 140 | 165 | 3.3673 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_050M | Luanshya Town Center | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-23 |  |  | Gen Logic |  | 20 |  | 8581 | 8593 | 12 | 24 | OK |  |  |  |  | 195 |  |  | 141 | 100 | 241 | 54 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_210A | LUANSHYA | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-19 |  |  | CK Works |  | 20 |  | 8013 | 8074 | 61 | 120 | OK |  |  |  |  | 268 |  |  | 55 | 150 | 205 | 213 | 3.4918 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_049M | Mikomfwa East | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-19 |  |  | Gen Logic |  | 16 |  | 6625 | 6703 | 78 | 120 | OK |  |  |  |  | 313 |  |  | 40 | 150 | 190 | 273 | 3.5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_054M | Mikomfwa Market | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-23 |  |  | Yanmar |  | 16 |  | 12563 | 12576 | 13 | 24 | OK |  |  |  |  | 121 |  |  | 69 | 100 | 169 | 52 | 4 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_058M | Mikomfwa | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-22 |  |  | Gen Logic |  | 16 |  | 7953 | 7982 | 29 | 48 | OK |  |  |  |  | 100 |  |  | 10 | 50 | 60 | 90 | 3.1034 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_069M | Mpatamato West | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-15 |  |  | Gen Logic |  | 16 |  | 16031 | 16149 | 118 | 216 | OK |  |  |  |  | 480 |  |  | 30 | 100 | 130 | 450 | 3.8136 | 2 | [5 empty] | 0 | [8 empty] | TOTAL |  | CAPTURED
IHS_CBT_339A | Katuni Eden Institute | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-15 |  |  | Gen Logic |  | 10 |  | 15851 | 15947 | 96 | 216 | OK |  |  |  |  | 320 |  |  | 32 | 100 | 132 | 288 | 3 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_211A | MPATAMATU | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-23 |  |  | IMG |  | 20 |  | 7949 | 7951 | 2 | 24 | OK |  |  |  |  | 60 |  |  | 53 | 50 | 103 | 7 | 3.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_058M | Mikomfwa | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-24 |  |  | Gen Logic |  | 16 |  | 7982 | 7992 | 10 | 0 | inconsitent RH |  |  |  |  | 60 |  |  | 25 | 100 | 125 | 35 | 3.5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | TOTAL |  | CAPTURED
IHS_CBT_025M | Pamozi Extension | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-23 |  |  | GL Yanmar |  | 16 |  | 3506 | 3523 | 17 | 24 | OK |  |  |  |  | 77 |  |  | 24 | 200 | 224 | 53 | 3.1176 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_264A | NDOLA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-22 |  |  | Gen Logic |  | 16 |  | 6162 | 6174 | 12 | 48 | OK |  |  |  |  | 69 |  |  | 13 | 200 | 213 | 56 | 4.6667 | 2 | [5 empty] | 0 | [8 empty] | IHS PUMA |  | CAPTURED
IHS_CBT_361A | Mitengo TDRC | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-20 |  |  | CK Works |  | 20 |  | 5683 | 5747 | 64 | 96 | OK |  |  |  |  | 395 |  |  | 107 | 100 | 207 | 288 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_257A | TWAPIA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-23 |  |  | CK Works |  | 20 |  | 12823 | 12836 | 13 | 24 | OK |  |  |  |  | 104 |  |  | 45 | 200 | 245 | 59 | 4.5385 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_041M | Kaniki | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-23 |  |  | GL Yanmar |  | 16 |  | 11460 | 11460 | 0 | 24 | OK |  |  |  |  | 139 |  |  | 139 | 200 | 339 | 0 | #DIV/0! | 2 | [5 empty] | 0 | [7 empty] | DG DIDNT RUN | IHS PUMA |  | CAPTURED
IHS_CBT_361A | Mitengo TDRC | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-24 |  |  | CK Works |  | 20 |  | 5747 | 5754 | 7 | 0 | inconsitent RH |  |  |  |  | 207 |  |  | 175 | 200 | 375 | 32 | 4.5714 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_018M | Nkwanzi | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-23 |  |  | CK Works |  | 20 |  | 1592 | 1612 | 20 | 24 | OK |  |  |  |  | 139 |  |  | 49 | 200 | 249 | 90 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_359A | Cross Crescent | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-22 |  |  | CK Works |  | 20 |  | 5783 | 5820 | 37 | 48 | OK |  |  |  |  | 230 |  |  | 52 | 200 | 252 | 178 | 4.8108 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_005M | Premium Plaza | CCS | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Roof Top |  | 2025-10-24 | 2025-10-22 |  |  | N/A |  | N/A |  | 8839 | 8876 | 37 | 48 | OK |  |  |  |  | 151 |  |  | 24 | 150 | 174 | 127 | 3.4324 | N/A | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_233A | CHIPULUKUSU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-22 |  |  | Earth Technology |  | 15 |  | 5017 | 5044 | 27 | 48 | OK |  |  |  |  | 251 |  |  | 120 | 200 | 320 | 131 | 4.8519 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_245A | NORTHRISE | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-22 |  |  | Lamasat |  | 20 |  | 8790 | 8803 | 13 | 48 | OK |  |  |  |  | 178 |  |  | 138 | 200 | 338 | 40 | 3.0769 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_219M | PETAUKE CRESCENT | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-22 |  |  | CK Works |  | 20 |  | 4041 | 4062 | 21 | 48 | OK |  |  |  |  | 253 |  |  | 152 | 200 | 352 | 101 | 4.8095 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_023M | Twapia | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-18 |  |  | Gen Logic |  | 15 |  | 7701 | 7773 | 72 | 144 | OK |  |  |  |  | 315 |  |  | 27 | 150 | 177 | 288 | 4 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_029M | Zafico | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-23 |  |  | Green Power |  | 15 |  | 3469 | 3483 | 14 | 24 | OK |  |  |  |  | 128 |  |  | 80 | 150 | 230 | 48 | 3.4286 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_013M | Dola Hill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-22 |  |  | Himoinsa |  | 30 |  | 5883 | 5915 | 32 | 48 | OK |  |  |  |  | 369 |  |  | 209 | 200 | 409 | 160 | 5 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_222M | TWAPIA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-23 |  |  | Generator City |  | 13 |  | 1120 | 1133 | 13 | 24 | OK |  |  |  |  | 116 |  |  | 64 | 150 | 214 | 52 | 4 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_252A | CHIFUBU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-23 |  |  | Gen Logic |  | 30 |  | 4322 | 4331 | 9 | 24 | OK |  |  |  |  | 102 |  |  | 68 | 100 | 168 | 34 | 3.7778 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_364A | Chifubu Sec. School | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-18 |  |  | CK Works |  | 20 |  | 848 | 881 | 33 | 144 | OK |  |  |  |  | 334 |  |  | 103 | 100 | 203 | 231 | 7 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_017M | Overspill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-23 |  |  | Falcon |  | 20 |  | 8892 | 8915 | 23 | 24 | OK |  |  |  |  | 147 |  |  | 78 | 100 | 178 | 69 | 3 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_218A | PAMODZI | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-18 |  |  | Gen Logic |  | 20 |  | 13855 | 13929 | 74 | 144 | OK |  |  |  |  | 326 |  |  | 111 | 100 | 211 | 215 | 2.9054 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_306A | TUG-ARGAN | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-21 |  |  | Yanmar |  | 16 |  | 13149 | 13199 | 50 | 72 | OK |  |  |  |  | 303 |  |  | 136 | 100 | 236 | 167 | 3.34 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_346A | Nilkant Mine | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Solar-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-21 |  |  | CK Works |  | 20 |  | 11527 | 11553 | 26 | 72 | OK |  |  |  |  | 280 |  |  | 187 | 200 | 387 | 93 | 3.5769 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_085M | Dangote | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-21 |  |  | Earth technology |  | 13 |  | 8108 | 8163 | 55 | 72 | OK |  |  |  |  | 342 |  |  | 184 | 100 | 284 | 158 | 2.8727 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_325A | KALOKO KAFULAFUTA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-16 |  |  | GL Yanmar |  | 15 |  | 7629 | 7666 | 37 | 192 | OK |  |  |  |  | 260 |  |  | 167 | 100 | 267 | 93 | 2.5135 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_362A | Ndola Central Police | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-22 |  |  | CK Works |  | 20 |  | 12181 | 12236 | 55 | 48 | inconsitent RH |  |  |  |  | 175 |  |  | 21 | 200 | 221 | 154 | 2.8 | 4.5 | [5 empty] | 0 | [7 empty] | faulty controller | IHS PUMA |  | CAPTURED
IHS_CBT_207A | KANINI | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-19 |  |  | Gen Logic |  | 16 |  | 9220 | 9276 | 56 | 120 | OK |  |  |  |  | 199 |  |  | 13 | 200 | 213 | 186 | 3.3214 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_004M | Ndola T. Centre | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-22 |  |  | Falcon |  | 20 |  | 422 | 455 | 33 | 48 | OK |  |  |  |  | 216 |  |  | 64 | 200 | 264 | 152 | 4.6061 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_360A | Hilcrest Extension | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-20 |  |  | CK Works |  | 20 |  | 10708 | 10752 | 44 | 96 | OK |  |  |  |  | 252 |  |  | 45 | 200 | 245 | 207 | 4.7045 | 5.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_014M | Lubuto | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-20 |  |  | CK Works |  | 20 |  | 3907 | 3972 | 65 | 96 | OK |  |  |  |  | 360 |  |  | 54 | 200 | 254 | 306 | 4.7077 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_293A | MUSAKASONKA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-19 |  |  | Gen Logic |  | 20 |  | 1405 | 1450 | 45 | 120 | OK |  |  |  |  | 220 |  |  | 5 | 200 | 205 | 215 | 4.7778 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_040M | Seed Of Hope | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-21 |  |  | Lamasat |  | 15 |  | 25195 | 25238 | 43 | 72 | OK |  |  |  |  | 210 |  |  | 52 | 200 | 252 | 158 | 3.6744 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_016M | Itawa | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-22 |  |  | Vitalgen |  | 30 |  | 4798 | 4818 | 20 | 48 | OK |  |  |  |  | 293 |  |  | 181 | 200 | 381 | 112 | 5.6 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_224M | SKYWAYS KAPIRI ROAD | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-23 |  |  | Generator City |  | 13 |  | 4443 | 4450 | 7 | 24 | OK |  |  |  |  | 89 |  |  | 63 | 200 | 263 | 26 | 3.7143 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_010M | Kabushi | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-20 |  |  | IMG |  | 15 |  | 7739 | 7790 | 51 | 96 | OK |  |  |  |  | 298 |  |  | 109 | 200 | 309 | 189 | 3.7059 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_283A | MASALA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-22 |  |  | IMG |  | 20 |  | 7876 | 7899 | 23 | 48 | OK |  |  |  |  | 275 |  |  | 194 | 200 | 394 | 81 | 3.5217 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_102M | Richmond | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-19 |  |  | Gen Logic |  | 16 |  | 2962 | 3050 | 88 | 120 | OK |  |  |  |  | 303 |  |  | 5 | 100 | 105 | 298 | 3.3864 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_274A | ZNS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-23 |  |  | Gen Logic |  | 16 |  | 13359 | 13361 | 2 | 24 | OK |  |  |  |  | 112 |  |  | 106 | 200 | 306 | 6 | 3 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_084M | Kitwe ZNS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-23 |  |  | CDP |  | 15 |  | 18381 | 18403 | 22 | 24 | OK |  |  |  |  | 124 |  |  | 68 | 200 | 268 | 56 | 2.5455 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_092M | Nkana Stadium | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-20 |  |  | Gen Logic |  | 16 |  | 5664 | 5714 | 50 | 96 | OK |  |  |  |  | 285 |  |  | 79 | 100 | 179 | 206 | 4.12 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_356A | New Ndeke Village | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-22 |  |  | CK Works |  | 20 |  | 1044 | 1082 | 38 | 48 | OK |  |  |  |  | 252 |  |  | 72 | 100 | 172 | 180 | 4.7368 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_334A | Miseshi Village | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-19 |  |  | Generator City |  | 16 |  | 3367 | 3452 | 85 | 120 | OK |  |  |  |  | 551 |  |  | 122 | 100 | 222 | 429 | 5.0471 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_079M | Ndeke | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-23 |  |  | CK Works |  | 20 |  | 10156 | 10172 | 16 | 24 | OK |  |  |  |  | 182 |  |  | 98 | 100 | 198 | 84 | 5.25 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_223M | SHOW GROUNDS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-19 |  |  | Generator City |  | 16 |  | FAULTY | FAULTY | #VALUE! | 120 | #VALUE! |  |  |  |  | 205 |  |  | 5 | 100 | 105 | 200 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | IHS PUMA |  | CAPTURED
IHS_CBT_353A | Court Barrifs | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-22 |  |  | CK Works |  | 20 |  | 10658 | 10694 | 36 | 48 | OK |  |  |  |  | 163 |  |  | 20 | 100 | 120 | 143 | 3.9722 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_300A | LUBAMBE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-23 |  |  | Jiuan |  | 30 |  | 5284 | 5301 | 17 | 24 | OK |  |  |  |  | 125 |  |  | 33 | 100 | 133 | 92 | 5.4118 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_083M | Nkana East | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-22 |  |  | Gen Logic |  | 16 |  | 4073 | 4094 | 21 | 48 | OK |  |  |  |  | 273 |  |  | 180 | 100 | 280 | 93 | 4.4286 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_113M | Green Belt | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-23 |  |  | IMG |  | 20 |  | 10726 | 10739 | 13 | 24 | OK |  |  |  |  | 226 |  |  | 149 | 200 | 349 | 77 | 5.9231 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_235M | KAWAMA KCC (Chimwemwe rlf | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-23 |  |  | CK Works |  | 20 |  | 9677 | 9690 | 13 | 24 | OK |  |  |  |  | 141 |  |  | 73 | 150 | 223 | 68 | 5.2308 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_114M | Kamatipa North | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-23 |  |  | perkins |  | 15 |  | 1174 | 1177 | 3 | 24 | OK |  |  |  |  | 110 |  |  | 97 | 100 | 197 | 13 | 4.3333 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_103M | Kwacha central | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-23 |  |  | Gen Logic |  | 16 |  | 949 | 954 | 5 | 24 | OK |  |  |  |  | 63 |  |  | 42 | 200 | 242 | 21 | 4.2 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_249A | BUCHI | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-05 |  |  | Gen Logic |  | 16 |  | 9039 | 187 | -8852 | 456 | OK |  |  |  |  | 154 |  |  | 128 | 100 | 228 | 26 | -0.0029372 | 2 | [5 empty] | 0 | [7 empty] | DG SWAP | IHS PUMA |  | CAPTURED
IHS_CBT_229A | CHIMWEMWE | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-23 |  |  | Gen Logic |  | 20 |  | 528 | 550 | 22 | 24 | OK |  |  |  |  | 238 |  |  | 119 | 250 | 369 | 119 | 5.4091 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_296A | KAMUNGA | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-23 |  |  | Gen Logic |  | 16 |  | 6372 | 6397 | 25 | 24 | inconsitent RH |  |  |  |  | 105 |  |  | 22 | 100 | 122 | 83 | 3.32 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_241A | BULANGILILO | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-23 |  |  | perkins |  | 20 |  | 3256 | 3261 | 5 | 24 | OK |  |  |  |  | 55 |  |  | 37 | 100 | 137 | 18 | 3.6 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_090M | Jambo Drive | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-23 |  |  | Gen Logic |  | 16 |  | 8779 | 8790 | 11 | 24 | OK |  |  |  |  | 125 |  |  | 79 | 100 | 179 | 46 | 4.1818 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_089M | Valley View | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-23 |  |  | ASCOT |  | 30 |  | 3179 | 3192 | 13 | 24 | OK |  |  |  |  | 241 |  |  | 173 | 200 | 373 | 68 | 5.2308 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_354A | Mufuchani | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Gen Only |  |  | Green Field |  | 2025-10-24 | 2025-10-22 |  |  | CK Works |  | 20 |  | 13220 | 13250 | 30 | 48 | OK |  |  |  |  | 163 |  |  | 57 | 100 | 157 | 106 | 3.5333 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_269A | SOSOLISO | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-23 |  |  | Jiuan |  | 15 |  | 5728 | 5757 | 29 | 24 | inconsitent RH |  |  |  |  | 198 |  |  | 108 | 100 | 208 | 90 | 3.1034 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_351A | Riverside Congo Way | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-23 |  |  | CK Works |  | 20 |  | 6082 | 6093 | 11 | 24 | OK |  |  |  |  | 123 |  |  | 64 | 100 | 164 | 59 | 5.3636 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_119M | Lumumba | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-24 | 2025-10-15 |  |  | Gen Logic |  | 16 |  | 9694 | 9872 | 178 | 216 | OK |  |  |  |  | 414 |  |  | 5 | 200 | 205 | 409 | 2.2978 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH |  |  | CAPTURED
IHS_CBT_239A | LUFWANYAMA ROAD | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-10 |  |  | Diesel Electric |  | 16 |  | FAULTY | 7513 | #VALUE! | 360 | #VALUE! |  |  |  |  | 147 |  |  | 0 | 100 | 100 | 147 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_261A | CHATI | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Solar-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-09 |  |  | perkins |  | 16 |  | 14992 | 15034 | 42 | 384 | OK |  |  |  |  | 300 |  |  | 140 | 100 | 240 | 160 | 3.8095 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_133M | Chibuluma Golf Club | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-24 |  |  | Powerol |  | 13 |  | 5500 | 5526 | 26 | 24 | inconsitent RH |  |  |  |  | 250 |  |  | 156 | 200 | 356 | 94 | 3.6154 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_047M | Kamirenda | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-13 |  |  | Gen Logic |  | 16 |  | 13181 | 13251 | 70 | 288 | OK |  |  |  |  | 262 |  |  | 40 | 200 | 240 | 222 | 3.1714 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_054M | Mikomfwa Market | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-24 |  |  | Yanmar |  | 16 |  | 12576 | 12590 | 14 | 24 | OK |  |  |  |  | 169 |  |  | 113 | 100 | 213 | 56 | 4 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_049M | Mikomfwa East | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-24 |  |  | Gen Logic |  | 16 |  | 6703 | 6717 | 14 | 24 | OK |  |  |  |  | 190 |  |  | 124 | 100 | 224 | 66 | 4.7143 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_307A | TVTC | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-13 |  |  | Gen Logic |  | 16 |  | FAULTY | FAULTY | #VALUE! | 288 | #VALUE! |  |  |  |  | 281 |  |  | 108 | 200 | 308 | 173 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | IHS PUMA |  | CAPTURED
IHS_CBT_048M | Kamirenda Extension | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-23 |  |  | Vitalgen |  | 20 |  | 9835 | 9861 | 26 | 48 | OK |  |  |  |  | 184 |  |  | 82 | 200 | 282 | 102 | 3.9231 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_314A | KAFUBU BLOCK | GNM | Royd | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-22 |  |  | CK Works |  | 20 |  | 7652 | 7687 | 35 | 72 | OK |  |  |  |  | 271 |  |  | 141 | 200 | 341 | 130 | 3.7143 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_044M | Kafubu Block | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-22 |  |  | Yanmar |  | 16 |  | 17975 | 18002 | 27 | 72 | OK |  |  |  |  | 120 |  |  | 30 | 200 | 230 | 90 | 3.3333 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_312A | FISENGE | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-17 |  |  | Yanmar |  | 16 |  | 7427 | 7466 | 39 | 192 | OK |  |  |  |  | 432 |  |  | 276 | 200 | 476 | 156 | 4 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_093M | Kwacha East | GNM | Jaula | [10 empty] | 2025-10-25 | 2025-10-20 |  |  | Gen Logic |  | 30 |  | 190 | 254 | 64 | 120 | OK |  |  |  |  | 435 |  |  | 38 | 200 | 238 | 397 | 6.2031 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_087M | Lulamba School | GNM | Jaula | [10 empty] | 2025-10-25 | 2025-10-20 |  |  | perkins |  | 20 |  | 280 | 365 | 85 | 120 | OK |  |  |  |  | 354 |  |  | 16 | 200 | 216 | 338 | 3.9765 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_266A | KAWAMA Copperbelt | GNM | Jaula | [10 empty] | 2025-10-25 | 2025-10-23 |  |  | Gen Logic |  | 16 |  | 14648 | 14667 | 19 | 48 | OK |  |  |  |  | 50 |  |  | 5 | 250 | 255 | 45 | 2.3684 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_121M | Ichipe | GNM | Jaula | [10 empty] | 2025-10-25 | 2025-10-20 |  |  | IHS_CBT_121M |  | 15 |  | 14276 | 14343 | 67 | 120 | OK |  |  |  |  | 301 |  |  | 35 | 250 | 285 | 266 | 3.9701 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_114M | Kamatipa North | GNM | Jaula | [10 empty] | 2025-10-25 | 2025-10-24 |  |  | perkins |  | 15 |  | 1177 | 1196 | 19 | 24 | OK |  |  |  |  | 197 |  |  | 111 | 200 | 311 | 86 | 4.5263 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_235M | KAWAMA KCC (Chimwemwe rlf | GNM | Jaula | [10 empty] | 2025-10-25 | 2025-10-24 |  |  | CK Works |  | 20 |  | 9690 | 9708 | 18 | 24 | OK |  |  |  |  | 223 |  |  | 128 | 200 | 328 | 95 | 5.2778 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_296A | KAMUNGA | GNM | Jaula | [10 empty] | 2025-10-25 | 2025-10-24 |  |  | Gen Logic |  | 16 |  | 6397 | 6425 | 28 | 24 | inconsitent RH |  |  |  |  | 122 |  |  | 32 | 200 | 232 | 90 | 3.2143 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_241A | BULANGILILO | GNM | Jaula | [10 empty] | 2025-10-25 | 2025-10-24 |  |  | perkins |  | 20 |  | 3261 | 3284 | 23 | 24 | OK |  |  |  |  | 137 |  |  | 59 | 200 | 259 | 78 | 3.3913 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_285A | KWACHA | GNM | Jaula | [10 empty] | 2025-10-25 | 2025-10-22 |  |  | CK Works |  | 20 |  | 5530 | 5582 | 52 | 72 | OK |  |  |  |  | 227 |  |  | 47 | 250 | 297 | 180 | 3.4615 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_111M | Chimwemwe Nakadoli | GNM | Jaula | [10 empty] | 2025-10-25 | 2025-10-17 |  |  | GNM |  | 15 |  | 9688 | 9786 | 98 | 192 | OK |  |  |  |  | 472 |  |  | 206 | 200 | 406 | 266 | 2.7143 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_263A | NAKADOLI | GNM | Jaula | [10 empty] | 2025-10-25 | 2025-10-17 |  |  | Gen Logic |  | 16 |  | 6906 | 7022 | 116 | 192 | OK |  |  |  |  | 333 |  |  | 5 | 200 | 205 | 328 | 2.8276 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_333A | Mindolo North | GNM | Jaula | [10 empty] | 2025-10-25 | 2025-10-17 |  |  | perkins |  | 15 |  | 9075 | 9202 | 127 | 192 | OK |  |  |  |  | 301 |  |  | 0 | 300 | 300 | 301 | 2.3701 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_115M | Mindolo | GNM | Jaula | [10 empty] | 2025-10-25 | 2025-10-23 |  |  | Gen Logic |  | 16 |  | 7599 | 7637 | 38 | 48 | OK |  |  |  |  | 160 |  |  | 43 | 250 | 293 | 117 | 3.0789 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_090M | Jambo Drive | GNM | Jaula | [10 empty] | 2025-10-25 | 2025-10-24 |  |  | Gen Logic |  | 16 |  | 8790 | 8810 | 20 | 24 | OK |  |  |  |  | 179 |  |  | 76 | 250 | 326 | 103 | 5.15 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_351A | Riverside Congo Way | GNM | Jaula | [10 empty] | 2025-10-25 | 2025-10-24 |  |  | CK Works |  | 20 |  | 6095 | 6119 | 24 | 24 | OK |  |  |  |  | 164 |  |  | 41 | 300 | 341 | 123 | 5.125 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_234A | CHIWALA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-21 |  |  | Gen Logic |  | 20 |  | 21887 | 21926 | 39 | 96 | OK |  |  |  |  | 446 |  |  | 297 | 100 | 397 | 149 | 3.8205 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_056M | Masangano | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-23 |  |  | GL Yanmar |  | 16 |  | 23131 | 23142 | 11 | 48 | OK |  |  |  |  | 160 |  |  | 110 | 200 | 310 | 50 | 4.5455 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_336A | Fatima Girls | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-23 |  |  | perkins |  | 15 |  | 11461 | 11486 | 25 | 48 | OK |  |  |  |  | 180 |  |  | 92 | 200 | 292 | 88 | 3.52 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_236A | KALALANGABO | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-23 |  |  | ASCOT |  | 30 |  | 207 | 226 | 19 | 48 | OK |  |  |  |  | 220 |  |  | 131 | 200 | 331 | 89 | 4.6842 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_027M | Kantolomba | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-23 |  |  | CK Works |  | 20 |  | 5698 | 5731 | 33 | 48 | OK |  |  |  |  | 277 |  |  | 92 | 200 | 292 | 185 | 5.6061 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_021M | Sky ways | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-24 |  |  | CK Works |  | 20 |  | 7599 | 7619 | 20 | 24 | OK |  |  |  |  | 155 |  |  | 61 | 200 | 261 | 94 | 4.7 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_024M | Ndeke Township | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-23 |  |  | CK Works |  | 30 |  | 11776 | 11794 | 18 | 48 | OK |  |  |  |  | 249 |  |  | 150 | 300 | 450 | 99 | 5.5 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_012M | Itawa West | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-23 |  |  | Lamasat |  | 20 |  | 11716 | 11743 | 27 | 48 | OK |  |  |  |  | 175 |  |  | 94 | 200 | 294 | 81 | 3 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_288A | NDOLA BUS STATION | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-16 |  |  | CK Works |  | 20 |  | 389 | 485 | 96 | 216 | OK |  |  |  |  | 512 |  |  | 60 | 300 | 360 | 452 | 4.7083 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_003M | Swimming Pool | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-18 |  |  | CK Works |  | 30 |  | 7312 | 7364 | 52 | 168 | OK |  |  |  |  | 445 |  |  | 205 | 200 | 405 | 240 | 4.6154 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_360A | Hilcrest Extension | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-24 |  |  | CK Works |  | 20 |  | 10752 | 10773 | 21 | 24 | OK |  |  |  |  | 245 |  |  | 146 | 200 | 346 | 99 | 4.7143 | 5.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_002M | Hillcrest | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-23 |  |  | GL Yanmar |  | 20 |  | 7947 | 7949 | 2 | 48 | OK |  |  |  |  | 184 |  |  | 177 | 200 | 377 | 7 | 3.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_006M | Lubuto Central | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-23 |  |  | Lamasat |  | 15 |  | 1206 | 1242 | 36 | 48 | OK |  |  |  |  | 117 |  |  | 5 | 300 | 305 | 112 | 3.1111 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_253A | ITAWA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-21 |  |  | Gen Logic |  | 20 |  | 10866 | 10910 | 44 | 96 | OK |  |  |  |  | 292 |  |  | 124 | 200 | 324 | 168 | 3.8182 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_022M | Kasembo | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-23 |  |  | Gen Logic |  | 20 |  | 6381 | 6401 | 20 | 48 | OK |  |  |  |  | 204 |  |  | 110 | 300 | 410 | 94 | 4.7 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_118M | Kamaronde | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-24 |  |  | CK Works |  | 20 |  | 3260 | 3267 | 7 | 24 | OK |  |  |  |  | 310 |  |  | 282 | 100 | 382 | 28 | 4 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_238M | NAPSA Complex | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-24 |  |  | MPMC |  | 15 |  | 8776 | 8800 | 24 | 24 | OK |  |  |  |  | 131 |  |  | 44 | 200 | 244 | 87 | 3.625 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_206A | KALULUSHI | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-20 |  |  | IMG |  | 15 |  | 7569 | 7646 | 77 | 120 | OK |  |  |  |  | 383 |  |  | 36 | 250 | 286 | 347 | 4.5065 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_127M | Kalulushi | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-22 |  |  | Himoinsa |  | 30 |  | 10968 | 10984 | 16 | 72 | OK |  |  |  |  | 171 |  |  | 107 | 250 | 357 | 64 | 4 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_267A | KALULUSHI EAST | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-20 |  |  | Gen Logic |  | 16 |  | 13854 | 13955 | 101 | 120 | OK |  |  |  |  | 493 |  |  | 78 | 300 | 378 | 415 | 4.1089 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_132M | Kalulushi West | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-20 |  |  | Gen Logic |  | 20 |  | 5892 | 5945 | 53 | 120 | OK |  |  |  |  | 516 |  |  | 228 | 200 | 428 | 288 | 5.434 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_134M | Kalulushi East | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-24 |  |  | CK Works |  | 20 |  | 8540 | 8564 | 24 | 24 | OK |  |  |  |  | 205 |  |  | 116 | 200 | 316 | 89 | 3.7083 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_126M | Chibuluma | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-20 |  |  | Gen Logic |  | 20 |  | 3938 | 4008 | 70 | 120 | OK |  |  |  |  | 275 |  |  | 9 | 250 | 259 | 266 | 3.8 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_301A | CHIBULUMA TOWN | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-24 |  |  | Gen Logic |  | 16 |  | 9870 | 9870 | 0 | 24 | OK |  |  |  |  | 187 |  |  | 187 | 150 | 337 | 0 | #DIV/0! | 2 | [5 empty] | 0 | [7 empty] | DG DIDNT RUN | SAHARA |  | CAPTURED
IHS_CBT_117M | Chibote | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-24 |  |  | Gen Logic |  | 15 |  | 6038 | 6066 | 28 | 24 | inconsitent RH |  |  |  |  | 260 |  |  | 153 | 200 | 353 | 107 | 3.8214 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_213M | St. Marys Mission | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-15 |  |  | Pramac |  | 10 |  | FAULTY | FAULTY | #VALUE! | 240 | #VALUE! |  |  |  |  | 305 |  |  | 10 | 100 | 110 | 295 | #VALUE! | 1.5 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_329A | St. Marys Mission (MUTENDA ST. MARYS_1) | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-15 |  |  | METCO |  | 15 |  | FAULTY | FAULTY | #VALUE! | 240 | #VALUE! |  |  |  |  | 365 |  |  | 75 | 100 | 175 | 290 | #VALUE! | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_155M | St. Joseph | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-20 |  |  | Gen Logic |  | 16 |  | 6698 | 6778 | 80 | 120 | OK |  |  |  |  | 235 |  |  | 10 | 100 | 110 | 225 | 2.8125 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_328A | Lumpuma | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-14 |  |  | Gen Logic |  | 10 |  | 3462 | 3527 | 65 | 264 | OK |  |  |  |  | 394 |  |  | 149 | 100 | 249 | 245 | 3.7692 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_330A | Funda Junction (Mumena_5) | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-15 |  |  | METCO |  | 15 |  | FAULTY | FAULTY | #VALUE! | 240 | #VALUE! |  |  |  |  | 315 |  |  | 20 | 200 | 220 | 295 | #VALUE! | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_023M | Twapia | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-24 |  |  | Gen Logic |  | 15 |  | 7773 | 7789 | 16 | 24 | OK |  |  |  |  | 177 |  |  | 113 | 200 | 313 | 64 | 4 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_029M | Zafico | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-24 |  |  | Green Power |  | 15 |  | 3483 | 3500 | 17 | 24 | OK |  |  |  |  | 230 |  |  | 172 | 200 | 372 | 58 | 3.4118 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_222M | TWAPIA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-24 |  |  | Generator City |  | 13 |  | 1133 | 1151 | 18 | 24 | OK |  |  |  |  | 214 |  |  | 142 | 200 | 342 | 72 | 4 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_359A | Cross Crescent | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-24 |  |  | CK Works |  | 20 |  | 5820 | 5844 | 24 | 24 | OK |  |  |  |  | 252 |  |  | 136 | 200 | 336 | 116 | 4.8333 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_233A | CHIPULUKUSU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-24 |  |  | Earth Technology |  | 15 |  | 5044 | 5057 | 13 | 24 | OK |  |  |  |  | 320 |  |  | 257 | 100 | 357 | 63 | 4.8462 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_037M | Minsundu | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-20 |  |  | GL Yanmar |  | 16 |  | FAULTY | FAULTY | #VALUE! | 120 | #VALUE! |  |  |  |  | 384 |  |  | 79 | 300 | 379 | 305 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_344A | Nkwazi 3G | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-20 |  |  | CK Works |  | 20 |  | 45908 | 45999 | 91 | 120 | OK |  |  |  |  | 493 |  |  | 129 | 200 | 329 | 364 | 4 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_252A | CHIFUBU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-24 |  |  | Gen Logic |  | 30 |  | 4331 | 4338 | 7 | 24 | OK |  |  |  |  | 168 |  |  | 0 | 50 | 50 | 168 | 24 | 4.5 | [5 empty] | 0 | [7 empty] | Stolen fuel abiut 145 ltrs mattered reported at chifubu police ob number 6837/25 | SAHARA |  | CAPTURED
IHS_CBT_226M | CHIFUBU WEST | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-23 |  |  | Generator City |  | 13 |  | 19287 | 19319 | 32 | 48 | OK |  |  |  |  | 116 |  |  | 32 | 200 | 232 | 84 | 2.625 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_364A | Chifubu Sec. School | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-24 |  |  | CK Works |  | 20 |  | 881 | 890 | 9 | 24 | OK |  |  |  |  | 203 |  |  | 140 | 200 | 340 | 63 | 7 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_264A | NDOLA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-24 |  |  | Gen Logic |  | 16 |  | 6174 | 6212 | 38 | 24 | inconsitent RH |  |  |  |  | 213 |  |  | 30 | 300 | 330 | 183 | 4.8158 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_017M | Overspill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-24 |  |  | Falcon |  | 20 |  | 8915 | 8952 | 37 | 24 | inconsitent RH |  |  |  |  | 178 |  |  | 65 | 150 | 215 | 113 | 3.0541 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_025M | Pamozi Extension | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-24 |  |  | GL Yanmar |  | 16 |  | 3523 | 3567 | 44 | 24 | inconsitent RH |  |  |  |  | 224 |  |  | 92 | 100 | 192 | 132 | 3 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-23 |  |  | GL Yanmar |  | 20 |  | 490 | 507 | 17 | 48 | OK |  |  |  |  | 116 |  |  | 0 | 50 | 50 | 116 | 6.8235 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_218A | PAMODZI | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-24 |  |  | Gen Logic |  | 20 |  | 13929 | 13947 | 18 | 24 | OK |  |  |  |  | 211 |  |  | 158 | 100 | 258 | 53 | 2.9444 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_252A | CHIFUBU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-25 |  |  | Gen Logic |  | 30 |  | 4331 | 4338 | 7 | 0 | inconsitent RH |  |  |  |  | 50 |  |  | 16 | 50 | 66 | 34 | 4.8571 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_245A | NORTHRISE | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-24 |  |  | Lamasat |  | 20 |  | 8803 | 8845 | 42 | 24 | inconsitent RH |  |  |  |  | 338 |  |  | 149 | 100 | 249 | 189 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_219M | PETAUKE CRESCENT | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-24 |  |  | CK Works |  | 20 |  | 4062 | 4093 | 31 | 24 | inconsitent RH |  |  |  |  | 352 |  |  | 204 | 100 | 304 | 148 | 4.7742 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_005M | Premium Plaza | CCS | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Roof Top |  | 2025-10-25 | 2025-10-24 |  |  | N/A |  | N/A |  | 8876 | 8876 | 0 | 24 | OK |  |  |  |  | 174 |  |  | 174 | 100 | 274 | 0 | #DIV/0! | N/A | [5 empty] | 0 | [7 empty] | DG DIDNT RUN | SAHARA |  | CAPTURED
IHS_CBT_243A | GEDDIS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-26 |  |  | Gen Logic |  | 15 |  | 18015 | 18055 | 40 | -24 | inconsitent RH |  |  |  |  | 175 |  |  | 26 | 100 | 126 | 149 | 3.725 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_088M | Geddis | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-22 |  |  | CDP |  | 13 |  | 12157 | 12216 | 59 | 72 | OK |  |  |  |  | 137 |  |  | 5 | 100 | 105 | 132 | 2.2373 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_342A | Kantanta Street | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-23 |  |  | Gen Logic |  | 20 |  | 3989 | 4013 | 24 | 48 | OK |  |  |  |  | 120 |  |  | 20 | 100 | 120 | 100 | 4.1667 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_338A | Musa Kasonka_3_Rlf | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-22 |  |  | CK Works |  | 20 |  | 11197 | 11230 | 33 | 72 | OK |  |  |  |  | 180 |  |  | 57 | 300 | 357 | 123 | 3.7273 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_082M | Ndeke Extension | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-22 |  |  | Gen Logic |  | 20 |  | 7593 | 7633 | 40 | 72 | OK |  |  |  |  | 255 |  |  | 53 | 200 | 253 | 202 | 5.05 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_237A | NKANA WEST | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-23 |  |  | Earth technology |  | 20 |  | 12002 | 12054 | 52 | 48 | inconsitent RH |  |  |  |  | 205 |  |  | 17 | 300 | 317 | 188 | 3.6154 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_075M | Ndeke Changachanga | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-23 |  |  | Gen Logic |  | 20 |  | 3834 | 3862 | 28 | 48 | OK |  |  |  |  | 165 |  |  | 20 | 300 | 320 | 145 | 5.1786 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_074M | Luangwa | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-22 |  |  | Gen Logic |  | 16 |  | 4669 | 4717 | 48 | 72 | OK |  |  |  |  | 176 |  |  | 5 | 200 | 205 | 171 | 3.5625 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_305A | LUANGWA KAFUE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-22 |  |  | Yanmar |  | 16 |  | 1061 | 1164 | 103 | 72 | inconsitent RH |  |  |  |  | 223 |  |  | 223 | 200 | 423 | 0 | 0 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_073M | Cedrics Farm | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-23 |  |  | perkins |  | 15 |  | 17399 | 17427 | 28 | 48 | OK |  |  |  |  | 125 |  |  | 30 | 250 | 280 | 95 | 3.3929 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_078M | Bupe | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-20 |  |  | Gen Logic |  | 16 |  | 23108 | 23144 | 36 | 120 | OK |  |  |  |  | 120 |  |  | 22 | 150 | 172 | 98 | 2.7222 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_250A | SOB | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-22 |  |  | Gen Logic |  | 15 |  | 19617 | 19671 | 54 | 72 | OK |  |  |  |  | 129 |  |  | 5 | 150 | 155 | 124 | 2.2963 | 1.8 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_094M | Kitwe Primary | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-18 |  |  | Gen Logic |  | 16 |  | 2756 | 2765 | 9 | 168 | OK | [7 empty] | 20 | 200 | 220 | -20 | -2.2222 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_102M | Richmond | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-24 |  |  | Gen Logic |  | 16 |  | 3050 | 3069 | 19 | 24 | OK |  |  |  |  | 105 |  |  | 32 | 150 | 182 | 73 | 3.8421 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_242A | PARKLANDS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-23 |  |  | Gen Logic |  | 20 |  | 9882 | 9902 | 20 | 48 | OK |  |  |  |  | 105 |  |  | 22 | 30 | 52 | 83 | 4.15 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_352A | Parklands TBN | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-19 |  |  | CK Works |  | 20 |  | 8437 | 8544 | 107 | 144 | OK |  |  |  |  | 305 |  |  | 20 | 100 | 120 | 285 | 2.6636 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_297A | KITWE POLICE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-22 |  |  | Gen Logic |  | 16 |  | 7772 | 7824 | 52 | 72 | OK |  |  |  |  | 161 |  |  | 10 | 30 | 40 | 151 | 2.9038 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_251A | Kitwe Railways | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-26 |  |  | MPI |  | 20 |  | 5867 | 5912 | 45 | -24 | inconsitent RH |  |  |  |  | 191 |  |  | 20 | 40 | 60 | 171 | 3.8 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_242A | PARKLANDS |  | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-25 |  |  | Gen Logic |  | 20 |  | 9902 | 9907 | 5 | 0 | inconsitent RH |  |  |  |  | 52 |  |  | 32 | 150 | 182 | 20 | 4 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_297A | KITWE POLICE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-25 |  |  | Gen Logic |  | 16 |  | 7824 | 7834 | 10 | 0 | inconsitent RH |  |  |  |  | 40 |  |  | 10 | 100 | 110 | 30 | 3 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_251A | Kitwe Railways | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-25 |  |  | MPI |  | 20 |  | 5912 | 5922 | 10 | 0 | inconsitent RH |  |  |  |  | 60 |  |  | 19 | 150 | 169 | 41 | 4.1 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_222A | CHAMBOLI | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-22 |  |  | Gen Logic |  | 30 |  | 346 | 385 | 39 | 72 | OK |  |  |  |  | 218 |  |  | 35 | 200 | 235 | 183 | 4.6923 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_079M | Ndeke | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-24 |  |  | CK Works |  | 20 |  | 10172 | 10192 | 20 | 24 | OK |  |  |  |  | 198 |  |  | 89 | 200 | 289 | 109 | 5.45 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_244A | NDEKE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-23 |  |  | Earth technology |  | 15 |  | 4073 | 4110 | 37 | 48 | OK |  |  |  |  | 187 |  |  | 39 | 150 | 189 | 148 | 4 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_094M | Kitwe Primary | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-23 |  |  | Gen Logic |  | 16 |  | 2756 | 2765 | 9 | 48 | OK |  |  |  |  | 60 |  |  | 20 | 200 | 220 | 40 | 4.4444 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_119M | Lumumba | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-25 | 2025-10-24 |  |  | Gen Logic |  | 16 |  | 9872 | 9907 | 35 | 24 | inconsitent RH |  |  |  |  | 205 |  |  | 117 | 200 | 317 | 88 | 2.5143 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_129M | Emerald Mine Lufwanyama | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-20 |  |  | Gen Logic |  | 15 |  | 25400 | 25499 | 99 | 144 | OK |  |  |  |  | 330 |  |  | 50 | 150 | 200 | 280 | 2.8283 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_252A | CHIFUBU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-25 |  |  | Gen Logic |  | 30 |  | 4338 | 4352 | 14 | 24 | OK |  |  |  |  | 66 |  |  | 1 | 100 | 101 | 65 | 4.6429 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_146M | Miku Mining | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-24 |  |  | Gen Logic |  | 20 |  | 20739 | 20778 | 39 | 48 | OK |  |  |  |  | 105 |  |  | 0 | 200 | 200 | 105 | 2.6923 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_259A | KAMAKANGA I & II | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-16 |  |  | perkins |  | 20 |  | 21549 | 21608 | 59 | 240 | OK |  |  |  |  | 522 |  |  | 351 | 150 | 501 | 171 | 2.8983 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_167M | Kafubu | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-24 |  |  | LISTER PETTER |  | 16 |  | FAULTY | FAULTY | #VALUE! | 48 | #VALUE! |  |  |  |  | 120 |  |  | 100 | 150 | 250 | 20 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_155M | St. Joseph | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-25 |  |  | Gen Logic |  | 16 |  | 6778 | 6778 | 0 | 24 | OK |  |  |  |  | 110 |  |  | 110 | 100 | 210 | 0 | #DIV/0! | 2 | [5 empty] | 0 | [7 empty] | DG DIDNT RUN | SAHARA |  | CAPTURED
IHS_CBT_241M | Kagem mine | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-20 |  |  | perkins |  | 20 |  | 14314 | 14373 | 59 | 144 | OK |  |  |  |  | 215 |  |  | 15 | 150 | 165 | 200 | 3.3898 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_035M | Kaloko | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-23 |  |  | Himoinsa |  | 30 |  | 9607 | 9644 | 37 | 72 | OK |  |  |  |  | 160 |  |  | 10 | 250 | 260 | 150 | 4.0541 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_362A | Ndola Central Police | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-24 |  |  | CK Works |  | 20 |  | 12236 | 12276 | 40 | 48 | OK |  |  |  |  | 221 |  |  | 13 | 250 | 263 | 208 | 5.2 | 4.5 | [5 empty] | 0 | [7 empty] | faulty controller | MERU |  | CAPTURED
IHS_CBT_332A | Ndeke_Ndola | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Roof Top |  | 2025-10-26 | 2025-10-20 |  |  | 0 |  | 15 |  | 826 | 903 | 77 | 144 | OK |  |  |  |  | 331 |  |  | 71 | 300 | 371 | 260 | 3.3766 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_004M | Ndola T. Centre | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-24 |  |  | Falcon |  | 20 |  | 455 | 500 | 45 | 48 | OK |  |  |  |  | 264 |  |  | 52 | 150 | 202 | 212 | 4.7111 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_008M | Masala | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-20 |  |  | Generator City |  | 13 |  | 6562 | 6636 | 74 | 144 | OK |  |  |  |  | 367 |  |  | 91 | 250 | 341 | 276 | 3.7297 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_014M | Lubuto | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-24 |  |  | CK Works |  | 20 |  | 3972 | 4008 | 36 | 48 | OK |  |  |  |  | 254 |  |  | 84 | 250 | 334 | 170 | 4.7222 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_033M | Bwana Mukubwa | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-23 |  |  | GL Yanmar |  | 16 |  | 1105 | 1126 | 21 | 72 | OK |  |  |  |  | 205 |  |  | 106 | 200 | 306 | 99 | 4.7143 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_148M | Kaloko Trust | GNM | Kasoma | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-19 |  |  | Yanmar |  | 16 |  | 7229 | 7291 | 62 | 168 | OK |  |  |  |  | 210 |  |  | 30 | 200 | 230 | 180 | 2.9032 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_091M | Kalalangabo | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-23 |  |  | GL Yanmar |  | 16 |  | 5964 | 6008 | 44 | 72 | OK |  |  |  |  | 320 |  |  | 152 | 100 | 252 | 168 | 3.8182 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_016M | Itawa | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-24 |  |  | Vitalgen |  | 30 |  | 4818 | 4848 | 30 | 48 | OK |  |  |  |  | 381 |  |  | 213 | 250 | 463 | 168 | 5.6 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_363A | Milemu Sec. School | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-18 |  |  | CK Works |  | 20 |  | 10191 | 10287 | 96 | 192 | OK |  |  |  |  | 402 |  |  | 56 | 300 | 356 | 346 | 3.6042 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-25 |  |  | GL Yanmar |  | 20 |  | 507 | 522 | 15 | 24 | OK |  |  |  |  | 50 |  |  | 50 | 50 | 100 | 0 | 0 | 2 | [5 empty] | 0 | [7 empty] | Stolen fuel about 100 litres and a generator starter battery the matter has been reported at kawama police post OB number #2300/25 | SAHARA |  | CAPTURED
IHS_CBT_018M | Nkwanzi | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-24 |  |  | CK Works |  | 20 |  | 1612 | 1645 | 33 | 48 | OK |  |  |  |  | 249 |  |  | 100 | 200 | 300 | 149 | 4.5152 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_257A | TWAPIA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-24 |  |  | CK Works |  | 20 |  | 12836 | 12875 | 39 | 48 | OK |  |  |  |  | 245 |  |  | 69 | 200 | 269 | 176 | 4.5128 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_361A | Mitengo TDRC | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-24 |  |  | CK Works |  | 20 |  | 5754 | 5802 | 48 | 48 | OK |  |  |  |  | 375 |  |  | 159 | 300 | 459 | 216 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_335A | Daag Hamershold | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-21 |  |  | LAMASAT |  | 15 |  | 7875 | 7875 | 0 | 120 | OK |  |  |  |  | 274 |  |  | 0 | 50 | 50 | 274 | #DIV/0! | 1.8 | [5 empty] | 0 | [7 empty] | STOLEN FUEL ABOUT 274L REPORTED AT GEORGE POLICE POST 154/25 | SAHARA |  | CAPTURED
IHS_CBT_161M | Mikata Mpongwe | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Solar-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-23 |  |  | IMG |  | 20 |  | 9936 | 9973 | 37 | 72 | OK |  |  |  |  | 160 |  |  | 20 | 300 | 320 | 140 | 3.7838 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_215M | PHILIP FARM | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Solar-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-17 |  |  | perkins |  | 15 |  | 19531 | 19646 | 115 | 216 | OK |  |  |  |  | 270 |  |  | 20 | 300 | 320 | 250 | 2.1739 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_181M | Lukanga resettlement | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Solar-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-17 |  |  | CK Works |  | 20 |  | 5490 | 5645 | 155 | 216 | OK |  |  |  |  | 310 |  |  | 10 | 300 | 310 | 300 | 1.9355 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_265A | NEW TOWN | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-23 |  |  | Gen Logic |  | 16 |  | 1866 | 1904 | 38 | 72 | OK |  |  |  |  | 189 |  |  | 73 | 200 | 273 | 116 | 3.0526 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_043M | Fisenge | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-23 |  |  | Gen Logic |  | 16 |  | FAULTY | FAULTY | #VALUE! | 72 | #VALUE! |  |  |  |  | 253 |  |  | 214 | 200 | 414 | 39 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_050M | Luanshya Town Center | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-24 |  |  | Gen Logic |  | 20 |  | 8593 | 8593 | 0 | 48 | OK |  |  |  |  | 241 |  |  | 241 | 300 | 541 | 0 | #DIV/0! | 2.5 | [5 empty] | 0 | [7 empty] | DG DIDNT RUN | SAHARA |  | CAPTURED
IHS_CBT_227M | LUANSHYA EAST | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-23 |  |  | Generator City |  | 16 |  | 7712 | 7734 | 22 | 72 | OK |  |  |  |  | 229 |  |  | 132 | 200 | 332 | 97 | 4.4091 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_123M | Mukuba University | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-19 |  |  | IMG |  | 15 |  | 11755 | 11805 | 50 | 168 | OK |  |  |  |  | 286 |  |  | 111 | 300 | 411 | 175 | 3.5 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_112M | Kamtipa | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-20 |  |  | Gen Logic |  | 16 |  | 569 | 633 | 64 | 144 | OK |  |  |  |  | 407 |  |  | 138 | 200 | 338 | 269 | 4.2031 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_229A | CHIMWEMWE | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-24 |  |  | Gen Logic |  | 20 |  | 550 | 583 | 33 | 48 | OK |  |  |  |  | 369 |  |  | 187 | 300 | 487 | 182 | 5.5152 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_103M | Kwacha central | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-24 |  |  | Gen Logic |  | 16 |  | 954 | 990 | 36 | 48 | OK |  |  |  |  | 242 |  |  | 83 | 200 | 283 | 159 | 4.4167 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_093M | Kwacha East | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-25 |  |  | Gen Logic |  | 30 |  | 254 | 275 | 21 | 24 | OK |  |  |  |  | 238 |  |  | 105 | 300 | 405 | 133 | 6.3333 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_354A | Mufuchani | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Gen Only |  |  | Green Field |  | 2025-10-26 | 2025-10-24 |  |  | CK Works |  | 20 |  | 13250 | 13268 | 18 | 48 | OK |  |  |  |  | 157 |  |  | 94 | 200 | 294 | 63 | 3.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_080M | Kalambo | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-20 |  |  | Gen Logic |  | 16 |  | 6691 | 6746 | 55 | 144 | OK |  |  |  |  | 483 |  |  | 268 | 200 | 468 | 215 | 3.9091 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_089M | Valley View | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-24 |  |  | ASCOT |  | 30 |  | 3192 | 3214 | 22 | 48 | OK |  |  |  |  | 373 |  |  | 263 | 250 | 513 | 110 | 5 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_217M | KITWE MAIN SCHOOL | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-23 |  |  | Generator City |  | 16 |  | 16163 | 16193 | 30 | 72 | OK |  |  |  |  | 116 |  |  | 16 | 100 | 116 | 100 | 3.3333 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_225M | MUSHIPI | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-22 |  |  | Generator City |  | 16 |  | 9017 | 9058 | 41 | 96 | OK |  |  |  |  | 133 |  |  | 31 | 250 | 281 | 102 | 2.4878 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_081M | Chamboli | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-22 |  |  | Gen Logic |  | 16 |  | 13499 | 13541 | 42 | 96 | OK |  |  |  |  | 129 |  |  | 20 | 250 | 270 | 109 | 2.5952 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_356A | New Ndeke Village | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-24 |  |  | CK Works |  | 20 |  | 1082 | 1112 | 30 | 48 | OK |  |  |  |  | 172 |  |  | 30 | 300 | 330 | 142 | 4.7333 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_334A | Miseshi Village | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-24 |  |  | Generator City |  | 16 |  | 3452 | 3486 | 34 | 48 | OK |  |  |  |  | 222 |  |  | 37 | 400 | 437 | 185 | 5.4412 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_217A | MAPOSA | GNM | FACKSON | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-10 |  |  | Gen Logic |  | 30 |  | 25 | 32 | 7 | 384 | OK |  |  |  |  | 405 |  |  | 375 | 200 | 575 | 30 | 4.2857 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_345A | Ndeke Changachanga south 3G | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-23 |  |  | Gen Logic |  | 20 |  | 13706 | 13750 | 44 | 72 | OK |  |  |  |  | 132 |  |  | 5 | 200 | 205 | 127 | 2.8864 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_251A | Kitwe Railways | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-22 |  |  | MPI |  | 20 |  | 5922 | 5949 | 27 | 96 | OK |  |  |  |  | 169 |  |  | 51 | 300 | 351 | 118 | 4.3704 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_228A | MINDOLO | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-23 |  |  | Earth technology |  | 20 |  | 11393 | 11427 | 34 | 72 | OK |  |  |  |  | 134 |  |  | 30 | 300 | 330 | 104 | 3.0588 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_105M | Buntungwa | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-17 |  |  | Gen Logic |  | 16 |  | 5879 | 6005 | 126 | 216 | OK |  |  |  |  | 526 |  |  | 20 | 100 | 120 | 506 | 4.0159 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_083M | Nkana East | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-24 |  |  | Gen Logic |  | 16 |  | 4094 | 4130 | 36 | 48 | OK |  |  |  |  | 280 |  |  | 124 | 400 | 524 | 156 | 4.3333 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_368A | #N/A | #N/A | FACKSON | #N/A | #N/A | #N/A |  | #N/A | #N/A |  |  | #N/A |  | 2025-10-26 | 2025-10-15 |  |  | #N/A |  | #N/A |  | 9965 | 10116 | 151 | 264 | OK |  |  |  |  | 417 |  |  | 20 | 200 | 220 | 397 | 2.6291 | #N/A | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_088M | Geddis | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-25 |  |  | CDP |  | 13 |  | 12216 | 12251 | 35 | 24 | inconsitent RH |  |  |  |  | 105 |  |  | 5 | 300 | 305 | 100 | 2.8571 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_243A | GEDDIS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-22 |  |  | Gen Logic |  | 15 |  | 18055 | 18076 | 21 | 96 | OK |  |  |  |  | 126 |  |  | 54 | 200 | 254 | 72 | 3.4286 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_342A | Kantanta Street | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-23 |  |  | Gen Logic |  | 20 |  | 4013 | 4034 | 21 | 72 | OK |  |  |  |  | 120 |  |  | 31 | 300 | 331 | 89 | 4.2381 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_108M | Chachacha | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-26 | 2025-10-18 |  |  | perkins |  | 20 |  | 1635 | 1737 | 102 | 192 | OK |  |  |  |  | 521 |  |  | 52 | 300 | 352 | 469 | 4.598 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH |  |  | CAPTURED
IHS_CBT_013M | Dola Hill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-24 |  |  | Himoinsa |  | 30 |  | 5915 | 5965 | 50 | 72 | OK |  |  |  |  | 409 |  |  | 109 | 300 | 409 | 300 | 6 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_252A | CHIFUBU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-26 |  |  | Gen Logic |  | 30 |  | 4352 | 4371 | 19 | 24 | OK |  |  |  |  | 101 |  |  | 15 | 50 | 65 | 86 | 4.5263 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_226M | CHIFUBU WEST | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-25 |  |  | Generator City |  | 13 |  | 19319 | 19364 | 45 | 48 | OK |  |  |  |  | 232 |  |  | 115 | 200 | 315 | 117 | 2.6 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-26 |  |  | GL Yanmar |  | 20 |  | 507 | 522 | 15 | 24 | OK |  |  |  |  | 100 |  |  | 25 | 100 | 125 | 75 | 5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_025M | Pamozi Extension | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-25 |  |  | GL Yanmar |  | 16 |  | 3567 | 3600 | 33 | 48 | OK |  |  |  |  | 192 |  |  | 93 | 200 | 293 | 99 | 3 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_245A | NORTHRISE | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-25 |  |  | Lamasat |  | 20 |  | 8845 | 8862 | 17 | 48 | OK |  |  |  |  | 249 |  |  | 172 | 300 | 472 | 77 | 4.5294 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-27 |  |  | GL Yanmar |  | 20 |  | 522 | 522 | 0 | 0 | OK |  |  |  |  | 125 |  |  | 0 | 50 | 50 | 125 | #DIV/0! | 2 | [5 empty] | 0 | [7 empty] | Stolen fuel about 100 litres and a generator starter battery the matter has been reported at kawama police post OB number #2300/25 | MERU |  | CAPTURED
IHS_CBT_252A | CHIFUBU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-27 |  |  | Gen Logic |  | 30 |  | 4371 | 4371 | 0 | 0 | OK |  |  |  |  | 65 |  |  | 65 | 50 | 115 | 0 | #DIV/0! | 4.5 | [5 empty] | 0 | [7 empty] | Stolen fuel about 125 litres , Further details to be shared by Mr kambole | MERU |  | CAPTURED
IHS_CBT_041M | Kaniki | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-24 |  |  | GL Yanmar |  | 16 |  | 11460 | 11483 | 23 | 72 | OK |  |  |  |  | 339 |  |  | 274 | 200 | 474 | 65 | 2.8261 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_305A | LUANGWA KAFUE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-25 |  |  | Yanmar |  | 16 |  | 1164 | 1158 | -6 | 48 | OK |  |  |  |  | 229 |  |  | 229 | 400 | 629 | 0 | 0 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_092M | Nkana Stadium | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-24 |  |  | Gen Logic |  | 16 |  | 5714 | 5754 | 40 | 72 | OK |  |  |  |  | 179 |  |  | 23 | 250 | 273 | 156 | 3.9 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_074M | Luangwa | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-25 |  |  | Gen Logic |  | 16 |  | 4717 | 4758 | 41 | 48 | OK |  |  |  |  | 205 |  |  | 44 | 300 | 344 | 161 | 3.9268 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_081M | Chamboli | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-26 |  |  | Gen Logic |  | 16 |  | 13541 | 13549 | 8 | 24 | OK |  |  |  |  | 270 |  |  | 16 | 100 | 116 | 254 | 31.75 | 2 | [5 empty] | 0 | [7 empty] | STOLEN FUEL REPORTED AT WASUKILE POLICE POST OB NUMBER 12898/25 | SAHARA |  | CAPTURED
IHS_CBT_297A | KITWE POLICE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-25 |  |  | Gen Logic |  | 16 |  | 7834 | 7864 | 30 | 48 | OK |  |  |  |  | 110 |  |  | 20 | 300 | 320 | 90 | 3 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_244A | NDEKE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-25 |  |  | Earth technology |  | 15 |  | 4110 | 4144 | 34 | 48 | OK |  |  |  |  | 189 |  |  | 51 | 300 | 351 | 138 | 4.0588 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_079M | Ndeke | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-25 |  |  | CK Works |  | 20 |  | 10192 | 10221 | 29 | 48 | OK |  |  |  |  | 289 |  |  | 143 | 350 | 493 | 146 | 5.0345 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_355A | Ndeke Sub. A | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Gen Only |  |  | Green Field |  | 2025-10-27 | 2025-10-20 |  |  | CK Works |  | 20 |  | 15043 | 15113 | 70 | 168 | OK |  |  |  |  | 403 |  |  | 124 | 250 | 374 | 279 | 3.9857 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_218M | WUSAKILE POLICE CAMP | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-20 |  |  | Generator City |  | 16 |  | 7507 | 7582 | 75 | 168 | OK |  |  |  |  | 389 |  |  | 30 | 150 | 180 | 359 | 4.7867 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_102M | Richmond | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-25 |  |  | Gen Logic |  | 16 |  | 3069 | 3103 | 34 | 48 | OK |  |  |  |  | 182 |  |  | 36 | 200 | 236 | 146 | 4.2941 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_242A | PARKLANDS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-25 |  |  | Gen Logic |  | 20 |  | 9907 | 9957 | 50 | 48 | inconsitent RH |  |  |  |  | 182 |  |  | 20 | 200 | 220 | 162 | 3.24 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_352A | Parklands TBN | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-25 |  |  | CK Works |  | 20 |  | 8544 | 8580 | 36 | 48 | OK |  |  |  |  | 120 |  |  | 23 | 300 | 323 | 97 | 2.6944 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_094M | Kitwe Primary | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-25 |  |  | Gen Logic |  | 16 |  | 2765 | 2812 | 47 | 48 | OK |  |  |  |  | 220 |  |  | 36 | 200 | 236 | 184 | 3.9149 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_300A | LUBAMBE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-24 |  |  | Jiuan |  | 30 |  | 5301 | 5324 | 23 | 72 | OK |  |  |  |  | 133 |  |  | 10 | 100 | 110 | 123 | 5.3478 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_353A | Court Barrifs | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-24 |  |  | CK Works |  | 20 |  | 10694 | 10722 | 28 | 72 | OK |  |  |  |  | 120 |  |  | 20 | 100 | 120 | 100 | 3.5714 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_052M | Luanshya New Town | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-17 |  |  | Gen Logic |  | 16 |  | 15150 | 15257 | 107 | 240 | OK |  |  |  |  | 441 |  |  | 95 | 200 | 295 | 346 | 3.2336 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_343A | Chinese Colony | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-14 |  |  | Gen Logic |  | 20 |  | FAULTY | FAULTY | #VALUE! | 312 | #VALUE! |  |  |  |  | 437 |  |  | 82 | 200 | 282 | 355 | #VALUE! | 2.5 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_210A | LUANSHYA | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-24 |  |  | CK Works |  | 20 |  | 8074 | 8097 | 23 | 72 | OK |  |  |  |  | 205 |  |  | 121 | 200 | 321 | 84 | 3.6522 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_058M | Mikomfwa | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-24 |  |  | Gen Logic |  | 16 |  | 7992 | 8034 | 42 | 72 | OK |  |  |  |  | 125 |  |  | 5 | 200 | 205 | 120 | 2.8571 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_339A | Katuni Eden Institute | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-24 |  |  | Gen Logic |  | 10 |  | 15947 | 15989 | 42 | 72 | OK |  |  |  |  | 132 |  |  | 22 | 200 | 222 | 110 | 2.619 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_156M | Mpongwe Turnoff | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-19 |  |  | Himoinsa |  | 30 |  | 6865 | 6946 | 81 | 192 | OK |  |  |  |  | 427 |  |  | 142 | 100 | 242 | 285 | 3.5185 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_232A | LUBUTO | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-20 |  |  | Gen Logic |  | 20 |  | 11193 | 11266 | 73 | 168 | OK |  |  |  |  | 310 |  |  | 32 | 300 | 332 | 278 | 3.8082 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_027M | Kantolomba | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-25 |  |  | CK Works |  | 20 |  | 5731 | 5766 | 35 | 48 | OK |  |  |  |  | 292 |  |  | 96 | 300 | 396 | 196 | 5.6 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_001M | Kanini | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-19 |  |  | IMG |  | 20 |  | FAULTY | FAULTY | #VALUE! | 192 | #VALUE! |  |  |  |  | 258 |  |  | 0 | 300 | 300 | 258 | #VALUE! | 2.5 | [5 empty] | 0 | [7 empty] | faulty controller | MERU |  | CAPTURED
IHS_CBT_293A | MUSAKASONKA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-24 |  |  | Gen Logic |  | 20 |  | 1450 | 1483 | 33 | 72 | OK |  |  |  |  | 205 |  |  | 89 | 200 | 289 | 116 | 3.5152 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_217M | KITWE MAIN SCHOOL | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-26 |  |  | Generator City |  | 16 |  | 16193 | 16206 | 13 | 24 | OK |  |  |  |  | 116 |  |  | 70 | 300 | 370 | 46 | 3.5385 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_249A | BUCHI | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-24 |  |  | Gen Logic |  | 16 |  | 187 | 253 | 66 | 72 | OK |  |  |  |  | 100 |  |  | 0 | 300 | 300 | 100 | 1.5152 | 2 | [5 empty] | 0 | [8 empty] | IHS PUMA |  | CAPTURED
IHS_CBT_113M | Green Belt | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-24 |  |  | IMG |  | 20 |  | 10739 | 10788 | 49 | 72 | OK |  |  |  |  | 349 |  |  | 63 | 300 | 363 | 286 | 5.8367 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | IHS PUMA |  | CAPTURED
IHS_CBT_090M | Jambo Drive | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-25 |  |  | Gen Logic |  | 16 |  | 8810 | 8819 | 9 | 48 | OK |  |  |  |  | 326 |  |  | 12 | 300 | 312 | 314 | 34.8889 | 2 | [5 empty] | 0 | [7 empty] | STOLEN ABOUT 281L REPORTED AT RIVERSIDE POLICE POST OB NUMBER 13004/25 | IHS PUMA |  | CAPTURED
IHS_CBT_238M | NAPSA Complex | GNM | SAMUEL | 2025-10-27 | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-25 |  |  | MPMC |  | 15 |  | 8800 | 8841 | 41 | 48 | OK |  |  |  |  | 244 |  |  | 103 | 200 | 303 | 141 | 3.439 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_206A | KALULUSHI | GNM | SAMUEL | 2025-10-27 | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-25 |  |  | IMG |  | 15 |  | 7646 | 7675 | 29 | 48 | OK |  |  |  |  | 286 |  |  | 125 | 200 | 325 | 161 | 5.5517 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_126M | Chibuluma | GNM | SAMUEL | 2025-10-27 | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-27 | 2025-10-25 |  |  | Gen Logic |  | 20 |  | 4008 | 4033 | 25 | 48 | OK |  |  |  |  | 259 |  |  | 164 | 200 | 364 | 95 | 3.8 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_133M | Chibuluma Golf Club | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-25 |  |  | Powerol |  | 13 |  | 5526 | 5591 | 65 | 72 | OK |  |  |  |  | 356 |  |  | 122 | 300 | 422 | 234 | 3.6 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_239A | LUFWANYAMA ROAD | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-25 |  |  | Diesel Electric |  | 16 |  | 7513 | 7518 | 5 | 72 | OK |  |  |  |  | 100 |  |  | 80 | 300 | 380 | 20 | 4 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_129M | Emerald Mine Lufwanyama | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-26 |  |  | Gen Logic |  | 15 |  | 25499 | 25546 | 47 | 48 | OK |  |  |  |  | 200 |  |  | 83 | 200 | 283 | 117 | 2.4894 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_172M | ST. Anthony | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-09 |  |  | CK Works |  | 20 |  | 5573 | 5611 | 38 | 456 | OK |  |  |  |  | 238 |  |  | 120 | 200 | 320 | 118 | 3.1053 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_179M | ETC Bio Energy Farm | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-09 |  |  | Gen Logic |  | 15 |  | 10311 | 10390 | 79 | 456 | OK |  |  |  |  | 253 |  |  | 30 | 200 | 230 | 223 | 2.8228 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CTR_271A | MACHIYA | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-09 |  |  | RID |  | 16 |  | 7652 | 7693 | 41 | 456 | OK |  |  |  |  | 310 |  |  | 170 | 300 | 470 | 140 | 3.4146 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_137M | Nkanga Hills | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-15 |  |  | GL Yanmar |  | 16 |  | 5735 | 5829 | 94 | 312 | OK |  |  |  |  | 325 |  |  | 60 | 200 | 260 | 265 | 2.8191 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_319A | Nkanga Hill (Mumena_1) | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-15 |  |  | GL Yanmar |  | 15 |  | FAULTY | FAULTY | #VALUE! | 312 | #VALUE! |  |  |  |  | 336 |  |  | 44 | 200 | 244 | 292 | #VALUE! | 1.8 | [5 empty] | 0 | [7 empty] | faulty controller | MERU |  | CAPTURED
IHS_CBT_076M | Masaiti | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-17 |  |  | GL Yanmar |  | 16 |  | 2092 | 2109 | 17 | 264 | OK |  |  |  |  | 100 |  |  | 10 | 100 | 110 | 90 | 5.2941 | 2 | [5 empty] | 0 | [7 empty] | STOLEN FUEL MATTER REPORTED AT MASAITI BOMA OB NUMBER 2488/25 | MERU |  | CAPTURED
IHS_CBT_162M | Mpongweboma | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 |  |  |  | Yanmar |  | 16 |  | 2099 | 2163 | 64 | 1102992 | OK | [7 empty] | 149 | 200 | 349 | -149 | -2.3281 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_254A | MPONGWE BOMA | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 |  |  |  | CK Works |  | 20 |  | 7806 | 7872 | 66 | 1102992 | OK | [7 empty] | 92 | 200 | 292 | -92 | -1.3939 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_071M | Masaiti Council | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 |  |  |  | GL Yanmar |  | 16 |  | 10479 | 10512 | 33 | 1102992 | OK | [7 empty] | 144 | 100 | 244 | -144 | -4.3636 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_230A | MIKOMFWA | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-17 |  |  | Earth technology |  | 15 |  | 996 | 1142 | 146 | 264 | OK |  |  |  |  | 369 |  |  | 0 | 200 | 200 | 369 | 2.5274 | 1.8 | [5 empty] | 0 | [7 empty] | SITE RUNNING ON GRC QA IS AWARE | MERU |  | CAPTURED
IHS_CBT_224A | MASAITI | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-17 |  |  | Earth Technology |  | 20 |  | 15129 | 15134 | 5 | 264 | OK | [7 empty] | 10 | 100 | 110 | -10 | -2 | 4.5 | [5 empty] | 0 | [7 empty] | STOLEN FUEL REPORTED OFFICER IN CHARGE 0777117362 OB NUMBER 2488/25 | MERU |  | CAPTURED
IHS_CBT_024M | Ndeke Township | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-25 |  |  | CK Works |  | 30 |  | 11794 | 11873 | 79 | 72 | inconsitent RH |  |  |  |  | 450 |  |  | 15 | 400 | 415 | 435 | 5.5063 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_040M | Seed Of Hope | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-24 |  |  | Lamasat |  | 15 |  | 25238 | 25302 | 64 | 96 | OK |  |  |  |  | 252 |  |  | 28 | 100 | 128 | 224 | 3.5 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_085M | Dangote | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-24 |  |  | Earth technology |  | 13 |  | 8163 | 8196 | 33 | 96 | OK |  |  |  |  | 284 |  |  | 190 | 200 | 390 | 94 | 2.8485 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_306A | TUG-ARGAN | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-24 |  |  | Yanmar |  | 16 |  | 13199 | 13220 | 21 | 96 | OK |  |  |  |  | 236 |  |  | 177 | 300 | 477 | 59 | 2.8095 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_309A | NDOLA LIME | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-13 |  |  | Gen Logic |  | 15 |  | 8886 | 8959 | 73 | 360 | OK |  |  |  |  | 316 |  |  | 40 | 150 | 190 | 276 | 3.7808 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_224M | SKYWAYS KAPIRI ROAD | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-25 |  |  | Generator City |  | 13 |  | 4450 | 4511 | 61 | 72 | OK |  |  |  |  | 263 |  |  | 37 | 250 | 287 | 226 | 3.7049 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_214A | NDOLA FRA SILOS | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Roof Top |  | 2025-10-28 | 2025-10-20 |  |  | Lamasat |  | 20 |  | 12990 | 13134 | 144 | 192 | OK |  |  |  |  | 454 |  |  | 36 | 400 | 436 | 418 | 2.9028 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_021M | Sky ways | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-25 |  |  | CK Works |  | 20 |  | 7619 | 7656 | 37 | 72 | OK |  |  |  |  | 261 |  |  | 87 | 300 | 387 | 174 | 4.7027 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_034M | Mushili Baracks | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-20 |  |  | GL Yanmar |  | 15 |  | 27896 | 27919 | 23 | 192 | OK |  |  |  |  | 230 |  |  | 161 | 200 | 361 | 69 | 3 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_331A | Mushili Baracks | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-16 |  |  | GL Isuzu |  | 10 |  | 10645 | 10671 | 26 | 288 | OK |  |  |  |  | 217 |  |  | 123 | 100 | 223 | 94 | 3.6154 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_220M | RAILWAY STATION | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-20 |  |  | CK Works |  | 20 |  | 7207 | 7269 | 62 | 192 | OK |  |  |  |  | 224 |  |  | 67 | 200 | 267 | 157 | 2.5323 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_004M | Ndola T. Centre | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-26 |  |  | Falcon |  | 20 |  | 500 | 538 | 38 | 48 | OK |  |  |  |  | 202 |  |  | 23 | 300 | 323 | 179 | 4.7105 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_360A | Hilcrest Extension | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-25 |  |  | CK Works |  | 20 |  | 10773 | 10812 | 39 | 72 | OK |  |  |  |  | 346 |  |  | 162 | 150 | 312 | 184 | 4.7179 | 5.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_207A | KANINI | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-24 |  |  | Gen Logic |  | 16 |  | 9276 | 9295 | 19 | 96 | OK |  |  |  |  | 213 |  |  | 146 | 150 | 296 | 67 | 3.5263 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_078M | Bupe | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-25 |  |  | Gen Logic |  | 16 |  | 23144 | 23158 | 14 | 72 | OK |  |  |  |  | 172 |  |  | 126 | 200 | 326 | 46 | 3.2857 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_083M | Nkana East | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-26 |  |  | Gen Logic |  | 16 |  | 4130 | 4151 | 21 | 48 | OK |  |  |  |  | 524 |  |  | 12 | 100 | 112 | 512 | 24.381 | 2 | [5 empty] | 0 | [7 empty] | STOLEN ABOUT 460L REPORTED AT ESTHER LUNGU POLICE POST OB NUMBER 2843/25 | MERU |  | CAPTURED
IHS_CBT_223M | SHOW GROUNDS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-24 |  |  | Generator City |  | 16 |  | FAULTY | FAULTY | #VALUE! | 96 | #VALUE! |  |  |  |  | 105 |  |  | 41 | 300 | 341 | 64 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | MERU |  | CAPTURED
IHS_CBT_237A | NKANA WEST | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-25 |  |  | Earth technology |  | 20 |  | 12054 | 12134 | 80 | 72 | inconsitent RH |  |  |  |  | 317 |  |  | 30 | 300 | 330 | 287 | 3.5875 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_075M | Ndeke Changachanga | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-25 |  |  | Gen Logic |  | 20 |  | 3862 | 3918 | 56 | 72 | OK |  |  |  |  | 320 |  |  | 39 | 200 | 239 | 281 | 5.0179 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_073M | Cedrics Farm | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-25 |  |  | perkins |  | 15 |  | 17427 | 17506 | 79 | 72 | inconsitent RH |  |  |  |  | 280 |  |  | 60 | 250 | 310 | 220 | 2.7848 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_274A | ZNS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-24 |  |  | Gen Logic |  | 16 |  | 13361 | 13444 | 83 | 96 | OK |  |  |  |  | 306 |  |  | 73 | 400 | 473 | 233 | 2.8072 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_084M | Kitwe ZNS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-24 |  |  | CDP |  | 15 |  | 18403 | 18487 | 84 | 96 | OK |  |  |  |  | 264 |  |  | 52 | 200 | 252 | 212 | 2.5238 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_082M | Ndeke Extension | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-25 |  |  | Gen Logic |  | 20 |  | 7633 | 7679 | 46 | 72 | OK |  |  |  |  | 253 |  |  | 40 | 150 | 190 | 213 | 4.6304 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_105M | Buntungwa | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-26 |  |  | Gen Logic |  | 16 |  | 6005 | 6032 | 27 | 48 | OK |  |  |  |  | 120 |  |  | 20 | 150 | 170 | 100 | 3.7037 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_353A | Court Barrifs | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-27 |  |  | CK Works |  | 20 |  | 10722 | 10753 | 31 | 24 | inconsitent RH | [7 empty] | 25 | 250 | 275 | -25 | -0.80645 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_300A | LUBAMBE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-27 |  |  | Jiuan |  | 30 |  | 5324 | 5344 | 20 | 24 | OK |  |  |  |  | 110 |  |  | 25 | 300 | 325 | 85 | 4.25 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_285A | KWACHA | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-25 |  |  | CK Works |  | 20 |  | 5582 | 5630 | 48 | 72 | OK |  |  |  |  | 297 |  |  | 125 | 300 | 425 | 172 | 3.5833 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_296A | KAMUNGA | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-25 |  |  | Gen Logic |  | 16 |  | 6425 | 6487 | 62 | 72 | OK |  |  |  |  | 232 |  |  | 10 | 300 | 310 | 222 | 3.5806 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_107M | Mindolo South | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-17 |  |  | perkins |  | 20 |  | 9494 | 9616 | 122 | 264 | OK |  |  |  |  | 387 |  |  | 13 | 300 | 313 | 374 | 3.0656 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_351A | Riverside Congo Way | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-25 |  |  | CK Works |  | 20 |  | 6119 | 6161 | 42 | 72 | OK |  |  |  |  | 341 |  |  | 132 | 300 | 432 | 209 | 4.9762 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_359A | Cross Crescent | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-25 |  |  | CK Works |  | 20 |  | 5844 | 5901 | 57 | 72 | OK |  |  |  |  | 336 |  |  | 62 | 300 | 362 | 274 | 4.807 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_252A | CHIFUBU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-27 |  |  | Gen Logic |  | 30 |  | 4371 | 4387 | 16 | 24 | OK |  |  |  |  | 115 |  |  | 38 | 100 | 138 | 77 | 4.8125 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_233A | CHIPULUKUSU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-25 |  |  | Earth Technology |  | 15 |  | 5057 | 5109 | 52 | 72 | OK |  |  |  |  | 357 |  |  | 107 | 300 | 407 | 250 | 4.8077 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-27 |  |  | GL Yanmar |  | 20 |  | 524 | 537 | 13 | 24 | OK |  |  |  |  | 50 |  |  | 25 | 150 | 175 | 25 | 1.9231 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_257A | TWAPIA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-26 |  |  | CK Works |  | 20 |  | 12875 | 12894 | 19 | 48 | OK |  |  |  |  | 269 |  |  | 183 | 200 | 383 | 86 | 4.5263 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_222M | TWAPIA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-25 |  |  | Generator City |  | 13 |  | 1151 | 1197 | 46 | 72 | OK |  |  |  |  | 342 |  |  | 158 | 250 | 408 | 184 | 4 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_023M | Twapia | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-25 |  |  | Gen Logic |  | 15 |  | 7737 | 7789 | 52 | 72 | OK |  |  |  |  | 313 |  |  | 121 | 200 | 321 | 192 | 3.6923 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_029M | Zafico | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-25 |  |  | Green Power |  | 15 |  | 3500 | 3548 | 48 | 72 | OK |  |  |  |  | 372 |  |  | 204 | 200 | 404 | 168 | 3.5 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_017M | Overspill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-25 |  |  | Falcon |  | 20 |  | 8952 | 9008 | 56 | 72 | OK |  |  |  |  | 215 |  |  | 47 | 250 | 297 | 168 | 3 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_218A | PAMODZI | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-25 |  |  | Gen Logic |  | 20 |  | 13947 | 13978 | 31 | 72 | OK |  |  |  |  | 258 |  |  | 165 | 200 | 365 | 93 | 3 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_344A | Nkwazi 3G | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-25 |  |  | CK Works |  | 20 |  | 45999 | 46054 | 55 | 72 | OK |  |  |  |  | 329 |  |  | 109 | 250 | 359 | 220 | 4 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_364A | Chifubu Sec. School | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-25 |  |  | CK Works |  | 20 |  | 890 | 913 | 23 | 72 | OK |  |  |  |  | 340 |  |  | 179 | 200 | 379 | 161 | 7 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_335A | Daag Hamershold | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-26 |  |  | LAMASAT |  | 15 |  | 7875 | 7879 | 4 | 48 | OK |  |  |  |  | 50 |  |  | 39 | 200 | 239 | 11 | 2.75 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-28 |  |  | GL Yanmar |  | 20 |  | 537 | 559 | 22 | 0 | inconsitent RH |  |  |  |  | 175 |  |  | 65 | 150 | 215 | 110 | 5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_018M | Nkwanzi | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-26 |  |  | CK Works |  | 20 |  | 1646 | 1682 | 36 | 48 | OK |  |  |  |  | 300 |  |  | 133 | 200 | 333 | 167 | 4.6389 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_127M | Kalulushi | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-25 |  |  | Himoinsa |  | 30 |  | 10984 | 11046 | 62 | 72 | OK |  |  |  |  | 357 |  |  | 109 | 200 | 309 | 248 | 4 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_267A | KALULUSHI EAST | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-25 |  |  | Gen Logic |  | 16 |  | 13955 | 14010 | 55 | 72 | OK |  |  |  |  | 378 |  |  | 147 | 200 | 347 | 231 | 4.2 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_301A | CHIBULUMA TOWN | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-25 |  |  | Gen Logic |  | 16 |  | 9870 | 9940 | 70 | 72 | OK |  |  |  |  | 337 |  |  | 71 | 200 | 271 | 266 | 3.8 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_117M | Chibote | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-25 |  |  | Gen Logic |  | 15 |  | 6066 | 6127 | 61 | 72 | OK |  |  |  |  | 353 |  |  | 98 | 150 | 248 | 255 | 4.1803 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_134M | Kalulushi East | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-25 |  |  | CK Works |  | 20 |  | 8564 | 8622 | 58 | 72 | OK |  |  |  |  | 316 |  |  | 66 | 200 | 266 | 250 | 4.3103 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_159M | Chembe South | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-24 |  |  | Gen Logic |  | 20 |  | FAULTY | FAULTY | #VALUE! | 96 | #VALUE! |  |  |  |  | 255 |  |  | 58 | 200 | 258 | 197 | #VALUE! | 2.5 | [5 empty] | 0 | [7 empty] | faulty controller | MERU |  | CAPTURED
IHS_CBT_146M | Miku Mining | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-26 |  |  | Gen Logic |  | 20 |  | 20778 | 20835 | 57 | 48 | inconsitent RH |  |  |  |  | 200 |  |  | 24 | 200 | 224 | 176 | 3.0877 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_241M | Kagem mine | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-26 |  |  | perkins |  | 20 |  | 14373 | 14418 | 45 | 48 | OK |  |  |  |  | 165 |  |  | 5 | 300 | 305 | 160 | 3.5556 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_119M | Lumumba | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-28 | 2025-10-25 |  |  | Gen Logic |  | 16 |  | 9907 | 9974 | 67 | 72 | OK |  |  |  |  | 317 |  |  | 156 | 150 | 306 | 161 | 2.403 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_252A | CHIFUBU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-28 |  |  | Gen Logic |  | 30 |  | 4387 | 4405 | 18 | 24 | OK |  |  |  |  | 138 |  |  | 51 | 150 | 201 | 87 | 4.8333 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_054M | Mikomfwa Market | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-25 |  |  | Yanmar |  | 16 |  | 12590 | 12626 | 36 | 96 | OK |  |  |  |  | 213 |  |  | 69 | 200 | 269 | 144 | 4 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_049M | Mikomfwa East | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-25 |  |  | Gen Logic |  | 16 |  | 6717 | 6753 | 36 | 96 | OK |  |  |  |  | 224 |  |  | 65 | 200 | 265 | 159 | 4.4167 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_044M | Kafubu Block | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-25 |  |  | Yanmar |  | 16 |  | 18002 | 18057 | 55 | 96 | OK |  |  |  |  | 230 |  |  | 54 | 200 | 254 | 176 | 3.2 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_314A | KAFUBU BLOCK | GNM | Royd | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-25 |  |  | CK Works |  | 20 |  | 7687 | 7734 | 47 | 96 | OK |  |  |  |  | 341 |  |  | 170 | 200 | 370 | 171 | 3.6383 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_048M | Kamirenda Extension | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-25 |  |  | Vitalgen |  | 20 |  | 9861 | 9884 | 23 | 96 | OK |  |  |  |  | 282 |  |  | 190 | 200 | 390 | 92 | 4 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_361A | Mitengo TDRC | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-26 |  |  | CK Works |  | 20 |  | 5802 | 5874 | 72 | 72 | OK |  |  |  |  | 459 |  |  | 135 | 300 | 435 | 324 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_219M | PETAUKE CRESCENT | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-25 |  |  | CK Works |  | 20 |  | 4093 | 4142 | 49 | 96 | OK |  |  |  |  | 304 |  |  | 68 | 300 | 368 | 236 | 4.8163 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_264A | NDOLA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-25 |  |  | Gen Logic |  | 16 |  | 6212 | 6276 | 64 | 96 | OK |  |  |  |  | 330 |  |  | 22 | 300 | 322 | 308 | 4.8125 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_229A | CHIMWEMWE | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-26 |  |  | Gen Logic |  | 20 |  | 583 | 621 | 38 | 72 | OK |  |  |  |  | 487 |  |  | 86 | 100 | 186 | 401 | 10.5526 | 2.5 | [5 empty] | 0 | [7 empty] | STOLEN FUEL ABOUT 187L REPORTED AT CHIMWEMWE POLICE POST 8181/25 | MERU |  | CAPTURED
IHS_CBT_089M | Valley View | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-26 |  |  | ASCOT |  | 30 |  | 3214 | 3240 | 26 | 72 | OK |  |  |  |  | 513 |  |  | 0 | 200 | 200 | 513 | 19.7308 | 4.5 | [5 empty] | 0 | [7 empty] | STOLEN FUEL ABOUT 388L MATTER REPORTED AT RIVERSIDE POLICE OB NUMBER 12972/25 | MERU |  | CAPTURED
IHS_CBT_235M | KAWAMA KCC (Chimwemwe rlf | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-25 |  |  | CK Works |  | 20 |  | 9709 | 9766 | 57 | 96 | OK |  |  |  |  | 328 |  |  | 41 | 200 | 241 | 287 | 5.0351 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_103M | Kwacha central | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-26 |  |  | Gen Logic |  | 16 |  | 990 | 1031 | 41 | 72 | OK |  |  |  |  | 283 |  |  | 91 | 200 | 291 | 192 | 4.6829 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_276A | KAKOLO I & II | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Solar-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-17 |  |  | Jiuan |  | 15 |  | 24187 | 24299 | 112 | 288 | OK |  |  |  |  | 460 |  |  | 135 | 300 | 435 | 325 | 2.9018 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_098M | Bulangililo | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-20 |  |  | Gen Logic |  | 16 |  | 8362 | 8443 | 81 | 216 | OK |  |  |  |  | 275 |  |  | 37 | 100 | 137 | 238 | 2.9383 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_251A | Kitwe Railways | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-25 |  |  | MPI |  | 20 |  | 5949 | 6013 | 64 | 96 | OK |  |  |  |  | 351 |  |  | 105 | 200 | 305 | 246 | 3.8438 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_083M | Nkana East | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-28 |  |  | Gen Logic |  | 16 |  | 4151 | 4156 | 5 | 24 | OK |  |  |  |  | 112 |  |  | 91 | 100 | 191 | 21 | 4.2 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_368A | #N/A | #N/A | FACKSON | #N/A | #N/A | #N/A |  | #N/A | #N/A |  |  | #N/A |  | 2025-10-29 | 2025-10-26 |  |  | #N/A |  | #N/A |  | 10116 | 10158 | 42 | 72 | OK |  |  |  |  | 220 |  |  | 73 | 200 | 273 | 147 | 3.5 | #N/A | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_356A | New Ndeke Village | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-26 |  |  | CK Works |  | 20 |  | 1112 | 1163 | 51 | 72 | OK |  |  |  |  | 330 |  |  | 75 | 150 | 225 | 255 | 5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_345A | Ndeke Changachanga south 3G | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-26 |  |  | Gen Logic |  | 20 |  | 13750 | 13792 | 42 | 72 | OK |  |  |  |  | 205 |  |  | 105 | 300 | 405 | 100 | 2.381 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_081M | Chamboli | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-27 |  |  | Gen Logic |  | 16 |  | 13549 | 13559 | 10 | 48 | OK |  |  |  |  | 116 |  |  | 89 | 150 | 239 | 27 | 2.7 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_250A | SOB | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-25 |  |  | Gen Logic |  | 15 |  | 19671 | FAULTY | #VALUE! | 96 | #VALUE! |  |  |  |  | 155 |  |  | 23 | 150 | 173 | 132 | #VALUE! | 1.8 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_289A | BUPE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-20 |  |  | Gen Logic |  | 15 |  | 13315 | 13346 | 31 | 216 | OK |  |  |  |  | 170 |  |  | 55 | 200 | 255 | 115 | 3.7097 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_222A | CHAMBOLI | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-25 |  |  | Gen Logic |  | 30 |  | 385 | 428 | 43 | 96 | OK |  |  |  |  | 235 |  |  | 35 | 300 | 335 | 200 | 4.6512 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_006M | Lubuto Central | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-25 |  |  | Lamasat |  | 15 |  | 1242 | 1308 | 66 | 96 | OK |  |  |  |  | 305 |  |  | 5 | 300 | 305 | 300 | 4.5455 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_010M | Kabushi | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-24 |  |  | IMG |  | 15 |  | 7790 | 7867 | 77 | 120 | OK |  |  |  |  | 309 |  |  | 31 | 300 | 331 | 278 | 3.6104 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_014M | Lubuto | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-26 |  |  | CK Works |  | 20 |  | 4008 | 4057 | 49 | 72 | OK |  |  |  |  | 334 |  |  | 108 | 300 | 408 | 226 | 4.6122 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_020M | Mushili | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-23 |  |  | CK Works |  | 30 |  | 8586 | 8659 | 73 | 144 | OK |  |  |  |  | 333 |  |  | 5 | 300 | 305 | 328 | 4.4932 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_349A | Kafubu Mall | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-22 |  |  | Gen Logic |  | 16 |  | 16363 | 16426 | 63 | 168 | OK |  |  |  |  | 320 |  |  | 131 | 300 | 431 | 189 | 3 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_091M | Kalalangabo | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-26 |  |  | GL Yanmar |  | 16 |  | 6008 | 6055 | 47 | 72 | OK |  |  |  |  | 252 |  |  | 67 | 200 | 267 | 185 | 3.9362 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_236A | KALALANGABO | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-25 |  |  | ASCOT |  | 30 |  | 226 | 287 | 61 | 96 | OK |  |  |  |  | 331 |  |  | 18 | 300 | 318 | 313 | 5.1311 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_056M | Masangano | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-25 |  |  | GL Yanmar |  | 16 |  | 23142 | 23175 | 33 | 96 | OK |  |  |  |  | 310 |  |  | 91 | 100 | 191 | 219 | 6.6364 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_045M | Tuckugan | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-21 |  |  | GL Yanmar |  | 16 |  | FAULTY | FAULTY | #VALUE! | 192 | #VALUE! | [7 empty] | 10 | 100 | 110 | -10 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_362A | Ndola Central Police | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-26 |  |  | CK Works |  | 20 |  | 12276 | 12347 | 71 | 72 | OK |  |  |  |  | 263 |  |  | 5 | 300 | 305 | 258 | 3.6338 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_022M | Kasembo | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-25 |  |  | Gen Logic |  | 20 |  | 6401 | 6461 | 60 | 96 | OK |  |  |  |  | 410 |  |  | 122 | 300 | 422 | 288 | 4.8 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_033M | Bwana Mukubwa | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-26 |  |  | GL Yanmar |  | 16 |  | 1126 | 1159 | 33 | 72 | OK |  |  |  |  | 306 |  |  | 151 | 200 | 351 | 155 | 4.697 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_246A | NDOLA TOWN | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 |  |  |  | CK Power |  | 30 |  |  | 200 | 200 | 1103016 | OK | [7 empty] | 5 | 400 | 405 | -5 | -0.025 | 4.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_118M | Kamaronde | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-25 |  |  | CK Works |  | 20 |  | 3267 | 3341 | 74 | 96 | OK |  |  |  |  | 382 |  |  | 86 | 200 | 286 | 296 | 4 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_203M | Lufwanyama | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-13 |  |  | Gen Logic |  | 13 |  | FAULTY | FAULTY | #VALUE! | 384 | #VALUE! |  |  |  |  | 205 |  |  | 10 | 300 | 310 | 195 | #VALUE! | 1.5 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_223A | LUFWANYAMA | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-13 |  |  | Gen Logic |  | 20 |  | 6540 | 6616 | 76 | 384 | OK |  |  |  |  | 225 |  |  | 15 | 300 | 315 | 210 | 2.7632 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_114M | Kamatipa North | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-29 | 2025-10-25 |  |  | perkins |  | 15 |  | 1196 | 1261 | 65 | 96 | OK |  |  |  |  | 311 |  |  | 10 | 100 | 110 | 301 | 4.6308 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH |  |  | CAPTURED
IHS_CBT_301A | CHIBULUMA TOWN | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-28 |  |  | Gen Logic |  | 16 |  | 9940 | 9982 | 42 | 48 | OK |  |  |  |  | 271 |  |  | 111 | 250 | 361 | 160 | 3.8095 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_126M | Chibuluma | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-27 |  |  | Gen Logic |  | 20 |  | 4033 | 4063 | 30 | 72 | OK |  |  |  |  | 364 |  |  | 250 | 150 | 400 | 114 | 3.8 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_117M | Chibote | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-28 |  |  | Gen Logic |  | 15 |  | 6127 | 6174 | 47 | 48 | OK |  |  |  |  | 248 |  |  | 69 | 250 | 319 | 179 | 3.8085 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_134M | Kalulushi East | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-28 |  |  | CK Works |  | 20 |  | 8622 | 8670 | 48 | 48 | OK |  |  |  |  | 266 |  |  | 59 | 300 | 359 | 207 | 4.3125 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_132M | Kalulushi West | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-25 |  |  | Gen Logic |  | 20 |  | 5945 | 6018 | 73 | 120 | OK |  |  |  |  | 428 |  |  | 28 | 300 | 328 | 400 | 5.4795 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_267A | KALULUSHI EAST | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-28 |  |  | Gen Logic |  | 16 |  | 14010 | 14064 | 54 | 48 | inconsitent RH |  |  |  |  | 347 |  |  | 117 | 200 | 317 | 230 | 4.2593 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_127M | Kalulushi | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-28 |  |  | Himoinsa |  | 30 |  | 11046 | 11108 | 62 | 48 | inconsitent RH |  |  |  |  | 309 |  |  | 61 | 200 | 261 | 248 | 4 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_206A | KALULUSHI | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-27 |  |  | IMG |  | 15 |  | 7675 | 7731 | 56 | 72 | OK |  |  |  |  | 325 |  |  | 73 | 150 | 223 | 252 | 4.5 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_238M | NAPSA Complex | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-27 |  |  | MPMC |  | 15 |  | 8841 | 8915 | 74 | 72 | inconsitent RH |  |  |  |  | 303 |  |  | 50 | 150 | 200 | 253 | 3.4189 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_277A | ROAN | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-14 |  |  | Gen Logic |  | 16 |  | FAULTY | FAULTY | #VALUE! | 384 | #VALUE! |  |  |  |  | 358 |  |  | 103 | 200 | 303 | 255 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_062M | Roan Township | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-24 |  |  | CK Works |  | 20 |  | 8414 | 8456 | 42 | 144 | OK |  |  |  |  | 140 |  |  | 10 | 200 | 210 | 130 | 3.0952 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_058M | Mikomfwa | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-27 |  |  | Gen Logic |  | 16 |  | 8034 | 8091 | 57 | 72 | OK |  |  |  |  | 205 |  |  | 5 | 200 | 205 | 200 | 3.5088 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_252A | CHIFUBU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-29 |  |  | Gen Logic |  | 30 |  | 4405 | 4424 | 19 | 24 | OK |  |  |  |  | 201 |  |  | 109 | 100 | 209 | 92 | 4.8421 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-28 |  |  | GL Yanmar |  | 20 |  | 559 | 583 | 24 | 48 | OK |  |  |  |  | 215 |  |  | 98 | 100 | 198 | 117 | 4.875 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_226M | CHIFUBU WEST | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-27 |  |  | Generator City |  | 13 |  | 19364 | 19435 | 71 | 72 | OK | [7 empty] | 130 | 200 | 330 | -130 | -1.831 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_222M | TWAPIA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-28 |  |  | Generator City |  | 13 |  | 1197 | 11893 | 10696 | 48 | inconsitent RH |  |  |  |  | 408 |  |  | 108 | 100 | 208 | 300 | 0.028048 | 2 | [5 empty] | 0 | [7 empty] | DG SWAP | SAHARA |  | CAPTURED
IHS_CBT_037M | Minsundu | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 |  |  |  | GL Yanmar |  | 16 |  | FAULTY | FAULTY | #VALUE! | 1103040 | #VALUE! | [7 empty] | 93 | 300 | 393 | -93 | #VALUE! | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_025M | Pamozi Extension | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-27 |  |  | GL Yanmar |  | 16 |  | 3600 | 3671 | 71 | 72 | OK |  |  |  |  | 293 |  |  | 80 | 100 | 180 | 213 | 3 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_005M | Premium Plaza | CCS | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Roof Top |  | 2025-10-30 | 2025-10-25 |  |  | N/A |  | N/A |  | 8870 | 8903 | 33 | 120 | OK |  |  |  |  | 274 |  |  | 161 | 300 | 461 | 113 | 3.4242 | N/A | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_257A | TWAPIA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-28 |  |  | CK Works |  | 20 |  | 12894 | 12933 | 39 | 48 | OK |  |  |  |  | 383 |  |  | 207 | 100 | 307 | 176 | 4.5128 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_336A | Fatima Girls | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-25 |  |  | perkins |  | 15 |  | 11486 | 11551 | 65 | 120 | OK |  |  |  |  | 292 |  |  | 64 | 100 | 164 | 228 | 3.5077 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_092M | Nkana Stadium | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-27 |  |  | Gen Logic |  | 16 |  | 5754 | 5816 | 62 | 72 | OK |  |  |  |  | 273 |  |  | 20 | 100 | 120 | 253 | 4.0806 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_218M | WUSAKILE POLICE CAMP | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-27 |  |  | Generator City |  | 16 |  | 7582 | 7644 | 62 | 72 | OK |  |  |  |  | 180 |  |  | 17 | 100 | 117 | 163 | 2.629 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_305A | LUANGWA KAFUE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-27 |  |  | Yanmar |  | 16 |  | 1158 | 1192 | 34 | 72 | OK |  |  |  |  | 474 |  |  | 474 | 150 | 624 | 0 | 0 | 2 | [5 empty] | 0 | [7 empty] | STOLEN FUEL ABOUT 336L MATTER REPORTED AT LUANGWA POLICE POST OB NUMBER 4875/25 | SAHARA |  | CAPTURED
IHS_CBT_074M | Luangwa | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-27 |  |  | Gen Logic |  | 16 |  | 4758 | 4792 | 34 | 72 | OK |  |  |  |  | 344 |  |  | 11 | 50 | 61 | 333 | 9.7941 | 2 | [5 empty] | 0 | [7 empty] | STOLEN ABOUT 200L REPORTED AT LUANGWA POLICE POST OB NUMBER 4875/25 | SAHARA |  | CAPTURED
IHS_CBT_244A | NDEKE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-27 |  |  | Earth technology |  | 15 |  | 4144 | 4192 | 48 | 72 | OK |  |  |  |  | 351 |  |  | 161 | 50 | 211 | 190 | 3.9583 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_081M | Chamboli | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-29 |  |  | Gen Logic |  | 16 |  | 13559 | 13560 | 1 | 24 | OK |  |  |  |  | 239 |  |  | 16 | 100 | 116 | 223 | 223 | 2 | [5 empty] | 0 | [7 empty] | STOLEN FUEL ABOUT 216LTRS MATTER REPORTED AT WUSAKILE POLICE POST OB NUMBER 12336 | SAHARA |  | CAPTURED
IHS_CBT_342A | Kantanta Street | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-25 |  |  | Gen Logic |  | 20 |  | 4034 | 4115 | 81 | 120 | OK |  |  |  |  | 331 |  |  | 10 | 100 | 110 | 321 | 3.963 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_297A | KITWE POLICE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-27 |  |  | Gen Logic |  | 16 |  | 7864 | 7950 | 86 | 72 | inconsitent RH |  |  |  |  | 320 |  |  | 80 | 50 | 130 | 240 | 2.7907 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_105M | Buntungwa | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-28 |  |  | Gen Logic |  | 16 |  | 6032 | 6063 | 31 | 48 | OK |  |  |  |  | 170 |  |  | 38 | 100 | 138 | 132 | 4.2581 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_228A | MINDOLO | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-26 |  |  | Earth technology |  | 20 |  | 11427 | 11525 | 98 | 96 | inconsitent RH |  |  |  |  | 330 |  |  | 51 | 300 | 351 | 279 | 2.8469 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_024M | Ndeke Township | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-28 |  |  | CK Works |  | 30 |  | 11873 | 1239 | -10634 | 48 | OK |  |  |  |  | 415 |  |  | 10 | 200 | 210 | 405 | -0.038085 | 4.5 | [5 empty] | 0 | [7 empty] | DG SWAP | SAHARA |  | CAPTURED
IHS_CBT_040M | Seed Of Hope | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-28 |  |  | Lamasat |  | 15 |  | 25302 | 25342 | 40 | 48 | OK |  |  |  |  | 128 |  |  | 5 | 100 | 105 | 123 | 3.075 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_283A | MASALA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-24 |  |  | IMG |  | 20 |  | 7899 | 7998 | 99 | 144 | OK |  |  |  |  | 394 |  |  | 52 | 300 | 352 | 342 | 3.4545 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_001M | Kanini | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-27 |  |  | IMG |  | 20 |  | FAULTY | 5689 | #VALUE! | 72 | #VALUE! |  |  |  |  | 300 |  |  | 5 | 300 | 305 | 295 | #VALUE! | 2.5 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_027M | Kantolomba | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-27 |  |  | CK Works |  | 20 |  | 5766 | 5819 | 53 | 72 | OK |  |  |  |  | 396 |  |  | 99 | 300 | 399 | 297 | 5.6038 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_016M | Itawa | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-26 |  |  | Vitalgen |  | 30 |  | 4848 | 4890 | 42 | 96 | OK |  |  |  |  | 463 |  |  | 229 | 200 | 429 | 234 | 5.5714 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_253A | ITAWA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-25 |  |  | Gen Logic |  | 20 |  | 10910 | 10986 | 76 | 120 | OK |  |  |  |  | 324 |  |  | 35 | 200 | 235 | 289 | 3.8026 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_012M | Itawa West | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-25 |  |  | Lamasat |  | 20 |  | 11743 | 11821 | 78 | 120 | OK |  |  |  |  | 294 |  |  | 60 | 200 | 260 | 234 | 3 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_288A | NDOLA BUS STATION | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-25 |  |  | CK Works |  | 20 |  | 485 | 531 | 46 | 120 | OK |  |  |  |  | 360 |  |  | 143 | 200 | 343 | 217 | 4.7174 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_003M | Swimming Pool | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-25 |  |  | CK Works |  | 30 |  | 7364 | 7428 | 64 | 120 | OK |  |  |  |  | 405 |  |  | 97 | 200 | 297 | 308 | 4.8125 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_089M | Valley View | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-29 |  |  | ASCOT |  | 30 |  | 3240 | 3266 | 26 | 24 | inconsitent RH |  |  |  |  | 200 |  |  | 70 | 100 | 170 | 130 | 5 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_269A | SOSOLISO | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-24 |  |  | Jiuan |  | 15 |  | 5757 | 5815 | 58 | 144 | OK |  |  |  |  | 208 |  |  | 13 | 200 | 213 | 195 | 3.3621 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_098M | Bulangililo | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-29 |  |  | Gen Logic |  | 16 |  | 8443 | 8465 | 22 | 24 | OK |  |  |  |  | 137 |  |  | 69 | 200 | 269 | 68 | 3.0909 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_115M | Mindolo | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-25 |  |  | Gen Logic |  | 16 |  | 7637 | 7693 | 56 | 120 | OK | [7 empty] | 124 | 200 | 324 | -124 | -2.2143 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_333A | Mindolo North | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-30 |  |  | perkins |  | 15 |  | 9202 | 9277 | 75 | 0 | inconsitent RH |  |  |  |  | 300 |  |  | 117 | 150 | 267 | 183 | 2.44 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_266A | KAWAMA Copperbelt | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-25 |  |  | Gen Logic |  | 16 |  | 14667 | 14756 | 89 | 120 | OK |  |  |  |  | 255 |  |  | 35 | 200 | 235 | 220 | 2.4719 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_235M | KAWAMA KCC (Chimwemwe rlf | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-29 |  |  | CK Works |  | 20 |  | 9766 | 9785 | 19 | 24 | OK |  |  |  |  | 241 |  |  | 146 | 300 | 446 | 95 | 5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_229A | CHIMWEMWE | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-29 |  |  | Gen Logic |  | 20 |  | 621 | 638 | 17 | 24 | OK |  |  |  |  | 186 |  |  | 89 | 100 | 189 | 97 | 5.7059 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_114M | Kamatipa North | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-30 | 2025-10-25 |  |  | perkins |  | 15 |  | 1261 | 1280 | 19 | 120 | OK |  |  |  |  | 110 |  |  | 27 | 100 | 127 | 83 | 4.3684 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_369A | BUANTUNGWA | #N/A | Royd | #N/A | #N/A | #N/A |  | #N/A | #N/A |  |  | #N/A |  | 2025-10-31 | 2025-09-09 |  |  | #N/A |  | #N/A |  | 0 | 0 | 0 | 1248 | OK |  |  |  |  | 20 |  |  | 0 | 300 | 300 | 20 | #DIV/0! | #N/A | [5 empty] | 0 | [7 empty] | NEW DG | SAHARA |  | CAPTURED
IHS_CBT_043M | Fisenge | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-26 |  |  | Gen Logic |  | 16 |  | FAULTY | FAULTY | #VALUE! | 120 | #VALUE! |  |  |  |  | 414 |  |  | 252 | 200 | 452 | 162 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_265A | NEW TOWN | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-26 |  |  | Gen Logic |  | 16 |  | 1904 | 1952 | 48 | 120 | OK |  |  |  |  | 273 |  |  | 119 | 200 | 319 | 154 | 3.2083 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_052M | Luanshya New Town | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-27 |  |  | Gen Logic |  | 16 |  | 15257 | 15288 | 31 | 96 | OK |  |  |  |  | 295 |  |  | 189 | 200 | 389 | 106 | 3.4194 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_210A | LUANSHYA | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-27 |  |  | CK Works |  | 20 |  | 8097 | 8123 | 26 | 96 | OK |  |  |  |  | 321 |  |  | 223 | 100 | 323 | 98 | 3.7692 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_227M | LUANSHYA EAST | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-26 |  |  | Generator City |  | 16 |  | 7734 | 7764 | 30 | 120 | OK |  |  |  |  | 332 |  |  | 194 | 200 | 394 | 138 | 4.6 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_343A | Chinese Colony | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-27 |  |  | Gen Logic |  | 20 |  | FAULTY | FAULTY | #VALUE! | 96 | #VALUE! |  |  |  |  | 282 |  |  | 190 | 200 | 390 | 92 | #VALUE! | 2.5 | [5 empty] | 0 | [7 empty] | faulty controller | MERU |  | CAPTURED
IHS_CBT_155M | St. Joseph | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-26 |  |  | Gen Logic |  | 16 |  | 6778 | 6850 | 72 | 120 | OK |  |  |  |  | 210 |  |  | 10 | 300 | 310 | 200 | 2.7778 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_167M | Kafubu | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-26 |  |  | LISTER PETTER |  | 16 |  | FAULTY | FAULTY | #VALUE! | 120 | #VALUE! | [7 empty] | 150 | 150 | 300 | -150 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_213M | St. Marys Mission | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-25 |  |  | Pramac |  | 10 |  | FAULTY | FAULTY | #VALUE! | 144 | #VALUE! |  |  |  |  | 110 |  |  | 5 | 300 | 305 | 105 | #VALUE! | 1.5 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_329A | St. Marys Mission (MUTENDA ST. MARYS_1) | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-25 |  |  | METCO |  | 15 |  | FAULTY | FAULTY | #VALUE! | 144 | #VALUE! |  |  |  |  | 175 |  |  | 45 | 200 | 245 | 130 | #VALUE! | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_146M | Miku Mining | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-28 |  |  | Gen Logic |  | 20 |  | 20835 | 20893 | 58 | 72 | OK |  |  |  |  | 224 |  |  | 54 | 200 | 254 | 170 | 2.931 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_102M | Richmond | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-27 |  |  | Gen Logic |  | 16 |  | 3103 | 3144 | 41 | 96 | OK |  |  |  |  | 236 |  |  | 77 | 150 | 227 | 159 | 3.878 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_094M | Kitwe Primary | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-27 |  |  | Gen Logic |  | 16 |  | 2812 | 2864 | 52 | 96 | OK |  |  |  |  | 236 |  |  | 20 | 150 | 170 | 216 | 4.1538 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_242A | PARKLANDS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-27 |  |  | Gen Logic |  | 20 |  | 9957 | 10013 | 56 | 96 | OK |  |  |  |  | 220 |  |  | 24 | 200 | 224 | 196 | 3.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_074M | Luangwa | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-30 |  |  | Gen Logic |  | 16 |  | 4792 | 4808 | 16 | 24 | OK |  |  |  |  | 61 |  |  | 5 | 250 | 255 | 56 | 3.5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_250A | SOB | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-29 |  |  | Gen Logic |  | 15 |  | 19671 | FAULTY | #VALUE! | 48 | #VALUE! |  |  |  |  | 173 |  |  | 11 | 50 | 61 | 162 | #VALUE! | 1.8 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_082M | Ndeke Extension | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-28 |  |  | Gen Logic |  | 20 |  | 7679 | 7705 | 26 | 72 | OK |  |  |  |  | 190 |  |  | 64 | 100 | 164 | 126 | 4.8462 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_079M | Ndeke | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-27 |  |  | CK Works |  | 20 |  | 10221 | 10279 | 58 | 96 | OK |  |  |  |  | 493 |  |  | 205 | 100 | 305 | 288 | 4.9655 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_355A | Ndeke Sub. A | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Gen Only |  |  | Green Field |  | 2025-10-31 | 2025-10-28 |  |  | CK Works |  | 20 |  | 15113 | 15146 | 33 | 72 | OK |  |  |  |  | 374 |  |  | 231 | 100 | 331 | 143 | 4.3333 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_088M | Geddis | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-26 |  |  | CDP |  | 13 |  | 12251 | 12366 | 115 | 120 | OK |  |  |  |  | 305 |  |  | 10 | 300 | 310 | 295 | 2.5652 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_243A | GEDDIS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-25 |  |  | Gen Logic |  | 15 |  | 18076 | 18142 | 66 | 144 | OK |  |  |  |  | 254 |  |  | 29 | 300 | 329 | 225 | 3.4091 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_342A | Kantanta Street | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-30 |  |  | Gen Logic |  | 20 |  | 4115 | 4138 | 23 | 24 | OK |  |  |  |  | 110 |  |  | 22 | 200 | 222 | 88 | 3.8261 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_075M | Ndeke Changachanga | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-28 |  |  | Gen Logic |  | 20 |  | 3918 | 3962 | 44 | 72 | OK |  |  |  |  | 239 |  |  | 22 | 100 | 122 | 217 | 4.9318 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_250A | SOB | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-31 |  |  | Gen Logic |  | 15 |  | FAULTY | FAULTY | #VALUE! | 0 | #VALUE! |  |  |  |  | 61 |  |  | 27 | 100 | 127 | 34 | #VALUE! | 1.8 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_233A | CHIPULUKUSU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-28 |  |  | Earth Technology |  | 15 |  | 5109 | 5158 | 49 | 72 | OK |  |  |  |  | 407 |  |  | 173 | 100 | 273 | 234 | 4.7755 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-30 |  |  | GL Yanmar |  | 20 |  | 583 | 604 | 21 | 24 | OK |  |  |  |  | 198 |  |  | 90 | 100 | 190 | 108 | 5.1429 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_252A | CHIFUBU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-30 |  |  | Gen Logic |  | 30 |  | 4424 | 4449 | 25 | 24 | inconsitent RH |  |  |  |  | 209 |  |  | 89 | 150 | 239 | 120 | 4.8 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_013M | Dola Hill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-27 |  |  | Himoinsa |  | 30 |  | 5965 | 6025 | 60 | 96 | OK |  |  |  |  | 409 |  |  | 49 | 300 | 349 | 360 | 6 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_359A | Cross Crescent | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-28 |  |  | CK Works |  | 20 |  | 5901 | 5936 | 35 | 72 | OK |  |  |  |  | 362 |  |  | 194 | 100 | 294 | 168 | 4.8 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_245A | NORTHRISE | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-31 |  |  | Lamasat |  | 20 |  | 8869 | 8955 | 86 | 0 | inconsitent RH |  |  |  |  | 472 |  |  | 88 | 300 | 388 | 384 | 4.4651 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_018M | Nkwanzi | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-28 |  |  | CK Works |  | 20 |  | 1682 | 1720 | 38 | 72 | OK |  |  |  |  | 333 |  |  | 162 | 300 | 462 | 171 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_361A | Mitengo TDRC | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-29 |  |  | CK Works |  | 20 |  | 5874 | 5941 | 67 | 48 | inconsitent RH |  |  |  |  | 435 |  |  | 133 | 100 | 233 | 302 | 4.5075 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_226A | SAKANIA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-20 |  |  | Gen Logic |  | 16 |  | 1889 | 1984 | 95 | 264 | OK |  |  |  |  | 440 |  |  | 193 | 300 | 493 | 247 | 2.6 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_354A | Mufuchani | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Gen Only |  |  | Green Field |  | 2025-10-31 | 2025-10-26 |  |  | CK Works |  | 20 |  | 13268 | 13332 | 64 | 120 | OK |  |  |  |  | 294 |  |  | 57 | 100 | 157 | 237 | 3.7031 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_113M | Green Belt | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-27 |  |  | IMG |  | 20 |  | 10788 | 10840 | 52 | 96 | OK |  |  |  |  | 363 |  |  | 66 | 100 | 166 | 297 | 5.7115 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_121M | Ichipe | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-25 |  |  | IHS_CBT_121M |  | 15 |  | 14343 | 14411 | 68 | 144 | OK |  |  |  |  | 285 |  |  | 26 | 100 | 126 | 259 | 3.8088 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_249A | BUCHI | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-27 |  |  | Gen Logic |  | 16 |  | 253 | 307 | 54 | 96 | OK |  |  |  |  | 300 |  |  | 93 | 300 | 393 | 207 | 3.8333 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_103M | Kwacha central | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-29 |  |  | Gen Logic |  | 16 |  | 1031 | 1069 | 38 | 48 | OK |  |  |  |  | 291 |  |  | 114 | 200 | 314 | 177 | 4.6579 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_112M | Kamtipa | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-26 |  |  | Gen Logic |  | 16 |  | 633 | 685 | 52 | 120 | OK |  |  |  |  | 338 |  |  | 98 | 300 | 398 | 240 | 4.6154 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_090M | Jambo Drive | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-27 |  |  | Gen Logic |  | 16 |  | 8819 | 8875 | 56 | 96 | OK |  |  |  |  | 312 |  |  | 25 | 300 | 325 | 287 | 5.125 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_263A | NAKADOLI | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-25 |  |  | Gen Logic |  | 16 |  | 7022 | 7089 | 67 | 144 | OK |  |  |  |  | 205 |  |  | 20 | 200 | 220 | 185 | 2.7612 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_080M | Kalambo | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-26 |  |  | Gen Logic |  | 16 |  | 6746 | 6787 | 41 | 120 | OK |  |  |  |  | 468 |  |  | 13 | 100 | 113 | 455 | 11.0976 | 2 | [5 empty] | 0 | [7 empty] | STOLEN ABOUT 296L REPORTED AT rRIVERSIDE POLICE POST OB NUMBER 13109/25 | SAHARA |  | CAPTURED
IHS_CBT_156M | Mpongwe Turnoff | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-27 |  |  | Himoinsa |  | 30 |  | 6946 | 7001 | 55 | 96 | OK |  |  |  |  | 242 |  |  | 45 | 200 | 245 | 197 | 3.5818 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_056M | Masangano | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-29 |  |  | GL Yanmar |  | 16 |  | 23184 | 23175 | -9 | 48 | OK | [7 empty] | 150 | 200 | 350 | -150 | 16.6667 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_008M | Masala | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-26 |  |  | Generator City |  | 13 |  | 6636 | 6710 | 74 | 120 | OK |  |  |  |  | 341 |  |  | 45 | 300 | 345 | 296 | 4 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_004M | Ndola T. Centre | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-28 |  |  | Falcon |  | 20 |  | 538 | 610 | 72 | 72 | OK |  |  |  |  | 323 |  |  | 5 | 300 | 305 | 318 | 4.4167 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_007M | Mpelembe House | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Roof Top |  | 2025-10-31 |  |  |  | Lamasat |  | 15 |  | 8730 | 8862 | 132 | 1103064 | OK | [7 empty] | 5 | 300 | 305 | -5 | -0.037879 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_036M | Lubendo | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-18 |  |  | GL Yanmar |  | 16 |  | 788 | 854 | 66 | 312 | OK |  |  |  |  | 305 |  |  | 53 | 200 | 253 | 252 | 3.8182 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_085M | Dangote | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-28 |  |  | Earth technology |  | 13 |  | 8196 | 8265 | 69 | 72 | OK |  |  |  |  | 390 |  |  | 180 | 200 | 380 | 210 | 3.0435 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_035M | Kaloko | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-26 |  |  | Himoinsa |  | 30 |  | 9644 | 9698 | 54 | 120 | OK |  |  |  |  | 260 |  |  | 5 | 300 | 305 | 255 | 4.7222 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_360A | Hilcrest Extension | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-28 |  |  | CK Works |  | 20 |  | 10812 | 10858 | 46 | 72 | OK |  |  |  |  | 312 |  |  | 95 | 200 | 295 | 217 | 4.7174 | 5.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_108M | Chachacha | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-10-31 | 2025-10-25 |  |  | perkins |  | 20 |  | 1737 | 1810 | 73 | 144 | OK |  |  |  |  | 352 |  |  | 45 | 300 | 345 | 307 | 4.2055 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_133M | Chibuluma Golf Club | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-28 |  |  | Powerol |  | 13 |  | 5591 | 5689 | 98 | 96 | inconsitent RH |  |  |  |  | 422 |  |  | 88 | 200 | 288 | 334 | 3.4082 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_239A | LUFWANYAMA ROAD | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-28 |  |  | Diesel Electric |  | 16 |  | 7518 | 7539 | 21 | 96 | OK |  |  |  |  | 380 |  |  | 0 | 100 | 100 | 380 | 18.0952 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_113M | Green Belt | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-31 |  |  | IMG |  | 20 |  | 10840 | 10853 | 13 | 24 | OK |  |  |  |  | 166 |  |  | 90 | 250 | 340 | 76 | 5.8462 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_351A | Riverside Congo Way | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-28 |  |  | CK Works |  | 20 |  | 6161 | 6235 | 74 | 96 | OK |  |  |  |  | 432 |  |  | 70 | 200 | 270 | 362 | 4.8919 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_080M | Kalambo | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-31 |  |  | Gen Logic |  | 16 |  | 6787 | 6801 | 14 | 24 | OK |  |  |  |  | 113 |  |  | 58 | 200 | 258 | 55 | 3.9286 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_089M | Valley View | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-30 |  |  | ASCOT |  | 30 |  | 3266 | 3306 | 40 | 48 | OK |  |  |  |  | 170 |  |  | 11 | 200 | 211 | 159 | 3.975 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_217M | KITWE MAIN SCHOOL | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-27 |  |  | Generator City |  | 16 |  | 16206 | 16292 | 86 | 120 | OK |  |  |  |  | 370 |  |  | 65 | 200 | 265 | 305 | 3.5465 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_103M | Kwacha central | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-31 |  |  | Gen Logic |  | 16 |  | 1069 | 1073 | 4 | 24 | OK |  |  |  |  | 314 |  |  | 13 | 200 | 213 | 301 | 75.25 | 2 | [5 empty] | 0 | [7 empty] | STOLEN FUEL ABOUT 283LTS REPORTED AT BULANGILO POLICE POST OB NUMBER 7531/25 | SAHARA |  | CAPTURED
IHS_CBT_111M | Chimwemwe Nakadoli | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-25 |  |  | GNM |  | 15 |  | 9786 | 9847 | 61 | 168 | OK |  |  |  |  | 406 |  |  | 253 | 100 | 353 | 153 | 2.5082 | 1.8 | [5 empty] | 0 | [7 empty] | 283 litres of fuel stolen at CBT 103M | SAHARA |  | CAPTURED
IHS_CBT_296A | KAMUNGA | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-28 |  |  | Gen Logic |  | 16 |  | 6487 | 6563 | 76 | 96 | OK |  |  |  |  | 310 |  |  | 10 | 200 | 210 | 300 | 3.9474 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_229A | CHIMWEMWE | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-30 |  |  | Gen Logic |  | 20 |  | 638 | 666 | 28 | 48 | OK |  |  |  |  | 189 |  |  | 38 | 300 | 338 | 151 | 5.3929 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_220A | ITIMPI | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-19 |  |  | MPI |  | 20 |  | 11470 | 11519 | 49 | 312 | OK |  |  |  |  | 362 |  |  | 220 | 100 | 320 | 142 | 2.898 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_118M | Kamaronde | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-29 |  |  | CK Works |  | 20 |  | 3341 | 3413 | 72 | 72 | OK |  |  |  |  | 286 |  |  | 5 | 400 | 405 | 281 | 3.9028 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_206A | KALULUSHI | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-30 |  |  | IMG |  | 15 |  | 7731 | 7760 | 29 | 48 | OK |  |  |  |  | 223 |  |  | 92 | 250 | 342 | 131 | 4.5172 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_238M | NAPSA Complex | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-30 |  |  | MPMC |  | 15 |  | 8915 | 8960 | 45 | 48 | OK |  |  |  |  | 200 |  |  | 38 | 250 | 288 | 162 | 3.6 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_119M | Lumumba | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-28 |  |  | Gen Logic |  | 16 |  | 9974 | 10072 | 98 | 96 | inconsitent RH |  |  |  |  | 306 |  |  | 61 | 200 | 261 | 245 | 2.5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_301A | CHIBULUMA TOWN | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-30 |  |  | Gen Logic |  | 16 |  | 9982 | 10036 | 54 | 48 | inconsitent RH |  |  |  |  | 361 |  |  | 152 | 150 | 302 | 209 | 3.8704 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_117M | Chibote | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-30 |  |  | Gen Logic |  | 15 |  | 6174 | 6196 | 22 | 48 | OK |  |  |  |  | 319 |  |  | 235 | 150 | 385 | 84 | 3.8182 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_267A | KALULUSHI EAST | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-30 |  |  | Gen Logic |  | 16 |  | 14064 | 14112 | 48 | 48 | OK |  |  |  |  | 317 |  |  | 115 | 150 | 265 | 202 | 4.2083 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_127M | Kalulushi | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-30 |  |  | Himoinsa |  | 30 |  | 11108 | 11156 | 48 | 48 | OK |  |  |  |  | 261 |  |  | 69 | 300 | 369 | 192 | 4 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_132M | Kalulushi West | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-30 |  |  | Gen Logic |  | 20 |  | 6018 | 6046 | 28 | 48 | OK |  |  |  |  | 328 |  |  | 172 | 200 | 372 | 156 | 5.5714 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_134M | Kalulushi East | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-30 |  |  | CK Works |  | 20 |  | 8670 | 8718 | 48 | 48 | OK |  |  |  |  | 359 |  |  | 152 | 250 | 402 | 207 | 4.3125 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_310A | CHEMBE CHATI | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-24 |  |  | Gen Logic |  | 17 |  | FAULTY | FAULTY | #VALUE! | 192 | #VALUE! |  |  |  |  | 321 |  |  | 124 | 200 | 324 | 197 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_159M | Chembe South | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-28 |  |  | Gen Logic |  | 20 |  | FAULTY | FAULTY | #VALUE! | 96 | #VALUE! | [7 empty] | 72 | 200 | 272 | -72 | #VALUE! | 2.5 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_328A | Lumpuma | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-25 |  |  | Gen Logic |  | 10 |  | 3527 | 3553 | 26 | 168 | OK |  |  |  |  | 249 |  |  | 174 | 200 | 374 | 75 | 2.8846 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_330A | Funda Junction (Mumena_5) | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-25 |  |  | METCO |  | 15 |  | FAULTY | FAULTY | #VALUE! | 168 | #VALUE! |  |  |  |  | 220 |  |  | 15 | 200 | 215 | 205 | #VALUE! | 1.8 | [5 empty] | 0 | [7 empty] | STOLEN FUEL REPORTED AT KALULUSHI CENTRAL POLICE POST OB#16100/23 | SAHARA |  | CAPTURED
IHS_CBT_241M | Kagem mine | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-28 |  |  | perkins |  | 20 |  | 14418 | 14475 | 57 | 96 | OK |  |  |  |  | 305 |  |  | 150 | 300 | 450 | 155 | 2.7193 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_025M | Pamozi Extension | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-30 |  |  | GL Yanmar |  | 16 |  | 3671 | 3714 | 43 | 48 | OK |  |  |  |  | 180 |  |  | 51 | 300 | 351 | 129 | 3 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-31 |  |  | GL Yanmar |  | 20 |  | 604 | 628 | 24 | 24 | OK |  |  |  |  | 190 |  |  | 70 | 100 | 170 | 120 | 5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_264A | NDOLA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-29 |  |  | Gen Logic |  | 16 |  | 6276 | 6330 | 54 | 72 | OK |  |  |  |  | 322 |  |  | 62 | 300 | 362 | 260 | 4.8148 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_017M | Overspill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-28 |  |  | Falcon |  | 20 |  | 9008 | 9099 | 91 | 96 | OK |  |  |  |  | 297 |  |  | 24 | 250 | 274 | 273 | 3 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_364A | Chifubu Sec. School | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-28 |  |  | CK Works |  | 20 |  | 913 | 940 | 27 | 96 | OK |  |  |  |  | 379 |  |  | 190 | 200 | 390 | 189 | 7 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_252A | CHIFUBU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-31 |  |  | Gen Logic |  | 30 |  | 4449 | 4473 | 24 | 24 | OK |  |  |  |  | 239 |  |  | 123 | 100 | 223 | 116 | 4.8333 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_344A | Nkwazi 3G | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-28 |  |  | CK Works |  | 20 |  | 46054 | 46129 | 75 | 96 | OK |  |  |  |  | 359 |  |  | 59 | 250 | 309 | 300 | 4 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_361A | Mitengo TDRC | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-31 |  |  | CK Works |  | 20 |  | 5941 | 5946 | 5 | 24 | OK |  |  |  |  | 233 |  |  | 210 | 250 | 460 | 23 | 4.6 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_222M | TWAPIA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-30 |  |  | Generator City |  | 13 |  | 11893 | 11927 | 34 | 48 | OK |  |  |  |  | 208 |  |  | 72 | 300 | 372 | 136 | 4 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_023M | Twapia | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-28 |  |  | Gen Logic |  | 15 |  | 7837 | 7909 | 72 | 96 | OK |  |  |  |  | 321 |  |  | 33 | 300 | 333 | 288 | 4 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_029M | Zafico | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-28 |  |  | Green Power |  | 15 |  | 3548 | 3618 | 70 | 96 | OK |  |  |  |  | 404 |  |  | 166 | 200 | 366 | 238 | 3.4 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_218A | PAMODZI | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-28 |  |  | Gen Logic |  | 20 |  | 13978 | 14033 | 55 | 96 | OK |  |  |  |  | 365 |  |  | 200 | 250 | 450 | 165 | 3 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_041M | Kaniki | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-27 |  |  | GL Yanmar |  | 16 |  | 11483 | 11626 | 143 | 120 | inconsitent RH |  |  |  |  | 474 |  |  | 87 | 200 | 287 | 387 | 2.7063 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_362A | Ndola Central Police | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-29 |  |  | CK Works |  | 20 |  | 12347 | 12419 | 72 | 72 | OK |  |  |  |  | 305 |  |  | 89 | 200 | 289 | 216 | 3 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_003M | Swimming Pool | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-30 |  |  | CK Works |  | 30 |  | 7428 | 7473 | 45 | 48 | OK |  |  |  |  | 297 |  |  | 87 | 300 | 387 | 210 | 4.6667 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_253A | ITAWA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-30 |  |  | Gen Logic |  | 20 |  | 10986 | 11033 | 47 | 48 | OK |  |  |  |  | 235 |  |  | 53 | 200 | 253 | 182 | 3.8723 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_021M | Sky ways | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-28 |  |  | CK Works |  | 20 |  | 7656 | 7734 | 78 | 96 | OK |  |  |  |  | 387 |  |  | 28 | 300 | 328 | 359 | 4.6026 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_224M | SKYWAYS KAPIRI ROAD | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-28 |  |  | Generator City |  | 13 |  | 4511 | 4575 | 64 | 96 | OK |  |  |  |  | 287 |  |  | 50 | 300 | 350 | 237 | 3.7031 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_336A | Fatima Girls | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-30 |  |  | perkins |  | 15 |  | 11551 | 11576 | 25 | 48 | OK |  |  |  |  | 164 |  |  | 94 | 300 | 394 | 70 | 2.8 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_024M | Ndeke Township | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-30 |  |  | CK Works |  | 30 |  | 1239 | 1286 | 47 | 48 | OK |  |  |  |  | 210 |  |  | 5 | 400 | 405 | 205 | 4.3617 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_027M | Kantolomba | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-30 |  |  | CK Works |  | 20 |  | 5819 | 5873 | 54 | 48 | inconsitent RH |  |  |  |  | 399 |  |  | 96 | 300 | 396 | 303 | 5.6111 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_040M | Seed Of Hope | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-30 |  |  | Lamasat |  | 15 |  | 25342 | 25362 | 20 | 48 | OK |  |  |  |  | 105 |  |  | 35 | 300 | 335 | 70 | 3.5 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_237A | NKANA WEST | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-28 |  |  | Earth technology |  | 20 |  | 12134 | 12221 | 87 | 96 | OK |  |  |  |  | 330 |  |  | 21 | 200 | 221 | 309 | 3.5517 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_297A | KITWE POLICE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-30 |  |  | Gen Logic |  | 16 |  | 7950 | 7984 | 34 | 48 | OK |  |  |  |  | 130 |  |  | 20 | 200 | 220 | 110 | 3.2353 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_345A | Ndeke Changachanga south 3G | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-29 |  |  | Gen Logic |  | 20 |  | 13792 | 13845 | 53 | 72 | OK |  |  |  |  | 405 |  |  | 63 | 200 | 263 | 342 | 6.4528 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_078M | Bupe | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-28 |  |  | Gen Logic |  | 16 |  | 23158 | 23231 | 73 | 96 | OK |  |  |  |  | 326 |  |  | 89 | 300 | 389 | 237 | 3.2466 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_075M | Ndeke Changachanga | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-31 |  |  | Gen Logic |  | 20 |  | 3962 | 3981 | 19 | 24 | OK |  |  |  |  | 122 |  |  | 26 | 250 | 276 | 96 | 5.0526 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_356A | New Ndeke Village | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-29 |  |  | CK Works |  | 20 |  | 1163 | 1213 | 50 | 72 | OK |  |  |  |  | 405 |  |  | 177 | 250 | 427 | 228 | 4.56 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_334A | Miseshi Village | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-26 |  |  | Generator City |  | 16 |  | 3486 | 3573 | 87 | 144 | OK |  |  |  |  | 437 |  |  | 11 | 300 | 311 | 426 | 4.8966 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_092M | Nkana Stadium | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-30 |  |  | Gen Logic |  | 16 |  | 5816 | 5824 | 8 | 48 | OK |  |  |  |  | 120 |  |  | 87 | 250 | 337 | 33 | 4.125 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_222A | CHAMBOLI | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-29 |  |  | Gen Logic |  | 30 |  | 428 | 467 | 39 | 72 | OK |  |  |  |  | 335 |  |  | 148 | 200 | 348 | 187 | 4.7949 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_105M | Buntungwa | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-30 |  |  | Gen Logic |  | 16 |  | 6063 | 6089 | 26 | 48 | OK |  |  |  |  | 138 |  |  | 41 | 200 | 241 | 97 | 3.7308 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_352A | Parklands TBN | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-27 |  |  | CK Works |  | 20 |  | 8580 | 8649 | 69 | 120 | OK |  |  |  |  | 323 |  |  | 134 | 250 | 384 | 189 | 2.7391 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_083M | Nkana East | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-29 |  |  | Gen Logic |  | 16 |  | 4156 | 4211 | 55 | 72 | OK |  |  |  |  | 191 |  |  | 10 | 100 | 110 | 181 | 3.2909 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_368A | #N/A | #N/A | FACKSON | #N/A | #N/A | #N/A |  | #N/A | #N/A |  |  | #N/A |  | 2025-11-01 | 2025-10-29 |  |  | #N/A |  | #N/A |  | 10158 | 10214 | 56 | 72 | OK |  |  |  |  | 273 |  |  | 88 | 200 | 288 | 185 | 3.3036 | #N/A | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_088M | Geddis | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-31 |  |  | CDP |  | 13 |  | 12366 | 12384 | 18 | 24 | OK |  |  |  |  | 310 |  |  | 0 | 50 | 50 | 310 | 17.2222 | 1.5 | [5 empty] | 0 | [7 empty] | STOLEN ABOUT 256L YET TO BE REPORTED | SAHARA |  | CAPTURED
IHS_CBT_114M | Kamatipa North | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-01 | 2025-10-30 |  |  | perkins |  | 15 |  | 1280 | 1308 | 28 | 48 | OK |  |  |  |  | 127 |  |  | 10 | 250 | 260 | 117 | 4.1786 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_146M | Miku Mining | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-31 |  |  | Gen Logic |  | 20 |  | 20893 | 20967 | 74 | 48 | inconsitent RH |  |  |  |  | 254 |  |  | 30 | 250 | 280 | 224 | 3.027 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_250A | SOB | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-31 |  |  | Gen Logic |  | 15 |  | FAULTY | 21732 | #VALUE! | 48 | #VALUE! |  |  |  |  | 127 |  |  | 167 | 200 | 367 | -40 | #VALUE! | 1.8 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_155M | St. Joseph | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-31 |  |  | Gen Logic |  | 16 |  | 6850 | 6906 | 56 | 48 | inconsitent RH |  |  |  |  | 310 |  |  | 154 | 100 | 254 | 156 | 2.7857 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_261A | CHATI | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Solar-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-25 |  |  | perkins |  | 16 |  | 15034 | 15077 | 43 | 192 | OK |  |  |  |  | 240 |  |  | 73 | 150 | 223 | 167 | 3.8837 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_129M | Emerald Mine Lufwanyama | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-28 |  |  | Gen Logic |  | 15 |  | 25546 | 25611 | 65 | 120 | OK |  |  |  |  | 283 |  |  | 94 | 100 | 194 | 189 | 2.9077 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_133M | Chibuluma Golf Club | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-11-01 |  |  | Powerol |  | 13 |  | 5689 | 5709 | 20 | 24 | OK |  |  |  |  | 288 |  |  | 0 | 100 | 100 | 288 | 14.4 | 1.5 | [5 empty] | 0 | [7 empty] | 214ltrs stolen fuel reported at kalulushi central police OB NUMBER 16105/23 Const. Njamba. 0979315209 | SAHARA |  | CAPTURED
IHS_CBT_239A | LUFWANYAMA ROAD | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-11-01 |  |  | Diesel Electric |  | 16 |  | 7539 | 7551 | 12 | 24 | OK |  |  |  |  | 100 |  |  | 57 | 150 | 207 | 43 | 3.5833 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_359A | Cross Crescent | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-31 |  |  | CK Works |  | 20 |  | 5936 | 5948 | 12 | 48 | OK |  |  |  |  | 294 |  |  | 236 | 300 | 536 | 58 | 4.8333 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_219M | PETAUKE CRESCENT | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-29 |  |  | CK Works |  | 20 |  | 4142 | 4212 | 70 | 96 | OK |  |  |  |  | 368 |  |  | 32 | 400 | 432 | 336 | 4.8 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_013M | Dola Hill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-31 |  |  | Himoinsa |  | 30 |  | 6025 | 6069 | 44 | 48 | OK |  |  |  |  | 349 |  |  | 85 | 300 | 385 | 264 | 6 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_252A | CHIFUBU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-11-01 |  |  | Gen Logic |  | 30 |  | 4473 | 4497 | 24 | 24 | OK |  |  |  |  | 223 |  |  | 107 | 300 | 407 | 116 | 4.8333 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_226M | CHIFUBU WEST | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-30 |  |  | Generator City |  | 13 |  | 19435 | 19509 | 74 | 72 | inconsitent RH | [7 empty] | 137 | 300 | 437 | -137 | -1.8514 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-11-01 |  |  | GL Yanmar |  | 20 |  | 624 | 646 | 22 | 24 | OK |  |  |  |  | 170 |  |  | 60 | 300 | 360 | 110 | 5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_233A | CHIPULUKUSU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-31 |  |  | Earth Technology |  | 15 |  | 5158 | 5179 | 21 | 48 | OK |  |  |  |  | 273 |  |  | 172 | 300 | 472 | 101 | 4.8095 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_257A | TWAPIA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-30 |  |  | CK Works |  | 20 |  | 12933 | 12982 | 49 | 72 | OK |  |  |  |  | 307 |  |  | 86 | 300 | 386 | 221 | 4.5102 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_307A | TVTC | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-25 |  |  | Gen Logic |  | 16 |  | FAULTY | FAULTY | #VALUE! | 192 | #VALUE! |  |  |  |  | 308 |  |  | 10 | 200 | 210 | 298 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_047M | Kamirenda | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-25 |  |  | Gen Logic |  | 16 |  | 13251 | 13391 | 140 | 192 | OK |  |  |  |  | 240 |  |  | 5 | 200 | 205 | 235 | 1.6786 | 2 | [5 empty] | 0 | [7 empty] | SITE RUNNING ON GRC QA IS AWARE | SAHARA |  | CAPTURED
IHS_CBT_065M | Mpatamato East | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-24 |  |  | Yanmar |  | 16 |  | 8626 | 8657 | 31 | 216 | OK | [7 empty] | 58 | 200 | 258 | -58 | -1.871 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_069M | Mpatamato West | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-11-02 |  |  | Gen Logic |  | 16 |  | 16149 | 16167 | 18 | 0 | inconsitent RH |  |  |  |  | 130 |  |  | 58 | 200 | 258 | 72 | 4 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_211A | MPATAMATU | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-24 |  |  | IMG |  | 20 |  | 7951 | 7968 | 17 | 216 | OK | [7 empty] | 119 | 200 | 319 | -119 | -7 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_068M | Mpatamato Central | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-17 |  |  | perkins |  | 15 |  | 11414 | 11418 | 4 | 384 | OK | [7 empty] | 132 | 200 | 332 | -132 | -33 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_049M | Mikomfwa East | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-29 |  |  | Gen Logic |  | 16 |  | 6753 | 6790 | 37 | 96 | OK |  |  |  |  | 265 |  |  | 121 | 200 | 321 | 144 | 3.8919 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_058M | Mikomfwa | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-30 |  |  | Gen Logic |  | 16 |  | 8091 | 8126 | 35 | 72 | OK |  |  |  |  | 205 |  |  | 79 | 200 | 279 | 126 | 3.6 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_230A | MIKOMFWA | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-28 |  |  | Earth technology |  | 15 |  | 1142 | 1198 | 56 | 120 | OK |  |  |  |  | 200 |  |  | 10 | 50 | 60 | 190 | 3.3929 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_161M | Mikata Mpongwe | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Solar-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-26 |  |  | IMG |  | 20 |  | 9973 | 10059 | 86 | 168 | OK |  |  |  |  | 320 |  |  | 24 | 200 | 224 | 296 | 3.4419 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_215M | PHILIP FARM | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Solar-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-26 |  |  | perkins |  | 15 |  | FAULTY | FAULTY | #VALUE! | 168 | #VALUE! |  |  |  |  | 320 |  |  | 76 | 200 | 276 | 244 | #VALUE! | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_181M | Lukanga resettlement | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Solar-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-26 |  |  | CK Works |  | 20 |  | 5645 | 5781 | 136 | 168 | OK |  |  |  |  | 310 |  |  | 10 | 200 | 210 | 300 | 2.2059 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_300A | LUBAMBE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-28 |  |  | Jiuan |  | 30 |  | 5344 | 5407 | 63 | 120 | OK |  |  |  |  | 325 |  |  | 20 | 300 | 320 | 305 | 4.8413 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_251A | Kitwe Railways | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-29 |  |  | MPI |  | 20 |  | 6013 | 6100 | 87 | 96 | OK |  |  |  |  | 305 |  |  | 5 | 300 | 305 | 300 | 3.4483 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_088M | Geddis | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-11-01 |  |  | CDP |  | 13 |  | 12384 | 12399 | 15 | 24 | OK |  |  |  |  | 50 |  |  | 5 | 100 | 105 | 45 | 3 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_073M | Cedrics Farm | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-28 |  |  | perkins |  | 15 |  | 17506 | 17612 | 106 | 120 | OK |  |  |  |  | 310 |  |  | 22 | 250 | 272 | 288 | 2.717 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_305A | LUANGWA KAFUE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-30 |  |  | Yanmar |  | 16 |  | 1192 | 1247 | 55 | 72 | OK |  |  |  |  | 166 |  |  | 166 | 200 | 366 | 0 | 0 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_225M | MUSHIPI | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-26 |  |  | Generator City |  | 16 |  | 9058 | 9188 | 130 | 168 | OK |  |  |  |  | 281 |  |  | 10 | 200 | 210 | 271 | 2.0846 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_081M | Chamboli | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-30 |  |  | Gen Logic |  | 16 |  | 13560 | 13576 | 16 | 72 | OK |  |  |  |  | 116 |  |  | 76 | 100 | 176 | 40 | 2.5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_250A | SOB | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-11-02 |  |  | Gen Logic |  | 15 |  | FAULTY | FAULTY | #VALUE! | 0 | #VALUE! |  |  |  |  | 367 |  |  | 32 | 250 | 282 | 335 | #VALUE! | 1.8 | [5 empty] | 0 | [7 empty] | faulty controller | SAHARA |  | CAPTURED
IHS_CBT_218M | WUSAKILE POLICE CAMP | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-30 |  |  | Generator City |  | 16 |  | 7644 | 7681 | 37 | 72 | OK |  |  |  |  | 117 |  |  | 20 | 200 | 220 | 97 | 2.6216 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_094M | Kitwe Primary | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-31 |  |  | Gen Logic |  | 16 |  | 2864 | 2898 | 34 | 48 | OK |  |  |  |  | 170 |  |  | 24 | 300 | 324 | 146 | 4.2941 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_105M | Buntungwa | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-11-01 |  |  | Gen Logic |  | 16 |  | 6089 | 6092 | 3 | 24 | OK |  |  |  |  | 241 |  |  | 5 | 50 | 55 | 236 | 78.6667 | 2 | [5 empty] | 0 | [7 empty] | Stolen fuel at 105M Buntungwa Matter reported at mindolo police post OB#5793/25 | SAHARA |  | CAPTURED
IHS_CBT_067M | Mpatamato | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-02 | 2025-10-17 |  |  | Gen Logic |  | 16 |  | 6950 | 6973 | 23 | 384 | OK |  |  |  |  | 225 |  |  | 132 | 200 | 332 | 93 | 4.0435 | 2 | [5 empty] | 0 | [10 empty] | CAPTURED
IHS_CBT_083M | Nkana East | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-11-01 |  |  | Gen Logic |  | 16 |  | 4211 | 4229 | 18 | 48 | OK |  |  |  |  | 110 |  |  | 44 | 100 | 144 | 66 | 3.6667 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_244A | NDEKE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-28 |  |  | Earth technology |  | 15 |  | 4192 | 4248 | 56 | 144 | OK | [7 empty] | 5 | 50 | 55 | -5 | -0.089286 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_345A | Ndeke Changachanga south 3G | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-11-01 |  |  | Gen Logic |  | 20 |  | 13845 | 13868 | 23 | 48 | OK |  |  |  |  | 263 |  |  | 5 | 50 | 55 | 258 | 11.2174 | 2.5 | [5 empty] | 0 | [7 empty] | Stolen fuel at 345A Ndeke changa changa, about 194L missing Matter reported at Mulenga police post OB#6471 | MERU |  | CAPTURED
IHS_CBT_228A | MINDOLO | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-30 |  |  | Earth technology |  | 20 |  | 11525 | 11620 | 95 | 96 | OK |  |  |  |  | 351 |  |  | 69 | 100 | 169 | 282 | 2.9684 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_105M | Buntungwa | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-11-02 |  |  | Gen Logic |  | 16 |  | 6092 | 6105 | 13 | 24 | OK |  |  |  |  | 55 |  |  | 5 | 100 | 105 | 50 | 3.8462 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_237A | NKANA WEST | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-11-01 |  |  | Earth technology |  | 20 |  | 12221 | 12279 | 58 | 48 | inconsitent RH |  |  |  |  | 221 |  |  | 10 | 250 | 260 | 211 | 3.6379 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_342A | Kantanta Street | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-25 |  |  | Gen Logic |  | 20 |  | 4138 | 4199 | 61 | 216 | OK | [7 empty] | 5 | 300 | 305 | -5 | -0.081967 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_082M | Ndeke Extension | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-31 |  |  | Gen Logic |  | 20 |  | 7705 | 7721 | 16 | 72 | OK |  |  |  |  | 164 |  |  | 80 | 200 | 280 | 84 | 5.25 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_079M | Ndeke | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-31 |  |  | CK Works |  | 20 |  | 10279 | 10331 | 52 | 72 | OK |  |  |  |  | 305 |  |  | 42 | 400 | 442 | 263 | 5.0577 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_250A | SOB | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-11-02 |  |  | Gen Logic |  | 15 |  | FAULTY | FAULTY | #VALUE! | 24 | #VALUE! |  |  |  |  | 282 |  |  | 5 | 50 | 55 | 277 | #VALUE! | 1.8 | [5 empty] | 0 | [7 empty] | STOLEN FUEL ABOUT 265L REPORTED AT WUSAKILE POLICE POST OB NUMBER 13166/25 | MERU |  | CAPTURED
IHS_CBT_241A | BULANGILILO | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-25 |  |  | perkins |  | 20 |  | 3284 | 3358 | 74 | 216 | OK |  |  |  |  | 259 |  |  | 5 | 300 | 305 | 254 | 3.4324 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_121M | Ichipe | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-31 |  |  | IHS_CBT_121M |  | 15 |  | 14411 | 14438 | 27 | 72 | OK |  |  |  |  | 126 |  |  | 26 | 200 | 226 | 100 | 3.7037 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_285A | KWACHA | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-28 |  |  | CK Works |  | 20 |  | 5630 | 5728 | 98 | 144 | OK |  |  |  |  | 425 |  |  | 73 | 300 | 373 | 352 | 3.5918 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_093M | Kwacha East | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-26 |  |  | Gen Logic |  | 30 |  | 275 | 314 | 39 | 192 | OK |  |  |  |  | 405 |  |  | 138 | 300 | 438 | 267 | 6.8462 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_089M | Valley View | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-11-01 |  |  | ASCOT |  | 30 |  | 3306 | 3346 | 40 | 48 | OK |  |  |  |  | 211 |  |  | 11 | 300 | 311 | 200 | 5 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_354A | Mufuchani | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Gen Only |  |  | Green Field |  | 2025-11-03 | 2025-10-31 |  |  | CK Works |  | 20 |  | 13332 | 13380 | 48 | 72 | OK |  |  |  |  | 157 |  |  | 5 | 200 | 205 | 152 | 3.1667 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_269A | SOSOLISO | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-30 |  |  | Jiuan |  | 15 |  | 5815 | 5884 | 69 | 96 | OK |  |  |  |  | 213 |  |  | 13 | 200 | 213 | 200 | 2.8986 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_090M | Jambo Drive | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-31 |  |  | Gen Logic |  | 16 |  | 8875 | 8943 | 68 | 72 | OK |  |  |  |  | 325 |  |  | 12 | 200 | 212 | 313 | 4.6029 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_087M | Lulamba School | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-25 |  |  | perkins |  | 20 |  | 365 | 430 | 65 | 216 | OK |  |  |  |  | 216 |  |  | 16 | 250 | 266 | 200 | 3.0769 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_099M | Kitwe Town Center | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-20 |  |  | CDP |  | 15 |  | 9226 | 9313 | 87 | 336 | OK |  |  |  |  | 437 |  |  | 210 | 200 | 410 | 227 | 2.6092 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_229A | CHIMWEMWE | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-11-01 |  |  | Gen Logic |  | 20 |  | 666 | 703 | 37 | 48 | OK |  |  |  |  | 338 |  |  | 123 | 100 | 223 | 215 | 5.8108 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_020M | Mushili | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-29 |  |  | CK Works |  | 30 |  | 8659 | 8735 | 76 | 120 | OK |  |  |  |  | 305 |  |  | 5 | 300 | 305 | 300 | 3.9474 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_008M | Masala | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-31 |  |  | Generator City |  | 13 |  | 6710 | 6780 | 70 | 72 | OK |  |  |  |  | 345 |  |  | 65 | 250 | 315 | 280 | 4 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_293A | MUSAKASONKA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-27 |  |  | Gen Logic |  | 20 |  | 1483 | 1562 | 79 | 168 | OK |  |  |  |  | 289 |  |  | 5 | 300 | 305 | 284 | 3.5949 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_001M | Kanini | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-30 |  |  | IMG |  | 20 |  | 5689 | 5753 | 64 | 96 | OK |  |  |  |  | 305 |  |  | 65 | 300 | 365 | 240 | 3.75 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_207A | KANINI | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-28 |  |  | Gen Logic |  | 16 |  | 9295 | 9372 | 77 | 144 | OK |  |  |  |  | 296 |  |  | 25 | 300 | 325 | 271 | 3.5195 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_004M | Ndola T. Centre | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-31 |  |  | Falcon |  | 20 |  | 610 | 667 | 57 | 72 | OK |  |  |  |  | 305 |  |  | 20 | 300 | 320 | 285 | 5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_220M | RAILWAY STATION | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-28 |  |  | CK Works |  | 20 |  | 7269 | 7358 | 89 | 144 | OK |  |  |  |  | 267 |  |  | 5 | 300 | 305 | 262 | 2.9438 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_013M | Dola Hill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-11-02 |  |  | Himoinsa |  | 30 |  | 6069 | 6086 | 17 | 24 | OK |  |  |  |  | 385 |  |  | 286 | 100 | 386 | 99 | 5.8235 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_015M | Yengwe | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-18 |  |  | CK Works |  | 20 |  | 5868 | 5907 | 39 | 384 | OK |  |  |  |  | 367 |  |  | 179 | 100 | 279 | 188 | 4.8205 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_291A | MWATAYANVWA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-22 |  |  | Gen Logic |  | 20 |  | 4601 | 4628 | 27 | 288 | OK |  |  |  |  | 234 |  |  | 100 | 100 | 200 | 134 | 4.963 | 2.5 | [5 empty] | 0 | [7 empty] | OB#5793/25 | SAHARA |  | CAPTURED
IHS_CBT_216M | COOL BANANAS | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 |  |  |  | Generator City |  | 13 |  | 7989 | 8166 | 177 | 1103136 | OK |  |  |  |  | 530 |  |  | 140 | 300 | 440 | 390 | 2.2034 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_014M | Lubuto | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-29 |  |  | CK Works |  | 20 |  | 4057 | 4137 | 80 | 120 | OK |  |  |  |  | 408 |  |  | 27 | 300 | 327 | 381 | 4.7625 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_006M | Lubuto Central | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-29 |  |  | Lamasat |  | 15 |  | 1308 | 1369 | 61 | 120 | OK |  |  |  |  | 305 |  |  | 21 | 300 | 321 | 284 | 4.6557 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_010M | Kabushi | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-29 |  |  | IMG |  | 15 |  | 7867 | 7949 | 82 | 120 | OK |  |  |  |  | 331 |  |  | 28 | 300 | 328 | 303 | 3.6951 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_022M | Kasembo | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-29 |  |  | Gen Logic |  | 20 |  | 6461 | 6535 | 74 | 120 | OK |  |  |  |  | 422 |  |  | 66 | 300 | 366 | 356 | 4.8108 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_016M | Itawa | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-30 |  |  | Vitalgen |  | 30 |  | 4890 | 4934 | 44 | 96 | OK |  |  |  |  | 429 |  |  | 182 | 300 | 482 | 247 | 5.6136 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_033M | Bwana Mukubwa | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-29 |  |  | GL Yanmar |  | 16 |  | 1159 | 1247 | 88 | 120 | OK |  |  |  |  | 351 |  |  | 5 | 300 | 305 | 346 | 3.9318 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_232A | LUBUTO | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-27 |  |  | Gen Logic |  | 20 |  | 11266 | 11353 | 87 | 168 | OK |  |  |  |  | 332 |  |  | 10 | 300 | 310 | 322 | 3.7011 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_338A | Musa Kasonka_3_Rlf | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-25 |  |  | CK Works |  | 20 |  | 11230 | 11345 | 115 | 216 | OK |  |  |  |  | 357 |  |  | 5 | 300 | 305 | 352 | 3.0609 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_349A | Kafubu Mall | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-29 |  |  | Gen Logic |  | 16 |  | 16426 | 16524 | 98 | 120 | OK |  |  |  |  | 431 |  |  | 88 | 300 | 388 | 343 | 3.5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_360A | Hilcrest Extension | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-31 |  |  | CK Works |  | 20 |  | 10858 | 10901 | 43 | 72 | OK |  |  |  |  | 295 |  |  | 89 | 300 | 389 | 206 | 4.7907 | 5.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_009M | Tazama Building | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Roof Top |  | 2025-11-03 | 2025-10-20 |  |  | IMG |  | 16 |  | 29083 | 29223 | 140 | 336 | OK | [7 empty] | 21 | 400 | 421 | -21 | -0.15 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_244A | NDEKE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-30 |  |  | Earth technology |  | 15 |  | 4192 | 4248 | 56 | 96 | OK |  |  |  |  | 211 |  |  | 5 | 50 | 55 | 206 | 3.6786 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_351A | Riverside Congo Way | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-11-01 |  |  | CK Works |  | 20 |  | 6235 | 6279 | 44 | 48 | OK |  |  |  |  | 270 |  |  | 50 | 200 | 250 | 220 | 5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_296A | KAMUNGA | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-11-01 |  |  | Gen Logic |  | 16 |  | 6563 | 6628 | 65 | 48 | inconsitent RH |  |  |  |  | 210 |  |  | 5 | 100 | 105 | 205 | 3.1538 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_107M | Mindolo South | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-03 | 2025-10-28 |  |  | perkins |  | 20 |  | 9616 | 9675 | 59 | 144 | OK |  |  |  |  | 300 |  |  | 92 | 200 | 292 | 208 | 3.5254 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_245A | NORTHRISE | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-10-31 |  |  | Lamasat |  | 20 |  | 8955 | 9024 | 69 | 96 | OK |  |  |  |  | 388 |  |  | 74 | 300 | 374 | 314 | 4.5507 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_210A | LUANSHYA | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-10-31 |  |  | CK Works |  | 20 |  | 8123 | 8156 | 33 | 96 | OK |  |  |  |  | 323 |  |  | 198 | 200 | 398 | 125 | 3.7879 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_048M | Kamirenda Extension | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-10-29 |  |  | Vitalgen |  | 20 |  | 9884 | 9934 | 50 | 144 | OK |  |  |  |  | 390 |  |  | 195 | 150 | 345 | 195 | 3.9 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_064M | Finsansa Basic | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-10-14 |  |  | Yanmar |  | 16 |  | 7884 | 7999 | 115 | 504 | OK |  |  |  |  | 425 |  |  | 68 | 100 | 168 | 357 | 3.1043 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_312A | FISENGE | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-03 |  |  | Yanmar |  | 16 |  | 7466 | 7524 | 58 | 24 | inconsitent RH |  |  |  |  | 476 |  |  | 267 | 200 | 467 | 209 | 3.6034 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_043M | Fisenge | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-10-31 |  |  | Gen Logic |  | 16 |  | 4809 | 4844 | 35 | 96 | OK |  |  |  |  | 452 |  |  | 319 | 200 | 519 | 133 | 3.8 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_314A | KAFUBU BLOCK | GNM | Royd | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-10-29 |  |  | CK Works |  | 20 |  | 7734 | 7766 | 32 | 144 | OK |  |  |  |  | 370 |  |  | 248 | 150 | 398 | 122 | 3.8125 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_044M | Kafubu Block | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-10-29 |  |  | Yanmar |  | 16 |  | 18057 | 18133 | 76 | 144 | OK |  |  |  |  | 254 |  |  | 30 | 150 | 180 | 224 | 2.9474 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_277A | ROAN | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-10-30 |  |  | Gen Logic |  | 16 |  | FAULTY | FAULTY | #VALUE! | 120 | #VALUE! |  |  |  |  | 303 |  |  | 177 | 200 | 377 | 126 | #VALUE! | 2 | [5 empty] | 0 | [7 empty] | faulty controller | MERU |  | CAPTURED
IHS_CBT_062M | Roan Township | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-10-30 |  |  | CK Works |  | 20 |  | 8456 | 8490 | 34 | 120 | OK |  |  |  |  | 210 |  |  | 94 | 200 | 294 | 116 | 3.4118 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_050M | Luanshya Town Center | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-10-26 |  |  | Gen Logic |  | 20 |  | 8593 | 8629 | 36 | 216 | OK |  |  |  |  | 541 |  |  | 364 | 200 | 564 | 177 | 4.9167 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_288A | NDOLA BUS STATION | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-10-30 |  |  | CK Works |  | 20 |  | 531 | 591 | 60 | 120 | OK |  |  |  |  | 343 |  |  | 55 | 300 | 355 | 288 | 4.8 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_234A | CHIWALA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-10-25 |  |  | Gen Logic |  | 20 |  | 21926 | 22004 | 78 | 240 | OK |  |  |  |  | 397 |  |  | 90 | 200 | 290 | 307 | 3.9359 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_306A | TUG-ARGAN | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-10-28 |  |  | Yanmar |  | 16 |  | 13220 | 13312 | 92 | 168 | OK |  |  |  |  | 477 |  |  | 247 | 100 | 347 | 230 | 2.5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_230A | MIKOMFWA | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-02 |  |  | Earth technology |  | 15 |  | 1198 | 1223 | 25 | 48 | OK |  |  |  |  | 60 |  |  | 0 | 200 | 200 | 60 | 2.4 | 1.8 | [5 empty] | 0 | [7 empty] | SITE RUNNING ON GRC QA IS AWARE | MERU |  | CAPTURED
IHS_CBT_339A | Katuni Eden Institute | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-10-27 |  |  | Gen Logic |  | 10 |  | 15989 | 16032 | 43 | 192 | OK |  |  |  |  | 222 |  |  | 88 | 200 | 288 | 134 | 3.1163 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_244A | NDEKE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-03 |  |  | Earth technology |  | 15 |  | 4248 | 4259 | 11 | 24 | OK |  |  |  |  | 55 |  |  | 14 | 300 | 314 | 41 | 3.7273 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_090M | Jambo Drive | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-03 |  |  | Gen Logic |  | 16 |  | 8943 | 8960 | 17 | 24 | OK |  |  |  |  | 212 |  |  | 126 | 100 | 226 | 86 | 5.0588 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_249A | BUCHI | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-10-31 |  |  | Gen Logic |  | 16 |  | 307 | 376 | 69 | 96 | OK |  |  |  |  | 393 |  |  | 91 | 300 | 391 | 302 | 4.3768 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_263A | NAKADOLI | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-10-31 |  |  | Gen Logic |  | 16 |  | 7089 | 7153 | 64 | 96 | OK |  |  |  |  | 220 |  |  | 20 | 200 | 220 | 200 | 3.125 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_112M | Kamtipa | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-10-31 |  |  | Gen Logic |  | 16 |  | 685 | 710 | 25 | 96 | OK |  |  |  |  | 398 |  |  | 13 | 200 | 213 | 385 | 15.4 | 2 | [5 empty] | 0 | [7 empty] | STOLEN FUEL ABOUT 273L MATTER REPORTED AT KAWAMA POLICE POST OB # 10376 | MERU |  | CAPTURED
IHS_CBT_296A | KAMUNGA | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-03 |  |  | Gen Logic |  | 16 |  | 6628 | 6650 | 22 | 24 | OK |  |  |  |  | 105 |  |  | 34 | 200 | 234 | 71 | 3.2273 | 2 | [5 empty] | 0 | [7 empty] | NEW DG | MERU |  | CAPTURED
IHS_CBT_229A | CHIMWEMWE | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-03 |  |  | Gen Logic |  | 20 |  | 703 | 723 | 20 | 24 | OK |  |  |  |  | 223 |  |  | 104 | 100 | 204 | 119 | 5.95 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_113M | Green Belt | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-01 |  |  | IMG |  | 20 |  | 10853 | 10899 | 46 | 72 | OK |  |  |  |  | 340 |  |  | 41 | 300 | 341 | 299 | 6.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_235M | KAWAMA KCC (Chimwemwe rlf | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-10-30 |  |  | CK Works |  | 20 |  | 9785 | 9857 | 72 | 120 | OK |  |  |  |  | 446 |  |  | 45 | 200 | 245 | 401 | 5.5694 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_222M | TWAPIA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-01 |  |  | Generator City |  | 13 |  | 11927 | 11956 | 29 | 72 | OK |  |  |  |  | 372 |  |  | 280 | 200 | 480 | 92 | 3.1724 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_023M | Twapia | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-01 |  |  | Gen Logic |  | 15 |  | 7909 | 7931 | 22 | 72 | OK |  |  |  |  | 333 |  |  | 240 | 300 | 540 | 93 | 4.2273 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_029M | Zafico | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-01 |  |  | Green Power |  | 15 |  | 3618 | 3668 | 50 | 72 | OK |  |  |  |  | 366 |  |  | 191 | 150 | 341 | 175 | 3.5 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_005M | Premium Plaza | CCS | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Roof Top |  | 2025-11-04 | 2025-10-30 |  |  | N/A |  | N/A |  | 8903 | 8978 | 75 | 120 | OK |  |  |  |  | 461 |  |  | 206 | 150 | 356 | 255 | 3.4 | N/A | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_264A | NDOLA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-01 |  |  | Gen Logic |  | 16 |  | 6330 | 6395 | 65 | 72 | OK |  |  |  |  | 362 |  |  | 50 | 300 | 350 | 312 | 4.8 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_025M | Pamozi Extension | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-01 |  |  | GL Yanmar |  | 16 |  | 3714 | 3788 | 74 | 72 | inconsitent RH |  |  |  |  | 351 |  |  | 129 | 300 | 429 | 222 | 3 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_364A | Chifubu Sec. School | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-01 |  |  | CK Works |  | 20 |  | 940 | 966 | 26 | 72 | OK |  |  |  |  | 390 |  |  | 208 | 150 | 358 | 182 | 7 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_344A | Nkwazi 3G | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-01 |  |  | CK Works |  | 20 |  | 46129 | 46188 | 59 | 72 | OK |  |  |  |  | 309 |  |  | 73 | 300 | 373 | 236 | 4 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_018M | Nkwanzi | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-10-31 |  |  | CK Works |  | 20 |  | 1720 | 1790 | 70 | 96 | OK |  |  |  |  | 462 |  |  | 147 | 300 | 447 | 315 | 4.5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_041M | Kaniki | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-01 |  |  | GL Yanmar |  | 16 |  | 11626 | 11631 | 5 | 72 | OK |  |  |  |  | 287 |  |  | 273 | 300 | 573 | 14 | 2.8 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_074M | Luangwa | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-10-31 |  |  | Gen Logic |  | 16 |  | 4808 | 4878 | 70 | 96 | OK |  |  |  |  | 255 |  |  | 5 | 250 | 255 | 250 | 3.5714 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_250A | SOB | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-03 |  |  | Gen Logic |  | 15 |  | FAULTY | FAULTY | #VALUE! | 24 | #VALUE! |  |  |  |  | 55 |  |  | 35 | 50 | 85 | 20 | #VALUE! | 1.8 | [5 empty] | 0 | [7 empty] | faulty controller | MERU |  | CAPTURED
IHS_CBT_228A | MINDOLO | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-03 |  |  | Earth technology |  | 20 |  | 11620 | 11631 | 11 | 24 | OK |  |  |  |  | 169 |  |  | 137 | 200 | 337 | 32 | 2.9091 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_102M | Richmond | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-10-31 |  |  | Gen Logic |  | 16 |  | 3144 | 3228 | 84 | 96 | OK |  |  |  |  | 227 |  |  | 5 | 200 | 205 | 222 | 2.6429 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_242A | PARKLANDS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-10-31 |  |  | Gen Logic |  | 20 |  | 10013 | 10092 | 79 | 96 | OK |  |  |  |  | 224 |  |  | 5 | 300 | 305 | 219 | 2.7722 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_334A | Miseshi Village | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-01 |  |  | Generator City |  | 16 |  | 3573 | 3638 | 65 | 72 | OK |  |  |  |  | 311 |  |  | 5 | 400 | 405 | 306 | 4.7077 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_075M | Ndeke Changachanga | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-01 |  |  | Gen Logic |  | 20 |  | 3981 | 4035 | 54 | 72 | OK |  |  |  |  | 276 |  |  | 10 | 400 | 410 | 266 | 4.9259 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_345A | Ndeke Changachanga south 3G | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-03 |  |  | Gen Logic |  | 20 |  | 13868 | 13884 | 16 | 24 | OK |  |  |  |  | 55 |  |  | 5 | 200 | 205 | 50 | 3.125 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_084M | Kitwe ZNS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-10-28 |  |  | CDP |  | 15 |  | 18487 | 18597 | 110 | 168 | OK |  |  |  |  | 252 |  |  | 5 | 300 | 305 | 247 | 2.2455 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_274A | ZNS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-10-28 |  |  | Gen Logic |  | 16 |  | 13444 | 13554 | 110 | 168 | OK |  |  |  |  | 473 |  |  | 169 | 400 | 569 | 304 | 2.7636 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_222A | CHAMBOLI | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-01 |  |  | Gen Logic |  | 30 |  | 467 | 512 | 45 | 72 | OK |  |  |  |  | 348 |  |  | 141 | 300 | 441 | 207 | 4.6 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_092M | Nkana Stadium | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-01 |  |  | Gen Logic |  | 16 |  | 5824 | 5860 | 36 | 72 | OK |  |  |  |  | 337 |  |  | 179 | 100 | 279 | 158 | 4.3889 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_083M | Nkana East | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-03 |  |  | Gen Logic |  | 16 |  | 4229 | 4261 | 32 | 24 | inconsitent RH |  |  |  |  | 144 |  |  | 20 | 300 | 320 | 124 | 3.875 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_088M | Geddis | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-02 |  |  | CDP |  | 13 |  | 12399 | 12434 | 35 | 48 | OK |  |  |  |  | 105 |  |  | 5 | 100 | 105 | 100 | 2.8571 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_289A | BUPE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-10-29 |  |  | Gen Logic |  | 15 |  | 13346 | 13354 | 8 | 144 | OK |  |  |  |  | 255 |  |  | 17 | 100 | 117 | 238 | 29.75 | 1.8 | [5 empty] | 0 | [7 empty] | Fuel theft at Cbt 289A Bupe about 209L reported at wusakile police station OB NUMBER 13209/25 | MERU |  | CAPTURED
IHS_CBT_117M | Chibote | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-01 |  |  | Gen Logic |  | 15 |  | 6196 | 6251 | 55 | 72 | OK |  |  |  |  | 385 |  |  | 27 | 100 | 127 | 358 | 6.5091 | 1.8 | [5 empty] | 0 | [7 empty] | STOLEN FUEL ABOUT 106L | MERU |  | CAPTURED
IHS_CBT_119M | Lumumba | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-01 |  |  | Gen Logic |  | 16 |  | 10072 | 10134 | 62 | 72 | OK |  |  |  |  | 261 |  |  | 106 | 150 | 256 | 155 | 2.5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_132M | Kalulushi West | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-01 |  |  | Gen Logic |  | 20 |  | 6046 | 6092 | 46 | 72 | OK |  |  |  |  | 372 |  |  | 27 | 200 | 227 | 345 | 7.5 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_267A | KALULUSHI EAST | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-01 |  |  | Gen Logic |  | 16 |  | 14112 | 14166 | 54 | 72 | OK |  |  |  |  | 265 |  |  | 37 | 200 | 237 | 228 | 4.2222 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_127M | Kalulushi | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-01 |  |  | Himoinsa |  | 30 |  | 11156 | 11202 | 46 | 72 | OK |  |  |  |  | 369 |  |  | 185 | 150 | 335 | 184 | 4 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_206A | KALULUSHI | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-01 |  |  | IMG |  | 15 |  | 7760 | 7813 | 53 | 72 | OK |  |  |  |  | 342 |  |  | 103 | 150 | 253 | 239 | 4.5094 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_133M | Chibuluma Golf Club | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-02 |  |  | Powerol |  | 13 |  | 5709 | 5715 | 6 | 48 | OK |  |  |  |  | 100 |  |  | 78 | 200 | 278 | 22 | 3.6667 | 1.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_238M | NAPSA Complex | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-01 |  |  | MPMC |  | 15 |  | 8960 | 9025 | 65 | 72 | OK |  |  |  |  | 288 |  |  | 57 | 150 | 207 | 231 | 3.5538 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_301A | CHIBULUMA TOWN | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-01 |  |  | Gen Logic |  | 16 |  | 10036 | 10084 | 48 | 72 | OK |  |  |  |  | 302 |  |  | 120 | 150 | 270 | 182 | 3.7917 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_114M | Kamatipa North | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-04 | 2025-11-01 |  |  | perkins |  | 15 |  | 1308 | 1362 | 54 | 72 | OK |  |  |  |  | 260 |  |  | 10 | 200 | 210 | 250 | 4.6296 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_203M | Lufwanyama | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 | 2025-10-29 |  |  | Gen Logic |  | 13 |  | FAULTY | 2292 | #VALUE! | 168 | #VALUE! |  |  |  |  | 310 |  |  | 165 | 200 | 365 | 145 | #VALUE! | 1.5 | [5 empty] | 0 | [7 empty] | faulty controller | MERU |  | CAPTURED
IHS_CBT_223A | LUFWANYAMA | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 | 2025-10-29 |  |  | Gen Logic |  | 20 |  | 6616 | 6678 | 62 | 168 | OK |  |  |  |  | 315 |  |  | 145 | 100 | 245 | 170 | 2.7419 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_117M | Chibote | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 | 2025-11-04 |  |  | Gen Logic |  | 15 |  | 6251 | 6263 | 12 | 24 | OK |  |  |  |  | 127 |  |  | 82 | 150 | 232 | 45 | 3.75 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_118M | Kamaronde | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 | 2025-11-01 |  |  | CK Works |  | 20 |  | 3413 | 3494 | 81 | 96 | OK |  |  |  |  | 405 |  |  | 98 | 300 | 398 | 307 | 3.7901 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_129M | Emerald Mine Lufwanyama | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 | 2025-11-02 |  |  | Gen Logic |  | 15 |  | 25611 | 25631 | 20 | 72 | OK |  |  |  |  | 194 |  |  | 138 | 300 | 438 | 56 | 2.8 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | MERU |  | CAPTURED
IHS_CBT_219M | PETAUKE CRESCENT | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 | 2025-11-02 |  |  | CK Works |  | 20 |  | 4212 | 4281 | 69 | 72 | OK |  |  |  |  | 432 |  |  | 87 | 100 | 187 | 345 | 5 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_013M | Dola Hill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 | 2025-11-03 |  |  | Himoinsa |  | 30 |  | 6086 | 6131 | 45 | 48 | OK |  |  |  |  | 386 |  |  | 116 | 100 | 216 | 270 | 6 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_361A | Mitengo TDRC | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 | 2025-11-01 |  |  | CK Works |  | 20 |  | 5946 | 6024 | 78 | 96 | OK |  |  |  |  | 460 |  |  | 85 | 100 | 185 | 375 | 4.8077 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_252A | CHIFUBU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 | 2025-11-02 |  |  | Gen Logic |  | 30 |  | 4497 | 4571 | 74 | 72 | inconsitent RH |  |  |  |  | 407 |  |  | 51 | 100 | 151 | 356 | 4.8108 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_017M | Overspill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 | 2025-11-01 |  |  | Falcon |  | 20 |  | 9099 | 9197 | 98 | 96 | inconsitent RH |  |  |  |  | 274 |  |  | 20 | 100 | 120 | 254 | 2.5918 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 | 2025-11-02 |  |  | GL Yanmar |  | 20 |  | 646 | 701 | 55 | 72 | OK |  |  |  |  | 360 |  |  | 85 | 100 | 185 | 275 | 5 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_243A | GEDDIS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 | 2025-10-31 |  |  | Gen Logic |  | 15 |  | 18142 | 18215 | 73 | 120 | OK |  |  |  |  | 329 |  |  | 72 | 150 | 222 | 257 | 3.5205 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_297A | KITWE POLICE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 | 2025-11-01 |  |  | Gen Logic |  | 16 |  | 7984 | 8059 | 75 | 96 | OK |  |  |  |  | 220 |  |  | 10 | 100 | 110 | 210 | 2.8 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_305A | LUANGWA KAFUE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 | 2025-11-02 |  |  | Yanmar |  | 16 |  | 1247 | 1297 | 50 | 72 | OK |  |  |  |  | 366 |  |  | 10 | 100 | 110 | 356 | 7.12 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_356A | New Ndeke Village | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 | 2025-11-01 |  |  | CK Works |  | 20 |  | 1213 | 1288 | 75 | 96 | OK |  |  |  |  | 427 |  |  | 98 | 100 | 198 | 329 | 4.3867 | 2 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_289A | BUPE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 | 2025-11-04 |  |  | Gen Logic |  | 15 |  | 13354 | 13363 | 9 | 24 | OK |  |  |  |  | 117 |  |  | 84 | 50 | 134 | 33 | 3.6667 | 1.8 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_300A | LUBAMBE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 | 2025-11-02 |  |  | Jiuan |  | 30 |  | 5407 | 5471 | 64 | 72 | OK |  |  |  |  | 320 |  |  | 10 | 100 | 110 | 310 | 4.8438 | 4.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_251A | Kitwe Railways | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 | 2025-11-02 |  |  | MPI |  | 20 |  | 6100 | 6175 | 75 | 72 | inconsitent RH |  |  |  |  | 305 |  |  | 5 | 100 | 105 | 300 | 4 | 2.5 | [5 empty] | 0 | [7 empty] | NORMAL CPH | SAHARA |  | CAPTURED
IHS_CBT_056M | Masangano | GNM | KASOMA | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 |  |  |  | GL Yanmar |  | 16 |  | 23194 | 23201 | 7 | 1103184 | OK | [7 empty] | 251 | 100 | 351 | -251 | -35.8571 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_227A | FIWALE | GNM | KASOMA | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 |  |  |  | GNM |  | 15 |  |  | 5258 | 5258 | 1103184 | OK | [7 empty] | 45 | 100 | 145 | -45 | -0.0085584 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_070M | Kauanga Basic | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 | 2025-10-20 |  |  | Earth technology |  | 20 |  | 12636 | 12676 | 40 | 384 | OK |  |  |  |  | 345 |  |  | 100 | 100 | 200 | 245 | 6.125 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_283A | MASALA | GNM | KASOMA | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 |  |  |  | IMG |  | 20 |  | 7998 | 8091 | 93 | 1103184 | OK | [7 empty] | 26 | 100 | 126 | -26 | -0.27957 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_246A | NDOLA TOWN | GNM | KASOMA | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 |  |  |  | CK Power |  | 30 |  | 200 | 244 | 44 | 1103184 | OK | [7 empty] | 202 | 200 | 402 | -202 | -4.5909 | 4.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_363A | Milemu Sec. School | GNM | KASOMA | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 |  |  |  | CK Works |  | 20 |  | 10287 | 10380 | 93 | 1103184 | OK | [7 empty] | 5 | 300 | 305 | -5 | -0.053763 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_214A | NDOLA FRA SILOS | GNM | KASOMA | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Roof Top |  | 2025-11-05 |  |  |  | Lamasat |  | 20 |  | 13134 | 13256 | 122 | 1103184 | OK | [7 empty] | 70 | 400 | 470 | -70 | -0.57377 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_033M | Bwana Mukubwa | GNM | KASOMA | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 |  |  |  | GL Yanmar |  | 16 |  | 1247 | 1331 | 84 | 1103184 | OK | [7 empty] | 5 | 200 | 205 | -5 | -0.059524 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_014M | Lubuto | GNM | KASOMA | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 |  |  |  | CK Works |  | 20 |  | 4137 | 4191 | 54 | 1103184 | OK | [7 empty] | 67 | 100 | 167 | -67 | -1.2407 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_032M | Cleveland | GNM | KASOMA | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 |  |  |  | CK Works |  | 20 |  | 6299 | 6394 | 95 | 1103184 | OK | [7 empty] | 84 | 60 | 144 | -84 | -0.88421 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_035M | Kaloko | GNM | KASOMA | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 |  |  |  | Himoinsa |  | 30 |  |  | 9768 | 9768 | 1103184 | OK | [7 empty] | 20 | 200 | 220 | -20 | -0.0020475 | 4.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_331A | Mushili Baracks | GNM | KASOMA | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 |  |  |  | GL Isuzu |  | 10 |  | 10671 | 10704 | 33 | 1103184 | OK | [7 empty] | 98 | 200 | 298 | -98 | -2.9697 | 1.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_034M | Mushili Baracks | GNM | KASOMA | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 | 2025-10-28 |  |  | GL Yanmar |  | 15 |  | 27919 | 28025 | 106 | 192 | OK |  |  |  |  | 361 |  |  | 43 | 300 | 343 | 318 | 3 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_089M | Valley View | GNM | JAULA | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 |  |  |  | ASCOT |  | 30 |  | 3346 | 3396 | 50 | 1103184 | OK | [7 empty] | 64 | 200 | 264 | -64 | -1.28 | 4.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_266A | KAWAMA Copperbelt | GNM | JAULA | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 |  |  |  | Gen Logic |  | 16 |  | 14756 | 14857 | 101 | 1103184 | OK | [7 empty] | 5 | 100 | 105 | -5 | -0.049505 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_229A | CHIMWEMWE | GNM | JAULA | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 |  |  |  | Gen Logic |  | 20 |  | 723 | 745 | 22 | 1103184 | OK | [7 empty] | 93 | 100 | 193 | -93 | -4.2273 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_103M | Kwacha central | GNM | JAULA | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 |  |  |  | Gen Logic |  | 16 |  | 1073 | 1123 | 50 | 1103184 | OK | [7 empty] | 13 | 100 | 113 | -13 | -0.26 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_080M | Kalambo | GNM | JAULA | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 |  |  |  | Gen Logic |  | 16 |  | 6801 |  | -6801 | 1103184 | OK | [7 empty] | 82 | 100 | 182 | -82 | 0.012057 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_014M | Lubuto | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-05 |  |  |  | CK Works |  | 20 |  | 4137 | 4191 | 54 | 1103184 | OK | [7 empty] | 67 | 100 | 167 | -67 | -1.2407 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_257A | TWAPIA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | CK Works |  | 20 |  | 12982 | 15057 | 2075 | 1103208 | OK | [7 empty] | 48 | 100 | 148 | -48 | -0.023133 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_017M | Overspill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | Falcon |  | 20 |  | 9197 | 9217 | 20 | 1103208 | OK | [7 empty] | 60 | 50 | 110 | -60 | -3 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | GL Yanmar |  | 20 |  | 701 | 717 | 16 | 1103208 | OK | [7 empty] | 97 | 50 | 147 | -97 | -6.0625 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_252A | CHIFUBU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | Gen Logic |  | 30 |  | 4571 | 4593 | 22 | 1103208 | OK | [7 empty] | 41 | 50 | 91 | -41 | -1.8636 | 4.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_219M | PETAUKE CRESCENT | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | CK Works |  | 20 |  | 4281 | 4298 | 17 | 1103208 | OK | [7 empty] | 102 | 50 | 152 | -102 | -6 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_233A | CHIPULUKUSU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | Earth Technology |  | 15 |  | 5179 | 5253 | 74 | 1103208 | OK | [7 empty] | 102 | 50 | 152 | -102 | -1.3784 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_022M | Kasembo | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | Gen Logic |  | 20 |  |  | 6575 | 6575 | 1103208 | OK | [7 empty] | 10 | 50 | 60 | -10 | -0.0015209 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_238M | NAPSA Complex | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | MPMC |  | 15 |  | 9025 | 9072 | 47 | 1103208 | OK | [7 empty] | 37 | 100 | 137 | -37 | -0.78723 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_206A | KALULUSHI | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | IMG |  | 15 |  | 7813 | 7845 | 32 | 1103208 | OK | [7 empty] | 109 | 100 | 209 | -109 | -3.4062 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_127M | Kalulushi | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | Himoinsa |  | 30 |  | 11202 | 11256 | 54 | 1103208 | OK | [7 empty] | 119 | 100 | 219 | -119 | -2.2037 | 4.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_132M | Kalulushi West | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | Gen Logic |  | 20 |  | 6092 | 6127 | 35 | 1103208 | OK | [7 empty] | 34 | 150 | 184 | -34 | -0.97143 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_134M | Kalulushi East | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | CK Works |  | 20 |  | 8715 | 8784 | 69 | 1103208 | OK | [7 empty] | 118 | 100 | 218 | -118 | -1.7101 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_239A | LUFWANYAMA ROAD | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | Diesel Electric |  | 16 |  | 7551 | 7593 | 42 | 1103208 | OK | [7 empty] | 50 | 100 | 150 | -50 | -1.1905 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_090M | Jambo Drive | GNM | JAULA | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | Gen Logic |  | 16 |  | 8960 | 8993 | 33 | 1103208 | OK | [7 empty] | 56 | 100 | 156 | -56 | -1.697 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_217M | KITWE MAIN SCHOOL | GNM | JAULA | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | Generator City |  | 16 |  | 16292 | 16364 | 72 | 1103208 | OK | [7 empty] | 16 | 100 | 116 | -16 | -0.22222 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_121M | Ichipe | GNM | JAULA | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | IHS_CBT_121M |  | 15 |  | 14438 | 14491 | 53 | 1103208 | OK | [7 empty] | 39 | 100 | 139 | -39 | -0.73585 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_115M | Mindolo | GNM | JAULA | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | Gen Logic |  | 16 |  | 7693 | 7795 | 102 | 1103208 | OK | [7 empty] | 10 | 50 | 60 | -10 | -0.098039 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_087M | Lulamba School | GNM | JAULA | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | perkins |  | 20 |  | 430 | 477 | 47 | 1103208 | OK | [7 empty] | 10 | 50 | 60 | -10 | -0.21277 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_229A | CHIMWEMWE | GNM | JAULA | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | Gen Logic |  | 20 |  | 745 | 755 | 10 | 1103208 | OK | [7 empty] | 19 | 100 | 119 | -19 | -1.9 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_080M | Kalambo | GNM | JAULA | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | Gen Logic |  | 16 |  |  | 6825 | 6825 | 1103208 | OK | [7 empty] | 41 | 100 | 141 | -41 | -0.0060073 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_103M | Kwacha central | GNM | JAULA | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | Gen Logic |  | 16 |  | 1123 | 1149 | 26 | 1103208 | OK | [7 empty] | 13 | 50 | 63 | -13 | -0.5 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_114M | Kamatipa North | GNM | JAULA | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | perkins |  | 15 |  | 1362 | 1410 | 48 | 1103208 | OK | [7 empty] | 10 | 50 | 60 | -10 | -0.20833 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_094M | Kitwe Primary | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | Gen Logic |  | 16 |  | 2899 | 2966 | 67 | 1103208 | OK | [7 empty] | 25 | 50 | 75 | -25 | -0.37313 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_105M | Buntungwa | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | Gen Logic |  | 16 |  | 6105 | 6172 | 67 | 1103208 | OK | [7 empty] | 5 | 50 | 55 | -5 | -0.074627 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_088M | Geddis | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | CDP |  | 13 |  | 12434 | 12473 | 39 | 1103208 | OK | [7 empty] | 5 | 50 | 55 | -5 | -0.12821 | 1.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_237A | NKANA WEST | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | Earth technology |  | 20 |  | 12279 | 12339 | 60 | 1103208 | OK | [7 empty] | 38 | 100 | 138 | -38 | -0.63333 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_250A | SOB | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | Gen Logic |  | 15 |  | faulty | faulty | #VALUE! | 1103208 | #VALUE! | [7 empty] | 20 | 50 | 70 | -20 | #VALUE! | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_108M | Chachacha | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | perkins |  | 20 |  | 1810 | 1872 | 62 | 1103208 | OK | [7 empty] | 52 | 50 | 102 | -52 | -0.83871 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_345A | Ndeke Changachanga south 3G | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | Gen Logic |  | 20 |  | 13884 | 13910 | 26 | 1103208 | OK | [7 empty] | 5 | 50 | 55 | -5 | -0.19231 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_355A | Ndeke Sub. A | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Gen Only |  |  | Green Field |  | 2025-11-06 |  |  |  | CK Works |  | 20 |  | 10818 | 10910 | 92 | 1103208 | OK | [7 empty] | 20 | 50 | 70 | -20 | -0.21739 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_083M | Nkana East | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | Gen Logic |  | 16 |  | 4261 | 4280 | 19 | 1103208 | OK | [7 empty] | 10 | 100 | 110 | -10 | -0.52632 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_193M | Chambatata | GNM | ROYD | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | Yanmar |  | 16 |  | 12744 | 12851 | 107 | 1103208 | OK | [7 empty] | 20 | 50 | 70 | -20 | -0.18692 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_161M | Mikata Mpongwe | GNM | ROYD | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Solar-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | IMG |  | 20 |  | 10059 | 10111 | 52 | 1103208 | OK | [7 empty] | 25 | 50 | 75 | -25 | -0.48077 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_254A | MPONGWE BOMA | GNM | ROYD | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | CK Works |  | 20 |  | 7872 | 7928 | 56 | 1103208 | OK | [7 empty] | 90 | 50 | 140 | -90 | -1.6071 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_065M | Mpatamato East | GNM | ROYD | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | Yanmar |  | 16 |  | 8657 | 8719 | 62 | 1103208 | OK | [7 empty] | 5 | 50 | 55 | -5 | -0.080645 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_058M | Mikomfwa | GNM | ROYD | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | Gen Logic |  | 16 |  |  | 8193 | 8193 | 1103208 | OK | [7 empty] | 24 | 50 | 74 | -24 | -0.0029293 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_307A | TVTC | GNM | ROYD | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | Gen Logic |  | 16 |  | FAULTY | FAULTY | #VALUE! | 1103208 | #VALUE! | [7 empty] | 10 | 50 | 60 | -10 | #VALUE! | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_047M | Kamirenda | GNM | ROYD | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | Gen Logic |  | 16 |  | 13391 | 13458 | 67 | 1103208 | OK | [7 empty] | 0 | 50 | 50 | 0 | 0 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_094M | Kitwe Primary | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | Gen Logic |  | 16 |  | 2898 | 2966 | 68 | 1103208 | OK | [7 empty] | 25 | 50 | 75 | -25 | -0.36765 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_105M | Buntungwa | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | Gen Logic |  | 16 |  | 6105 | 6172 | 67 | 1103208 | OK | [7 empty] | 5 | 50 | 55 | -5 | -0.074627 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_088M | Geddis | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | CDP |  | 13 |  | 12434 | 12473 | 39 | 1103208 | OK | [7 empty] | 5 | 50 | 55 | -5 | -0.12821 | 1.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_237A | NKANA WEST | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | Earth technology |  | 20 |  | 12279 | 12339 | 60 | 1103208 | OK | [7 empty] | 38 | 100 | 138 | -38 | -0.63333 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_250A | SOB | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | Gen Logic |  | 15 |  | faulty | faulty | #VALUE! | 1103208 | #VALUE! | [7 empty] | 20 | 50 | 70 | -20 | #VALUE! | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_108M | Chachacha | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | perkins |  | 20 |  | 1810 | 1872 | 62 | 1103208 | OK | [7 empty] | 50 | 102 | 152 | -50 | -0.80645 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_345A | Ndeke Changachanga south 3G | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | Gen Logic |  | 20 |  | 13884 | 13910 | 26 | 1103208 | OK | [7 empty] | 5 | 50 | 55 | -5 | -0.19231 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_353A | Court Barrifs | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | CK Works |  | 20 |  | 10818 | 10910 | 92 | 1103208 | OK | [7 empty] | 20 | 50 | 70 | -20 | -0.21739 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_083M | Nkana East | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-06 |  |  |  | Gen Logic |  | 16 |  | 4261 | 4280 | 19 | 1103208 | OK | [7 empty] | 10 | 100 | 110 | -10 | -0.52632 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_230A | MIKOMFWA | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Earth technology |  | 15 |  | 1225 | 1250 | 25 | 1103232 | OK | [7 empty] | 114 | 100 | 214 | -114 | -4.56 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_058M | Mikomfwa | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Gen Logic |  | 16 |  | 8193 | 8200 | 7 | 1103232 | OK | [7 empty] | 48 | 200 | 248 | -48 | -6.8571 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_054M | Mikomfwa Market | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Yanmar |  | 16 |  | 12661 | 12721 | 60 | 1103232 | OK | [7 empty] | 89 | 200 | 289 | -89 | -1.4833 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_049M | Mikomfwa East | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Gen Logic |  | 16 |  | 6790 | 6853 | 63 | 1103232 | OK | [7 empty] | 43 | 200 | 243 | -43 | -0.68254 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_227M | LUANSHYA EAST | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Generator City |  | 16 |  | 7764 | 7806 | 42 | 1103232 | OK | [7 empty] | 205 | 100 | 305 | -205 | -4.881 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_307A | TVTC | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Gen Logic |  | 16 |  |  | FAULTY | #VALUE! | 1103232 | #VALUE! | [7 empty] | 21 | 200 | 221 | -21 | #VALUE! | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_047M | Kamirenda | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Gen Logic |  | 16 |  | 13458 | 13466 | 8 | 1103232 | OK | [7 empty] | 20 | 200 | 220 | -20 | -2.5 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_044M | Kafubu Block | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Yanmar |  | 16 |  | 18133 | 18183 | 50 | 1103232 | OK | [7 empty] | 30 | 200 | 230 | -30 | -0.6 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_065M | Mpatamato East | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Yanmar |  | 16 |  | 8719 | 8726 | 7 | 1103232 | OK | [7 empty] | 29 | 150 | 179 | -29 | -4.1429 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_064M | Finsansa Basic | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Yanmar |  | 16 |  | 7999 | 8041 | 42 | 1103232 | OK | [7 empty] | 25 | 200 | 225 | -25 | -0.59524 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_123M | Mukuba University | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | IMG |  | 15 |  | 11805 | 11923 | 118 | 1103232 | OK | [7 empty] | 29 | 200 | 229 | -29 | -0.24576 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_113M | Green Belt | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | IMG |  | 20 |  | 10899 | 10946 | 47 | 1103232 | OK | [7 empty] | 69 | 300 | 369 | -69 | -1.4681 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_266A | KAWAMA Copperbelt | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Gen Logic |  | 16 |  | 14857 | 14909 | 52 | 1103232 | OK | [7 empty] | 0 | 100 | 100 | 0 | 0 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_114M | Kamatipa North | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | perkins |  | 15 |  | 1410 | 1412 | 2 | 1103232 | OK | [7 empty] | 51 | 200 | 251 | -51 | -25.5 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_112M | Kamtipa | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Gen Logic |  | 16 |  | 710 | 752 | 42 | 1103232 | OK | [7 empty] | 27 | 200 | 227 | -27 | -0.64286 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_235M | KAWAMA KCC (Chimwemwe rlf | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | CK Works |  | 20 |  | 9857 | 9897 | 40 | 1103232 | OK | [7 empty] | 45 | 200 | 245 | -45 | -1.125 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_229A | CHIMWEMWE | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Gen Logic |  | 20 |  | 755 | 774 | 19 | 1103232 | OK | [7 empty] | 24 | 300 | 324 | -24 | -1.2632 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_296A | KAMUNGA | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Gen Logic |  | 16 |  | 6650 | 6713 | 63 | 1103232 | OK | [7 empty] | 5 | 200 | 205 | -5 | -0.079365 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_103M | Kwacha central | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Gen Logic |  | 16 |  | 1149 | 1164 | 15 | 1103232 | OK | [7 empty] | 13 | 150 | 163 | -13 | -0.86667 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_241A | BULANGILILO | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | perkins |  | 20 |  | 3358 | 3427 | 69 | 1103232 | OK | [7 empty] | 69 | 100 | 169 | -69 | -1 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_093M | Kwacha East | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Gen Logic |  | 30 |  | 314 | 371 | 57 | 1103232 | OK | [7 empty] | 47 | 200 | 247 | -47 | -0.82456 | 4.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_089M | Valley View | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | ASCOT |  | 30 |  | 3396 | 3427 | 31 | 1103232 | OK | [7 empty] | 91 | 200 | 291 | -91 | -2.9355 | 4.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_354A | Mufuchani | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Gen Only |  |  | Green Field |  | 2025-11-07 |  |  |  | CK Works |  | 20 |  | 13380 | 13436 | 56 | 1103232 | OK | [7 empty] | 5 | 150 | 155 | -5 | -0.089286 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_090M | Jambo Drive | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Gen Logic |  | 16 |  | 8993 | 9021 | 28 | 1103232 | OK | [7 empty] | 12 | 200 | 212 | -12 | -0.42857 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_351A | Riverside Congo Way | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | CK Works |  | 20 |  | 6323 | 6346 | 23 | 1103232 | OK | [7 empty] | 38 | 100 | 138 | -38 | -1.6522 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_269A | SOSOLISO | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Jiuan |  | 15 |  | 5884 | 5949 | 65 | 1103232 | OK | [7 empty] | 13 | 100 | 113 | -13 | -0.2 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_300A | LUBAMBE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Jiuan |  | 30 |  | 5471 | 5488 | 17 | 1103232 | OK | [7 empty] | 20 | 400 | 420 | -20 | -1.1765 | 4.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_353A | Court Barrifs | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | CK Works |  | 20 |  | 10910 | 10916 | 6 | 1103232 | OK | [7 empty] | 48 | 200 | 248 | -48 | -8 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_105M | Buntungwa | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Gen Logic |  | 16 |  | 6132 | 6142 | 10 | 1103232 | OK | [7 empty] | 13 | 200 | 213 | -13 | -1.3 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_228A | MINDOLO | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Earth technology |  | 20 |  | 11631 | 11705 | 74 | 1103232 | OK | [7 empty] | 132 | 200 | 332 | -132 | -1.7838 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_108M | Chachacha | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | perkins |  | 20 |  | 1872 | 1883 | 11 | 1103232 | OK | [7 empty] | 57 | 300 | 357 | -57 | -5.1818 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_237A | NKANA WEST | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Earth technology |  | 20 |  | 12339 | 12364 | 25 | 1103232 | OK | [7 empty] | 48 | 300 | 348 | -48 | -1.92 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_083M | Nkana East | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Gen Logic |  | 16 |  | 4280 | 4295 | 15 | 1103232 | OK | [7 empty] | 44 | 300 | 344 | -44 | -2.9333 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_073M | Cedrics Farm | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | perkins |  | 15 |  | 17612 | 17703 | 91 | 1103232 | OK | [7 empty] | 10 | 200 | 210 | -10 | -0.10989 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_074M | Luangwa | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Gen Logic |  | 16 |  | 4878 | 4927 | 49 | 1103232 | OK | [7 empty] | 30 | 100 | 130 | -30 | -0.61224 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_305A | LUANGWA KAFUE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Yanmar |  | 16 |  | 1297 | 1326 | 29 | 1103232 | OK | [7 empty] | 10 | 100 | 110 | -10 | -0.34483 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_225M | MUSHIPI | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Generator City |  | 16 |  | 9188 | 9294 | 106 | 1103232 | OK | [7 empty] | 5 | 50 | 55 | -5 | -0.04717 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_081M | Chamboli | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Gen Logic |  | 16 |  | 13910 | 13928 | 18 | 1103232 | OK | [7 empty] | 37 | 50 | 87 | -37 | -2.0556 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_345A | Ndeke Changachanga south 3G | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Gen Logic |  | 20 |  | 6175 | 6207 | 32 | 1103232 | OK | [7 empty] | 5 | 50 | 55 | -5 | -0.15625 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_251A | Kitwe Railways | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | MPI |  | 20 |  | 6175 | 6207 | 32 | 1103232 | OK | [7 empty] | 5 | 100 | 105 | -5 | -0.15625 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_297A | KITWE POLICE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Gen Logic |  | 16 |  | 8059 | 8094 | 35 | 1103232 | OK | [7 empty] | 10 | 50 | 60 | -10 | -0.28571 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_088M | Geddis | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | CDP |  | 13 |  | 12473 | 12490 | 17 | 1103232 | OK | [7 empty] | 5 | 50 | 55 | -5 | -0.29412 | 1.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_118M | Kamaronde | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | CK Works |  | 20 |  | 3497 | 3557 | 60 | 1103232 | OK | [7 empty] | 146 | 200 | 346 | -146 | -2.4333 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_238M | NAPSA Complex | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | MPMC |  | 15 |  | 9072 | 9098 | 26 | 1103232 | OK | [7 empty] | 43 | 150 | 193 | -43 | -1.6538 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_133M | Chibuluma Golf Club | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Powerol |  | 13 |  | 5715 | 5756 | 41 | 1103232 | OK | [7 empty] | 130 | 150 | 280 | -130 | -3.1707 | 1.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_267A | KALULUSHI EAST | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Gen Logic |  | 16 |  | 14166 | 14210 | 44 | 1103232 | OK | [7 empty] | 52 | 150 | 202 | -52 | -1.1818 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_132M | Kalulushi West | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Gen Logic |  | 20 |  | 6127 | 6146 | 19 | 1103232 | OK | [7 empty] | 79 | 250 | 329 | -79 | -4.1579 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_134M | Kalulushi East | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | CK Works |  | 20 |  | 8784 | 8808 | 24 | 1103232 | OK | [7 empty] | 114 | 150 | 264 | -114 | -4.75 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_126M | Chibuluma | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Gen Logic |  | 20 |  | 4063 | 4147 | 84 | 1103232 | OK | [7 empty] | 80 | 150 | 230 | -80 | -0.95238 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_119M | Lumumba | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Gen Logic |  | 16 |  | 10134 | 10238 | 104 | 1103232 | OK | [7 empty] | 296 | 100 | 396 | -296 | -2.8462 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_117M | Chibote | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Gen Logic |  | 15 |  | 6263 | 6316 | 53 | 1103232 | OK | [7 empty] | 30 | 100 | 130 | -30 | -0.56604 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_146M | Miku Mining | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Gen Logic |  | 20 |  | 20967 | 21049 | 82 | 1103232 | OK | [7 empty] | 25 | 300 | 325 | -25 | -0.30488 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_259A | KAMAKANGA I & II | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | perkins |  | 20 |  | 21732 | 21799 | 67 | 1103232 | OK | [7 empty] | 180 | 100 | 280 | -180 | -2.6866 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_241M | Kagem mine | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | perkins |  | 20 |  | 14475 | 14550 | 75 | 1103232 | OK | [7 empty] | 180 | 200 | 380 | -180 | -2.4 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_301A | CHIBULUMA TOWN | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Gen Logic |  | 16 |  | 10084 | 10152 | 68 | 1103232 | OK | [7 empty] | 11 | 100 | 111 | -11 | -0.16176 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_016M | Itawa | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Vitalgen |  | 30 |  | 4934 | 4987 | 53 | 1103232 | OK | [7 empty] | 185 | 200 | 385 | -185 | -3.4906 | 4.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_024M | Ndeke Township | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | CK Works |  | 30 |  | 1286 | 1366 | 80 | 1103232 | OK | [7 empty] | 5 | 300 | 305 | -5 | -0.0625 | 4.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_224M | SKYWAYS KAPIRI ROAD | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Generator City |  | 13 |  | 4575 | 4627 | 52 | 1103232 | OK | [7 empty] | 157 | 200 | 357 | -157 | -3.0192 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_027M | Kantolomba | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | CK Works |  | 20 |  | 5873 | 5650 | -223 | 1103232 | OK | [7 empty] | 5 | 400 | 405 | -5 | 0.022422 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_346A | Nilkant Mine | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Solar-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | CK Works |  | 20 |  | 11553 | 11650 | 97 | 1103232 | OK | [7 empty] | 47 | 200 | 247 | -47 | -0.48454 | 2.5 | [5 empty] | 0 | [8 empty] | IHS PUMA |  | CAPTURED
IHS_CBT_336A | Fatima Girls | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | perkins |  | 15 |  | 11576 | 11638 | 62 | 1103232 | OK | [7 empty] | 134 | 200 | 334 | -134 | -2.1613 | 1.8 | [5 empty] | 0 | [8 empty] | IHS PUMA |  | CAPTURED
IHS_CBT_325A | KALOKO KAFULAFUTA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | GL Yanmar |  | 15 |  | 7666 | 7546 | -120 | 1103232 | OK | [7 empty] | 43 | 100 | 143 | -43 | 0.35833 | 1.8 | [5 empty] | 0 | [8 empty] | IHS PUMA |  | CAPTURED
IHS_CBT_085M | Dangote | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Earth technology |  | 13 |  | 3196 | 2343 | -853 | 1103232 | OK | [7 empty] | 51 | 100 | 151 | -51 | 0.059789 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_003M | Swimming Pool | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | CK Works |  | 30 |  | 7473 | 7542 | 69 | 1103232 | OK | [7 empty] | 55 | 400 | 455 | -55 | -0.7971 | 4.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_022M | Kasembo | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Gen Logic |  | 20 |  | 6535 | 6599 | 64 | 1103232 | OK | [7 empty] | 58 | 300 | 358 | -58 | -0.90625 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_014M | Lubuto | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | CK Works |  | 20 |  | 4191 | 4220 | 29 | 1103232 | OK | [7 empty] | 30 | 400 | 430 | -30 | -1.0345 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_006M | Lubuto Central | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Lamasat |  | 15 |  | 1369 | 1451 | 82 | 1103232 | OK | [7 empty] | 5 | 300 | 305 | -5 | -0.060976 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_362A | Ndola Central Police | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | CK Works |  | 20 |  |  | 12514 | 12514 | 1103232 | OK | [7 empty] | 5 | 300 | 305 | -5 | -0.00039955 | 4.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_060M | Kansafu | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Falcon |  | 16 |  | 1608 | 1668 | 60 | 1103232 | OK | [7 empty] | 236 | 200 | 436 | -236 | -3.9333 | 2 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_306A | TUG-ARGAN | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Yanmar |  | 16 |  | 13312 | 13357 | 45 | 1103232 | OK | [7 empty] | 257 | 100 | 357 | -257 | -5.7111 | 2 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_288A | NDOLA BUS STATION | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | CK Works |  | 20 |  | 591 | 629 | 38 | 1103232 | OK | [7 empty] | 172 | 200 | 372 | -172 | -4.5263 | 2.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_234A | CHIWALA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Gen Logic |  | 20 |  | 22004 | 22050 | 46 | 1103232 | OK | [7 empty] | 98 | 200 | 298 | -98 | -2.1304 | 4.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_040M | Seed Of Hope | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Lamasat |  | 15 |  | 25362 | 25422 | 60 | 1103232 | OK | [7 empty] | 99 | 200 | 299 | -99 | -1.65 | 1.8 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_021M | Sky ways | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | CK Works |  | 20 |  | 7656 | 7794 | 138 | 1103232 | OK | [7 empty] | 23 | 400 | 423 | -23 | -0.16667 | 2.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_219M | PETAUKE CRESCENT | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | CK Works |  | 20 |  | 4298 | 4315 | 17 | 1103232 | OK | [7 empty] | 67 | 200 | 267 | -67 | -3.9412 | 2.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_013M | Dola Hill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Himoinsa |  | 30 |  | 6131 | 6164 | 33 | 1103232 | OK | [7 empty] | 18 | 200 | 218 | -18 | -0.54545 | 4.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_017M | Overspill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Falcon |  | 20 |  | 9217 | 9238 | 21 | 1103232 | OK | [7 empty] | 47 | 200 | 247 | -47 | -2.2381 | 2.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_264A | NDOLA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Gen Logic |  | 16 |  | 6395 | 6443 | 48 | 1103232 | OK | [7 empty] | 119 | 100 | 219 | -119 | -2.4792 | 2 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | GL Yanmar |  | 20 |  | 717 | 724 | 7 | 1103232 | OK | [7 empty] | 109 | 200 | 309 | -109 | -15.5714 | 2 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_252A | CHIFUBU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Gen Logic |  | 30 |  | 4593 | 4609 | 16 | 1103232 | OK | [7 empty] | 14 | 200 | 214 | -14 | -0.875 | 4.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_361A | Mitengo TDRC | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | CK Works |  | 20 |  | 6024 | 6041 | 17 | 1103232 | OK | [7 empty] | 108 | 250 | 358 | -108 | -6.3529 | 2.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_364A | Chifubu Sec. School | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | CK Works |  | 20 |  | 966 | 1027 | 61 | 1103232 | OK | [7 empty] | 69 | 200 | 269 | -69 | -1.1311 | 4.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_005M | Premium Plaza | CCS | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Roof Top |  | 2025-11-07 |  |  |  | N/A |  | N/A |  | 8978 | 9016 | 38 | 1103232 | OK | [7 empty] | 223 | 100 | 323 | -223 | -5.8684 | N/A | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_245A | NORTHRISE | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Lamasat |  | 20 |  | 9024 | 9089 | 65 | 1103232 | OK | [7 empty] | 81 | 200 | 281 | -81 | -1.2462 | 2.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_233A | CHIPULUKUSU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Earth Technology |  | 15 |  | 5253 | 5266 | 13 | 1103232 | OK | [7 empty] | 89 | 200 | 289 | -89 | -6.8462 | 1.8 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_029M | Zafico | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Green Power |  | 15 |  | 3668 | 3729 | 61 | 1103232 | OK | [7 empty] | 133 | 300 | 433 | -133 | -2.1803 | 1.8 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_291A | MWATAYANVWA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Gen Logic |  | 20 |  | 4628 | 4666 | 38 | 1103232 | OK | [7 empty] | 17 | 200 | 217 | -17 | -0.44737 | 2.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_017M | Overspill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | Falcon |  | 20 |  | 9238 | 9251 | 13 | 1103232 | OK | [7 empty] | 0 | 50 | 50 | 0 | 0 | 2.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_018M | Nkwanzi | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | CK Works |  | 20 |  | 1790 | 1851 | 61 | 1103232 | OK | [7 empty] | 172 | 200 | 372 | -172 | -2.8197 | 2.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_257A | TWAPIA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-07 |  |  |  | CK Works |  | 20 |  | 13057 | 13081 | 24 | 1103232 | OK | [7 empty] | 40 | 200 | 240 | -40 | -1.6667 | 2.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_181M | Lukanga resettlement | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Solar-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | CK Works |  | 20 |  | 5781 | 5865 | 84 | 1103256 | OK | [7 empty] | 15 | 400 | 415 | -15 | -0.17857 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_215M | PHILIP FARM | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Solar-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | perkins |  | 15 |  |  | FAULTY | #VALUE! | 1103256 | #VALUE! | [7 empty] | 98 | 300 | 398 | -98 | #VALUE! | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_161M | Mikata Mpongwe | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Solar-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | IMG |  | 20 |  | 10111 | 10125 | 14 | 1103256 | OK | [7 empty] | 20 | 300 | 320 | -20 | -1.4286 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_321A | Fred Station (MAPOSA_2) | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | Gen Logic |  | 20 |  | 14249 | 14266 | 17 | 1103256 | OK | [7 empty] | 10 | 100 | 110 | -10 | -0.58824 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_042 | GOLDEN LAY | #N/A | Royd | #N/A | #N/A | #N/A |  | #N/A | #N/A |  |  | #N/A |  | 2025-11-08 |  |  |  | #N/A |  | #N/A |  | 8293 | 8350 | 57 | 1103256 | OK | [7 empty] | 0 | 100 | 100 | 0 | 0 | #N/A | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_314A | KAFUBU BLOCK | GNM | Royd | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | CK Works |  | 20 |  | 7766 | 7844 | 78 | 1103256 | OK | [7 empty] | 116 | 200 | 316 | -116 | -1.4872 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_210A | LUANSHYA | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | CK Works |  | 20 |  | 8156 | 8208 | 52 | 1103256 | OK | [7 empty] | 200 | 200 | 400 | -200 | -3.8462 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_309A | NDOLA LIME | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | Gen Logic |  | 15 |  | 8959 | 9003 | 44 | 1103256 | OK | [7 empty] | 36 | 200 | 236 | -36 | -0.81818 | 2.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_010M | Kabushi | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | IMG |  | 15 |  | 7949 | 8041 | 92 | 1103256 | OK | [7 empty] | 5 | 400 | 405 | -5 | -0.054348 | 2.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_283A | MASALA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | IMG |  | 20 |  | 8091 | 8121 | 30 | 1103256 | OK | [7 empty] | 21 | 300 | 321 | -21 | -0.7 | 2.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_008M | Masala | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | Generator City |  | 13 |  | 6780 | 6843 | 63 | 1103256 | OK | [7 empty] | 63 | 400 | 463 | -63 | -1 | 2 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_035M | Kaloko | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | Himoinsa |  | 30 |  | 9768 | 9307 | -461 | 1103256 | OK | [7 empty] | 30 | 400 | 430 | -30 | 0.065076 | 4.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_004M | Ndola T. Centre | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | Falcon |  | 20 |  | 667 | 725 | 58 | 1103256 | OK | [7 empty] | 5 | 300 | 305 | -5 | -0.086207 | 2.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_002M | Hillcrest | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | GL Yanmar |  | 20 |  | 7949 | 8088 | 139 | 1103256 | OK | [7 empty] | 5 | 400 | 405 | -5 | -0.035971 | 2.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_360A | Hilcrest Extension | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | CK Works |  | 20 |  | 10985 | 10901 | -84 | 1103256 | OK | [7 empty] | 86 | 300 | 386 | -86 | 1.0238 | 5.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_338A | Musa Kasonka_3_Rlf | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | CK Works |  | 20 |  | 11345 | 11404 | 59 | 1103256 | OK | [7 empty] | 104 | 300 | 404 | -104 | -1.7627 | 2.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_349A | Kafubu Mall | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | Gen Logic |  | 16 |  | 16521 | 16605 | 84 | 1103256 | OK | [7 empty] | 58 | 300 | 358 | -58 | -0.69048 | 2 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_022M | Kasembo | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | Gen Logic |  | 20 |  | 7473 | 7542 | 69 | 1103256 | OK | [7 empty] | 5 | 50 | 55 | -5 | -0.072464 | 2.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_012M | Itawa West | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | Lamasat |  | 20 |  | 11821 | 11919 | 98 | 1103256 | OK | [7 empty] | 5 | 300 | 305 | -5 | -0.05102 | 2.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_253A | ITAWA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | Gen Logic |  | 20 |  | 11113 | 11130 | 17 | 1103256 | OK | [7 empty] | 37 | 400 | 437 | -37 | -2.1765 | 2.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_297A | KITWE POLICE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | Gen Logic |  | 16 |  | 8094 | 8114 | 20 | 1103256 | OK | [7 empty] | 10 | 300 | 310 | -10 | -0.5 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_356A | New Ndeke Village | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | CK Works |  | 20 |  | 1288 | 1325 | 37 | 1103256 | OK | [7 empty] | 20 | 250 | 270 | -20 | -0.54054 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_082M | Ndeke Extension | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | Gen Logic |  | 20 |  | 7721 | 7769 | 48 | 1103256 | OK | [7 empty] | 24 | 300 | 324 | -24 | -0.5 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_079M | Ndeke | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | CK Works |  | 20 |  | 10331 | 10400 | 69 | 1103256 | OK | [7 empty] | 106 | 350 | 456 | -106 | -1.5362 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_244A | NDEKE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | Earth technology |  | 15 |  | 4259 | 4337 | 78 | 1103256 | OK | [7 empty] | 27 | 300 | 327 | -27 | -0.34615 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_075M | Ndeke Changachanga | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | Gen Logic |  | 20 |  | 4035 | 4099 | 64 | 1103256 | OK | [7 empty] | 89 | 400 | 489 | -89 | -1.3906 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_355A | Ndeke Sub. A | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Gen Only |  |  | Green Field |  | 2025-11-08 |  |  |  | CK Works |  | 20 |  | 15146 | 15225 | 79 | 1103256 | OK | [7 empty] | 23 | 300 | 323 | -23 | -0.29114 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_305A | LUANGWA KAFUE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | Yanmar |  | 16 |  | 1326 | 1337 | 11 | 1103256 | OK | [7 empty] | 68 | 250 | 318 | -68 | -6.1818 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_251A | Kitwe Railways | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | MPI |  | 20 |  | 6207 | 6230 | 23 | 1103256 | OK | [7 empty] | 10 | 400 | 410 | -10 | -0.43478 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_025M | Pamozi Extension | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | GL Yanmar |  | 16 |  | 3788 | 3869 | 81 | 1103256 | OK | [7 empty] | 186 | 200 | 386 | -186 | -2.2963 | 2 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | GL Yanmar |  | 20 |  | 724 | 751 | 27 | 1103256 | OK | [7 empty] | 165 | 300 | 465 | -165 | -6.1111 | 2 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_218A | PAMODZI | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | Gen Logic |  | 20 |  | 14033 | 14107 | 74 | 1103256 | OK | [7 empty] | 228 | 300 | 528 | -228 | -3.0811 | 2.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_017M | Overspill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | Falcon |  | 20 |  | 9251 | 9258 | 7 | 1103256 | OK | [7 empty] | 29 | 50 | 79 | -29 | -4.1429 | 2.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_037M | Minsundu | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | GL Yanmar |  | 16 |  | FAULTY | FAULTY | #VALUE! | 1103256 | #VALUE! | [7 empty] | 28 | 300 | 328 | -28 | #VALUE! | 2 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_283A | MASALA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | IMG |  | 20 |  | 5266 | 5290 | 24 | 1103256 | OK | [7 empty] | 173 | 300 | 473 | -173 | -7.2083 | 2.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_252A | CHIFUBU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | Gen Logic |  | 30 |  | 4609 | 4618 | 9 | 1103256 | OK | [7 empty] | 170 | 300 | 470 | -170 | -18.8889 | 4.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_219M | PETAUKE CRESCENT | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | CK Works |  | 20 |  | 4315 | 4321 | 6 | 1103256 | OK | [7 empty] | 237 | 300 | 537 | -237 | -39.5 | 2.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_013M | Dola Hill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | Himoinsa |  | 30 |  | 6164 | 6170 | 6 | 1103256 | OK | [7 empty] | 182 | 400 | 582 | -182 | -30.3333 | 4.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_017M | Overspill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | Falcon |  | 20 |  | 9258 | 9275 | 17 | 1103256 | OK | [7 empty] | 28 | 150 | 178 | -28 | -1.6471 | 2.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_344A | Nkwazi 3G | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | CK Works |  | 20 |  | 46188 | 46258 | 70 | 1103256 | OK | [7 empty] | 93 | 200 | 293 | -93 | -1.3286 | 2.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_226M | CHIFUBU WEST | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | Generator City |  | 13 |  | 19509 | 19638 | 129 | 1103256 | OK | [7 empty] | 62 | 300 | 362 | -62 | -0.48062 | 2 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_041M | Kaniki | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | GL Yanmar |  | 16 |  | 11631 | 11729 | 98 | 1103256 | OK | [7 empty] | 298 | 300 | 598 | -298 | -3.0408 | 2 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_216M | COOL BANANAS | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | Generator City |  | 13 |  | 8166 | 8246 | 80 | 1103256 | OK | [7 empty] | 246 | 300 | 546 | -246 | -3.075 | 2 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_072M | Twasekela Basic | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-08 |  |  |  | Ghadder |  | 20 |  | 9414 | 9532 | 118 | 1103256 | OK | [7 empty] | 80 | 300 | 380 | -80 | -0.67797 | 2.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_062M | Roan Township | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | CK Works |  | 20 |  | 8490 | 8558 | 68 | 1103280 | OK | [7 empty] | 70 | 200 | 270 | -70 | -1.0294 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_339A | Katuni Eden Institute | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | Gen Logic |  | 10 |  | 16032 | 16075 | 43 | 1103280 | OK | [7 empty] | 157 | 300 | 457 | -157 | -3.6512 | 1.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_254A | MPONGWE BOMA | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | CK Works |  | 20 |  | 7927 | 7942 | 15 | 1103280 | OK | [7 empty] | 95 | 300 | 395 | -95 | -6.3333 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_168M | Mpongwe | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | GL Yanmar |  | 16 |  | 11340 | 11410 | 70 | 1103280 | OK | [7 empty] | 45 | 50 | 95 | -45 | -0.64286 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_193M | Chambatata | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | Yanmar |  | 16 |  | 12851 | 12876 | 25 | 1103280 | OK | [7 empty] | 10 | 200 | 210 | -10 | -0.4 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_094M | Kitwe Primary | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | Gen Logic |  | 16 |  | 2966 | 2978 | 12 | 1103280 | OK | [7 empty] | 31 | 400 | 431 | -31 | -2.5833 | 2 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_342A | Kantanta Street | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | Gen Logic |  | 20 |  | 4199 | 4258 | 59 | 1103280 | OK | [7 empty] | 82 | 300 | 382 | -82 | -1.3898 | 2.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_088M | Geddis | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | CDP |  | 13 |  | 12490 | 12509 | 19 | 1103280 | OK | [7 empty] | 5 | 300 | 305 | -5 | -0.26316 | 1.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_243A | GEDDIS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | Gen Logic |  | 15 |  | 18215 | 18250 | 35 | 1103280 | OK | [7 empty] | 92 | 300 | 392 | -92 | -2.6286 | 1.8 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_086M | Minsenshi-natwange | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | Gen Logic |  | 16 |  |  | FAULTY | #VALUE! | 1103280 | #VALUE! | [7 empty] | 22 | 200 | 222 | -22 | #VALUE! | 2 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_345A | Ndeke Changachanga south 3G | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | Gen Logic |  | 20 |  | 13928 | 13935 | 7 | 1103280 | OK | [7 empty] | 33 | 50 | 83 | -33 | -4.7143 | 2.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_074M | Luangwa | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | Gen Logic |  | 16 |  | 4927 | 4927 | 0 | 1103280 | OK | [7 empty] | 130 | 250 | 380 | -130 | #DIV/0! | 2 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_078M | Bupe | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | Gen Logic |  | 16 |  | 23231 | FAULTY | #VALUE! | 1103280 | #VALUE! | [7 empty] | 204 | 200 | 404 | -204 | #VALUE! | 2 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_289A | BUPE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | Gen Logic |  | 15 |  | 13363 | 13935 | 572 | 1103280 | OK | [7 empty] | 99 | 300 | 399 | -99 | -0.17308 | 1.8 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_225M | MUSHIPI | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | Generator City |  | 16 |  | 9294 | 9312 | 18 | 1103280 | OK | [7 empty] | 12 | 200 | 212 | -12 | -0.66667 | 2 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_250A | SOB | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | Gen Logic |  | 15 |  | FAULTY | FAULTY | #VALUE! | 1103280 | #VALUE! | [7 empty] | 28 | 200 | 228 | -28 | #VALUE! | 1.8 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_081M | Chamboli | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | Gen Logic |  | 16 |  | 13617 | 13617 | 0 | 1103280 | OK | [7 empty] | 87 | 200 | 287 | -87 | #DIV/0! | 2 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_222A | CHAMBOLI | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | Gen Logic |  | 30 |  | 512 | 534 | 22 | 1103280 | OK | [7 empty] | 330 | 250 | 580 | -330 | -15 | 4.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_102M | Richmond | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | Gen Logic |  | 16 |  | 3228 | 3288 | 60 | 1103280 | OK | [7 empty] | 5 | 300 | 305 | -5 | -0.083333 | 2 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_242A | PARKLANDS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | Gen Logic |  | 20 |  | 10092 | 10180 | 88 | 1103280 | OK | [7 empty] | 10 | 300 | 310 | -10 | -0.11364 | 2.5 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_092M | Nkana Stadium | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | Gen Logic |  | 16 |  | 5860 | 5885 | 25 | 1103280 | OK | [7 empty] | 170 | 350 | 520 | -170 | -6.8 | 2 | [5 empty] | 0 | [8 empty] | PUMA |  | CAPTURED
IHS_CBT_301A | CHIBULUMA TOWN | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | Gen Logic |  | 16 |  | 10152 | 10179 | 27 | 1103280 | OK | [7 empty] | 13 | 300 | 313 | -13 | -0.48148 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_117M | Chibote | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | Gen Logic |  | 15 |  | 6316 | 6349 | 33 | 1103280 | OK | [7 empty] | 5 | 200 | 205 | -5 | -0.15152 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_238M | NAPSA Complex | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | MPMC |  | 15 |  | 9098 | 9140 | 42 | 1103280 | OK | [7 empty] | 51 | 300 | 351 | -51 | -1.2143 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_133M | Chibuluma Golf Club | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | Powerol |  | 13 |  | 5756 | 5777 | 21 | 1103280 | OK | [7 empty] | 183 | 200 | 383 | -183 | -8.7143 | 1.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_206A | KALULUSHI | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | IMG |  | 15 |  | 7845 | 7876 | 31 | 1103280 | OK | [7 empty] | 69 | 400 | 469 | -69 | -2.2258 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_127M | Kalulushi | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | Himoinsa |  | 30 |  | 11256 | 11287 | 31 | 1103280 | OK | [7 empty] | 95 | 400 | 495 | -95 | -3.0645 | 4.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_267A | KALULUSHI EAST | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | Gen Logic |  | 16 |  | 14210 | 14228 | 18 | 1103280 | OK | [7 empty] | 126 | 300 | 426 | -126 | -7 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_132M | Kalulushi West | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | Gen Logic |  | 20 |  | 6146 | 6162 | 16 | 1103280 | OK | [7 empty] | 241 | 200 | 441 | -241 | -15.0625 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_126M | Chibuluma | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | Gen Logic |  | 20 |  | 4147 | 4155 | 8 | 1103280 | OK | [7 empty] | 199 | 300 | 499 | -199 | -24.875 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_134M | Kalulushi East | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | CK Works |  | 20 |  | 8808 | 8882 | 74 | 1103280 | OK | [7 empty] | 74 | 200 | 274 | -74 | -1 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_239A | LUFWANYAMA ROAD | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | Diesel Electric |  | 16 |  | FAULTY | FAULTY | #VALUE! | 1103280 | #VALUE! | [7 empty] | 48 | 300 | 348 | -48 | #VALUE! | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_310A | CHEMBE CHATI | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | Gen Logic |  | 17 |  | FAULTY | FAULTY | #VALUE! | 1103280 | #VALUE! | [7 empty] | 105 | 200 | 305 | -105 | #VALUE! | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_119M | Lumumba | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | Gen Logic |  | 16 |  |  |  | 0 | 1103280 | OK | [7 empty] | 102 | 200 | 302 | -102 | #DIV/0! | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_118M | Kamaronde | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | CK Works |  | 20 |  | 3554 | 3604 | 50 | 1103280 | OK | [7 empty] | 158 | 250 | 408 | -158 | -3.16 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_330A | Funda Junction (Mumena_5) | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | METCO |  | 15 |  | FAULTY | FAULTY | #VALUE! | 1103280 | #VALUE! | [7 empty] | 5 | 300 | 305 | -5 | #VALUE! | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_329A | St. Marys Mission (MUTENDA ST. MARYS_1) | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | METCO |  | 15 |  | FAULTY | FAULTY | #VALUE! | 1103280 | #VALUE! | [7 empty] | 20 | 200 | 220 | -20 | #VALUE! | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_213M | St. Marys Mission | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | Pramac |  | 10 |  | FAULTY | FAULTY | #VALUE! | 1103280 | #VALUE! | [7 empty] | 30 | 300 | 330 | -30 | #VALUE! | 1.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_167M | Kafubu | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-09 |  |  |  | LISTER PETTER |  | 16 |  | FAULTY | FAULTY | #VALUE! | 1103280 | #VALUE! | [7 empty] | 10 | 200 | 210 | -10 | #VALUE! | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_264A | NDOLA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-10 |  |  |  | Gen Logic |  | 16 |  | 6443 | 6463 | 20 | 1103304 | OK | [7 empty] | 123 | 300 | 423 | -123 | -6.15 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_359A | Cross Crescent | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-10 |  |  |  | CK Works |  | 20 |  | 5945 | 6021 | 76 | 1103304 | OK | [7 empty] | 185 | 300 | 485 | -185 | -2.4342 | 4.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_025M | Pamozi Extension | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-10 |  |  |  | GL Yanmar |  | 16 |  | FAULTY | FAULTY | #VALUE! | 1103304 | #VALUE! | [7 empty] | 0 | 100 | 100 | 0 | #VALUE! | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-10 |  |  |  | GL Yanmar |  | 20 |  | 751 | 764 | 13 | 1103304 | OK | [7 empty] | 0 | 100 | 100 | 0 | 0 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_245A | NORTHRISE | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-10 |  |  |  | Lamasat |  | 20 |  | 9089 | 9098 | 9 | 1103304 | OK | [7 empty] | 240 | 300 | 540 | -240 | -26.6667 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_017M | Overspill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-10 |  |  |  | Falcon |  | 20 |  | 9272 | 9299 | 27 | 1103304 | OK | [7 empty] | 97 | 100 | 197 | -97 | -3.5926 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_025M | Pamozi Extension | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-10 |  |  |  | GL Yanmar |  | 16 |  | FAULTY | FAULTY | #VALUE! | 1103304 | #VALUE! | [7 empty] | 40 | 150 | 190 | -40 | #VALUE! | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-10 |  |  |  | GL Yanmar |  | 20 |  | 764 | 777 | 13 | 1103304 | OK | [7 empty] | 35 | 150 | 185 | -35 | -2.6923 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_015M | Yengwe | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-10 |  |  |  | CK Works |  | 20 |  | 5907 | 5913 | 6 | 1103304 | OK | [7 empty] | 252 | 100 | 352 | -252 | -42 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_291A | MWATAYANVWA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-10 |  |  |  | Gen Logic |  | 20 |  | 4666 | 4707 | 41 | 1103304 | OK | [7 empty] | 32 | 300 | 332 | -32 | -0.78049 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_222M | TWAPIA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-10 |  |  |  | Generator City |  | 13 |  | 11950 | 12030 | 80 | 1103304 | OK | [7 empty] | 160 | 300 | 460 | -160 | -2 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT-371A | JVC | #N/A | SAMUEL | #N/A | #N/A | #N/A |  | #N/A | #N/A |  |  | #N/A |  | 2025-11-11 |  |  |  | #N/A |  | #N/A |  | 0 | 0 | 0 | 1103328 | OK | [7 empty] | 0 | 200 | 200 | 0 | #DIV/0! | #N/A | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_380A | KALULUSHI | #N/A | SAMUEL | #N/A | #N/A | #N/A |  | #N/A | #N/A |  |  | #N/A |  | 2025-11-11 |  |  |  | #N/A |  | #N/A |  | 0 | 0 | 0 | 1103328 | OK | [7 empty] | 0 | 200 | 200 | 0 | #DIV/0! | #N/A | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_375A | KALULUSHI | #N/A | SAMUEL | #N/A | #N/A | #N/A |  | #N/A | #N/A |  |  | #N/A |  | 2025-11-11 |  |  |  | #N/A |  | #N/A |  | 0 | 0 | 0 | 1103328 | OK | [7 empty] | 0 | 200 | 200 | 0 | #DIV/0! | #N/A | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_345A | Ndeke Changachanga south 3G | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-11 |  |  |  | Gen Logic |  | 20 |  | 13935 | 13962 | 27 | 1103328 | OK | [7 empty] | 10 | 300 | 310 | -10 | -0.37037 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_356A | New Ndeke Village | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-11 |  |  |  | CK Works |  | 20 |  | 1325 | 1386 | 61 | 1103328 | OK | [7 empty] | 20 | 150 | 170 | -20 | -0.32787 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_073M | Cedrics Farm | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-11 |  |  |  | perkins |  | 15 |  | 17703 | 17771 | 68 | 1103328 | OK | [7 empty] | 20 | 50 | 70 | -20 | -0.29412 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_073M | Cedrics Farm | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-11 |  |  |  | perkins |  | 15 |  | 17771 | 17796 | 25 | 1103328 | OK | [7 empty] | 10 | 350 | 360 | -10 | -0.4 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_353A | Court Barrifs | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-11 |  |  |  | CK Works |  | 20 |  | 10916 | 10972 | 56 | 1103328 | OK | [7 empty] | 37 | 300 | 337 | -37 | -0.66071 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_088M | Geddis | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-11 |  |  |  | CDP |  | 13 |  | 12509 | 12586 | 77 | 1103328 | OK | [7 empty] | 61 | 100 | 161 | -61 | -0.79221 | 1.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_368A | #N/A | #N/A | FACKSON | #N/A | #N/A | #N/A |  | #N/A | #N/A |  |  | #N/A |  | 2025-11-11 |  |  |  | #N/A |  | #N/A |  | 10323 | 10328 | 5 | 1103328 | OK | [7 empty] | 46 | 250 | 296 | -46 | -9.2 | #N/A | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_368A | #N/A | #N/A | FACKSON | #N/A | #N/A | #N/A |  | #N/A | #N/A |  |  | #N/A |  | 2025-11-11 |  |  |  | #N/A |  | #N/A |  | 10214 | 10323 | 109 | 1103328 | OK | [7 empty] | 10 | 50 | 60 | -10 | -0.091743 | #N/A | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_083M | Nkana East | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-11 |  |  |  | Gen Logic |  | 16 |  | 4295 | 4334 | 39 | 1103328 | OK | [7 empty] | 171 | 300 | 471 | -171 | -4.3846 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_237A | NKANA WEST | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-11 |  |  |  | Earth technology |  | 20 |  | 12364 | 12465 | 101 | 1103328 | OK | [7 empty] | 5 | 300 | 305 | -5 | -0.049505 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_105M | Buntungwa | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-11 |  |  |  | Gen Logic |  | 16 |  | 6142 | 6200 | 58 | 1103328 | OK | [7 empty] | 5 | 50 | 55 | -5 | -0.086207 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_086M | Minsenshi-natwange | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-11 |  |  |  | Gen Logic |  | 16 |  | FAULTY | FAULTY | #VALUE! | 1103328 | #VALUE! | [7 empty] | 10 | 50 | 60 | -10 | #VALUE! | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_307A | TVTC | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-11 |  |  |  | Gen Logic |  | 16 |  | FAULTY |  | #VALUE! | 1103328 | #VALUE! | [7 empty] | 10 | 150 | 160 | -10 | #VALUE! | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_047M | Kamirenda | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-11 |  |  |  | Gen Logic |  | 16 |  | 13466 | 13528 | 62 | 1103328 | OK | [7 empty] | 28 | 200 | 228 | -28 | -0.45161 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_049M | Mikomfwa East | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-11 |  |  |  | Gen Logic |  | 16 |  | 6853 | 6907 | 54 | 1103328 | OK | [7 empty] | 20 | 200 | 220 | -20 | -0.37037 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_054M | Mikomfwa Market | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-11 |  |  |  | Yanmar |  | 16 |  | 12728 | 12775 | 47 | 1103328 | OK | [7 empty] | 67 | 200 | 267 | -67 | -1.4255 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_058M | Mikomfwa | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-11 |  |  |  | Gen Logic |  | 16 |  | 8200 | 8262 | 62 | 1103328 | OK | [7 empty] | 20 | 150 | 170 | -20 | -0.32258 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_230A | MIKOMFWA | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-11 |  |  |  | Earth technology |  | 15 |  | 1250 | 1300 | 50 | 1103328 | OK | [7 empty] | 44 | 200 | 244 | -44 | -0.88 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_207A | KANINI | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-11 |  |  |  | Gen Logic |  | 16 |  | 9372 | 9458 | 86 | 1103328 | OK | [7 empty] | 24 | 300 | 324 | -24 | -0.27907 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_246A | NDOLA TOWN | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-11 |  |  |  | CK Power |  | 30 |  | 244 | 296 | 52 | 1103328 | OK | [7 empty] | 142 | 450 | 592 | -142 | -2.7308 | 4.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_251A | Kitwe Railways | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-11 |  |  |  | MPI |  | 20 |  | 13081 | 13106 | 25 | 1103328 | OK | [7 empty] | 126 | 300 | 426 | -126 | -5.04 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_018M | Nkwanzi | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-11 |  |  |  | CK Works |  | 20 |  | 1851 | 1878 | 27 | 1103328 | OK | [7 empty] | 250 | 300 | 550 | -250 | -9.2593 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-11 |  |  |  | GL Yanmar |  | 20 |  | 777 | 808 | 31 | 1103328 | OK | [7 empty] | 5 | 50 | 55 | -5 | -0.16129 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_025M | Pamozi Extension | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-11 |  |  |  | GL Yanmar |  | 16 |  | FAULTY | FAULTY | #VALUE! | 1103328 | #VALUE! | [7 empty] | 45 | 50 | 95 | -45 | #VALUE! | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_361A | Mitengo TDRC | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-11 |  |  |  | CK Works |  | 20 |  | 6041 | 6123 | 82 | 1103328 | OK | [7 empty] | 6 | 100 | 106 | -6 | -0.073171 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_042 | GOLDEN LAY | #N/A | royd | #N/A | #N/A | #N/A |  | #N/A | #N/A |  |  | #N/A |  | 2025-11-12 |  |  |  | #N/A |  | #N/A |  | 538 | 8386 | 7848 | 1103352 | OK | [7 empty] | 5 | 100 | 105 | -5 | -0.0006371 | #N/A | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_321A | Fred Station (MAPOSA_2) | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Gen Logic |  | 20 |  | 14266 | 14269 | 3 | 1103352 | OK | [7 empty] | 99 | 100 | 199 | -99 | -33 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_043M | Fisenge | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Gen Logic |  | 16 |  |  | FAULTY | #VALUE! | 1103352 | #VALUE! | [7 empty] | 109 | 200 | 309 | -109 | #VALUE! | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_312A | FISENGE | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Yanmar |  | 16 |  | 7524 | 7589 | 65 | 1103352 | OK | [7 empty] | 220 | 150 | 370 | -220 | -3.3846 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_048M | Kamirenda Extension | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Vitalgen |  | 20 |  | 9984 | 10000 | 16 | 1103352 | OK | [7 empty] | 94 | 150 | 244 | -94 | -5.875 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_265A | NEW TOWN | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Gen Logic |  | 16 |  | 1952 | 2031 | 79 | 1103352 | OK | [7 empty] | 58 | 200 | 258 | -58 | -0.73418 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_052M | Luanshya New Town | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Gen Logic |  | 16 |  | 15288 | 15372 | 84 | 1103352 | OK | [7 empty] | 95 | 200 | 295 | -95 | -1.131 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_343A | Chinese Colony | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Gen Logic |  | 20 |  |  | FAULTY | #VALUE! | 1103352 | #VALUE! | [7 empty] | 90 | 200 | 290 | -90 | #VALUE! | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_277A | ROAN | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Gen Logic |  | 16 |  |  | FAULTY | #VALUE! | 1103352 | #VALUE! | [7 empty] | 109 | 150 | 259 | -109 | #VALUE! | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_065M | Mpatamato East | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Yanmar |  | 16 |  | 8726 | 8759 | 33 | 1103352 | OK | [7 empty] | 56 | 150 | 206 | -56 | -1.697 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_210A | LUANSHYA | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | CK Works |  | 20 |  | 4539 | 4655 | 116 | 1103352 | OK | [7 empty] | 20 | 200 | 220 | -20 | -0.17241 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_278A | MUKUMPU I & II | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | perkins |  | 15 |  | 6349 | 6397 | 48 | 1103352 | OK | [7 empty] | 30 | 200 | 230 | -30 | -0.625 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_238M | NAPSA Complex | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | MPMC |  | 15 |  | 9140 | 9214 | 74 | 1103352 | OK | [7 empty] | 84 | 150 | 234 | -84 | -1.1351 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_133M | Chibuluma Golf Club | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Powerol |  | 13 |  | 5777 | 5837 | 60 | 1103352 | OK | [7 empty] | 167 | 200 | 367 | -167 | -2.7833 | 1.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_134M | Kalulushi East | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | CK Works |  | 20 |  | 8852 | 8901 | 49 | 1103352 | OK | [7 empty] | 63 | 300 | 363 | -63 | -1.2857 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_119M | Lumumba | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Gen Logic |  | 16 |  | 10138 | 10138 | 0 | 1103352 | OK | [7 empty] | 66 | 200 | 266 | -66 | #DIV/0! | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_301A | CHIBULUMA TOWN | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Gen Logic |  | 16 |  | 10179 | 10254 | 75 | 1103352 | OK | [7 empty] | 28 | 150 | 178 | -28 | -0.37333 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_117M | Chibote | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Gen Logic |  | 15 |  | 6349 | 6397 | 48 | 1103352 | OK | [7 empty] | 22 | 200 | 222 | -22 | -0.45833 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_276A | KAKOLO I & II | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Solar-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Jiuan |  | 15 |  | 24299 | 24425 | 126 | 1103352 | OK | [7 empty] | 82 | 300 | 382 | -82 | -0.65079 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_354A | Mufuchani | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Gen Only |  |  | Green Field |  | 2025-11-12 |  |  |  | CK Works |  | 20 |  | 13436 | 15478 | 2042 | 1103352 | OK | [7 empty] | 8 | 300 | 308 | -8 | -0.0039177 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_098M | BULANGILILO | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Gen Logic |  | 16 |  | 8465 | 8555 | 90 | 1103352 | OK | [7 empty] | 5 | 300 | 305 | -5 | -0.055556 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_116M | Twatacha | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Gen Logic |  | 16 |  | 517 | 619 | 102 | 1103352 | OK | [7 empty] | 161 | 300 | 461 | -161 | -1.5784 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_229A | CHIMWEMWE | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Gen Logic |  | 20 |  | 813 | 859 | 46 | 1103352 | OK | [7 empty] | 121 | 300 | 421 | -121 | -2.6304 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_296A | KAMUNGA | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Gen Logic |  | 16 |  | 6713 | 6770 | 57 | 1103352 | OK | [7 empty] | 200 | 200 | 400 | -200 | -3.5088 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_108M | Chachacha | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | perkins |  | 20 |  | 1883 | 1960 | 77 | 1103352 | OK | [7 empty] | 48 | 250 | 298 | -48 | -0.62338 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_228A | MINDOLO | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Earth technology |  | 20 |  | 11705 | 11815 | 110 | 1103352 | OK | [7 empty] | 20 | 300 | 320 | -20 | -0.18182 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_105M | Buntungwa | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Gen Logic |  | 16 |  | 6200 | 6204 | 4 | 1103352 | OK | [7 empty] | 39 | 250 | 289 | -39 | -9.75 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_300A | LUBAMBE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Jiuan |  | 30 |  | 5488 | 5513 | 25 | 1103352 | OK | [7 empty] | 316 | 300 | 616 | -316 | -12.64 | 4.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_305A | LUANGWA KAFUE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Yanmar |  | 16 |  | 1337 | 1394 | 57 | 1103352 | OK | [7 empty] | 103 | 200 | 303 | -103 | -1.807 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_014M | Luangwa | GNM | FACKSON | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | CK Works |  | 20 |  | 4927 | 4985 | 58 | 1103352 | OK | [7 empty] | 159 | 200 | 359 | -159 | -2.7414 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_075M | Ndeke Changachanga | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Gen Logic |  | 20 |  | 4099 | 4154 | 55 | 1103352 | OK | [7 empty] | 205 | 250 | 455 | -205 | -3.7273 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_244A | NDEKE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Earth technology |  | 15 |  | 4337 | 4392 | 55 | 1103352 | OK | [7 empty] | 113 | 300 | 413 | -113 | -2.0545 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_079M | Ndeke | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | CK Works |  | 20 |  | 10400 | 10457 | 57 | 1103352 | OK | [7 empty] | 167 | 250 | 417 | -167 | -2.9298 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_082M | Ndeke Extension | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Gen Logic |  | 20 |  | 7769 | 7819 | 50 | 1103352 | OK | [7 empty] | 61 | 300 | 361 | -61 | -1.22 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_356A | New Ndeke Village | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | CK Works |  | 20 |  | 1386 | 1400 | 14 | 1103352 | OK | [7 empty] | 84 | 350 | 434 | -84 | -6 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_086M | Minsenshi-natwange | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Gen Logic |  | 16 |  | FAULTY | FAULTY | #VALUE! | 1103352 | #VALUE! | [7 empty] | 10 | 300 | 310 | -10 | #VALUE! | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_104M | Twibukishe | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Gen Logic |  | 16 |  | 24350 | 24438 | 88 | 1103352 | OK | [7 empty] | 10 | 100 | 110 | -10 | -0.11364 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_297A | KITWE POLICE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Gen Logic |  | 16 |  | 8114 | 8207 | 93 | 1103352 | OK | [7 empty] | 20 | 300 | 320 | -20 | -0.21505 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_251A | Kitwe Railways | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | MPI |  | 20 |  | 6230 | 6317 | 87 | 1103352 | OK | [7 empty] | 79 | 300 | 379 | -79 | -0.90805 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_088M | Geddis | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | CDP |  | 13 |  | 12586 | 12609 | 23 | 1103352 | OK | [7 empty] | 92 | 200 | 292 | -92 | -4 | 1.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_084M | Kitwe ZNS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | CDP |  | 15 |  | 18597 | 18710 | 113 | 1103352 | OK | [7 empty] | 5 | 200 | 205 | -5 | -0.044248 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_027M | Kantanta Street | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | CK Works |  | 20 |  | 5950 | 6005 | 55 | 1103352 | OK | [7 empty] | 97 | 300 | 397 | -97 | -1.7636 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_024M | Ndeke Township | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | CK Works |  | 30 |  | 1366 | 1434 | 68 | 1103352 | OK | [7 empty] | 5 | 400 | 405 | -5 | -0.073529 | 4.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_033M | Bwana Mukubwa | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | GL Yanmar |  | 16 |  | 5950 | 6005 | 55 | 1103352 | OK | [7 empty] | 48 | 300 | #REF! | #REF! | #REF! | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_016M | Itawa | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Vitalgen |  | 30 |  | 1366 | 1434 | 68 | 1103352 | OK | [7 empty] | 87 | 400 | #REF! | #REF! | #REF! | 4.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_362A | Ndola Central Police | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | CK Works |  | 20 |  | 1331 | 1365 | 34 | 1103352 | OK | [7 empty] | 5 | 300 | 348 | -48 | -1.4118 | 4.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_232A | LUBUTO | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Gen Logic |  | 20 |  | 4987 | 5049 | 62 | 1103352 | OK | [7 empty] | 25 | 400 | 487 | -87 | -1.4032 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_306A | TUG-ARGAN | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Yanmar |  | 16 |  |  | 12597 | 12597 | 1103352 | OK | [7 empty] | 200 | 200 | 305 | -5 | -0.00039692 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_156M | Mpongwe Turnoff | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Himoinsa |  | 30 |  | 11353 | 11428 | 75 | 1103352 | OK | [7 empty] | 28 | 200 | 425 | -25 | -0.33333 | 4.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_032M | Cleveland | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | CK Works |  | 20 |  | 6946 | 6400 | -546 | 1103352 | OK | [7 empty] | 84 | 100 | 400 | -200 | 0.3663 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | GL Yanmar |  | 20 |  | 808 | 819 | 11 | 1103352 | OK | [7 empty] | 1 | 100 | 228 | -28 | -2.5455 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_331A | Mushili Baracks | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | GL Isuzu |  | 10 |  | 10704 | 10778 | 74 | 1103352 | OK | [7 empty] | 31 | 150 | 184 | -84 | -1.1351 | 1.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_034M | Mushili Baracks | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | GL Yanmar |  | 15 |  | 28028 | 28107 | 79 | 1103352 | OK | [7 empty] | 97 | 300 | 101 | -1 | -0.012658 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_234A | CHIWALA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Gen Logic |  | 20 |  | 22050 | 22080 | 30 | 1103352 | OK | [7 empty] | 155 | 200 | 181 | -31 | -1.0333 | 4.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_291A | MWATAYANVWA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | Gen Logic |  | 20 |  | 4707 | 4771 | 64 | 1103352 | OK | [7 empty] | 44 | 25 | 397 | -97 | -1.5156 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_361A | Mitengo TDRC | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-12 |  |  |  | CK Works |  | 20 |  | 6123 | 6148 | 25 | 1103352 | OK | [7 empty] | 0 | 40 | 355 | -155 | -6.2 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_022M | Kasembo | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Gen Logic |  | 20 |  | 6599 | 6671 | 72 | 1103376 | OK | [7 empty] | 19 | 300 | 319 | -19 | -0.26389 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_148M | Kaloko Trust | GNM | Kasoma | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Yanmar |  | 16 |  | 7291 | 7397 | 106 | 1103376 | OK | [7 empty] | 10 | 100 | 110 | -10 | -0.09434 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_036M | Lubendo | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | GL Yanmar |  | 16 |  |  | 986 | 986 | 1103376 | OK | [7 empty] | 20 | 100 | 120 | -20 | -0.020284 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_236A | KALALANGABO | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | ASCOT |  | 30 |  | 351 | 382 | 31 | 1103376 | OK | [7 empty] | 209 | 150 | 359 | -209 | -6.7419 | 4.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_091M | Kalalangabo | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | GL Yanmar |  | 16 |  | 6127 | 6160 | 33 | 1103376 | OK | [7 empty] | 259 | 100 | 359 | -259 | -7.8485 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_060M | Kansafu | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Falcon |  | 16 |  | 1668 | 1745 | 77 | 1103376 | OK | [7 empty] | 128 | 250 | 378 | -128 | -1.6623 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_288A | NDOLA BUS STATION | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | CK Works |  | 20 |  | 629 | 691 | 62 | 1103376 | OK | [7 empty] | 65 | 300 | 365 | -65 | -1.0484 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_349A | Kafubu Mall | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Gen Logic |  | 16 |  | 16605 | 16715 | 110 | 1103376 | OK | [7 empty] | 55 | 300 | 355 | -55 | -0.5 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_003M | Swimming Pool | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | CK Works |  | 30 |  | 7542 | 7602 | 60 | 1103376 | OK | [7 empty] | 122 | 400 | 522 | -122 | -2.0333 | 4.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_045M | Tuckugan | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | GL Yanmar |  | 16 |  | FAULTY | FAULTY | #VALUE! | 1103376 | #VALUE! | [7 empty] | 10 | 100 | 110 | -10 | #VALUE! | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_014M | Lubuto | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | CK Works |  | 20 |  | 4220 | 4295 | 75 | 1103376 | OK | [7 empty] | 55 | 300 | 355 | -55 | -0.73333 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_009M | Tazama Building | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Roof Top |  | 2025-11-13 |  |  |  | IMG |  | 16 |  | 29223 | 29323 | 100 | 1103376 | OK | [7 empty] | 121 | 100 | 221 | -121 | -1.21 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_220M | RAILWAY STATION | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | CK Works |  | 20 |  | 7358 | 7440 | 82 | 1103376 | OK | [7 empty] | 18 | 250 | 268 | -18 | -0.21951 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_360A | Hilcrest Extension | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | CK Works |  | 20 |  | 10985 | 11032 | 47 | 1103376 | OK | [7 empty] | 184 | 200 | 384 | -184 | -3.9149 | 5.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_006M | Lubuto Central | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Lamasat |  | 15 |  | 1451 | 1503 | 52 | 1103376 | OK | [7 empty] | 65 | 300 | 365 | -65 | -1.25 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_020M | Mushili | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | CK Works |  | 30 |  | 8735 | 8811 | 76 | 1103376 | OK | [7 empty] | 5 | 300 | 305 | -5 | -0.065789 | 4.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_021M | Sky ways | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | CK Works |  | 20 |  | 7794 | 7873 | 79 | 1103376 | OK | [7 empty] | 56 | 300 | 356 | -56 | -0.70886 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_217A | MAPOSA | GNM | FACKSON | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Gen Logic |  | 30 |  | 293 | 304 | 11 | 1103376 | OK | [7 empty] | 58 | 100 | 158 | -58 | -5.2727 | 4.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_289A | Bupe | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Gen Logic |  | 15 |  | 13372 | 13400 | 28 | 1103376 | OK | [7 empty] | 287 | 300 | 587 | -287 | -10.25 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_225M | MUSHIPI | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Generator City |  | 16 |  | 9302 | FAULTY | #VALUE! | 1103376 | #VALUE! | [7 empty] | 74 | 250 | 324 | -74 | #VALUE! | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_081M | Chamboli | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Gen Logic |  | 16 |  | 13617 | 13669 | 52 | 1103376 | OK | [7 empty] | 141 | 250 | 391 | -141 | -2.7115 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_237A | NKANA WEST | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Earth technology |  | 20 |  | 12465 | 12513 | 48 | 1103376 | OK | [7 empty] | 126 | 200 | 326 | -126 | -2.625 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_104M | Twibukishe | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Gen Logic |  | 16 |  | 24438 | 24463 | 25 | 1103376 | OK | [7 empty] | 33 | 300 | 333 | -33 | -1.32 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_242A | PARKLANDS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Gen Logic |  | 20 |  | 10180 | 10255 | 75 | 1103376 | OK | [7 empty] | 33 | 300 | 333 | -33 | -0.44 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_102M | Richmond | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Gen Logic |  | 16 |  | 3288 | 3341 | 53 | 1103376 | OK | [7 empty] | 86 | 250 | 336 | -86 | -1.6226 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_094M | Kitwe Primary | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Gen Logic |  | 16 |  | 2978 | 3010 | 32 | 1103376 | OK | [7 empty] | 290 | 200 | 490 | -290 | -9.0625 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_342A | Kantanta Street | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Gen Logic |  | 20 |  | 4258 | 4309 | 51 | 1103376 | OK | [7 empty] | 181 | 300 | 481 | -181 | -3.549 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_243A | GEDDIS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Gen Logic |  | 15 |  | 18250 | 18312 | 62 | 1103376 | OK | [7 empty] | 169 | 200 | 369 | -169 | -2.7258 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_017M | Overspill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Falcon |  | 20 |  | 9299 | 9370 | 71 | 1103376 | OK | [7 empty] | 16 | 300 | 316 | -16 | -0.22535 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | GL Yanmar |  | 20 |  | 819 | 835 | 16 | 1103376 | OK | [7 empty] | 21 | 200 | 221 | -21 | -1.3125 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_025M | Pamozi Extension | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | GL Yanmar |  | 16 |  | FAULTY | FAULTY | #VALUE! | 1103376 | #VALUE! | [7 empty] | 41 | 200 | 241 | -41 | #VALUE! | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_291A | MWATAYANVWA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Gen Logic |  | 20 |  | 4771 | 4776 | 5 | 1103376 | OK | [7 empty] | 45 | 300 | 345 | -45 | -9 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_252A | CHIFUBU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Gen Logic |  | 30 |  | 4618 | 4693 | 75 | 1103376 | OK | [7 empty] | 95 | 300 | 395 | -95 | -1.2667 | 4.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_344A | Nkwazi 3G | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | CK Works |  | 20 |  | 46258 | 46330 | 72 | 1103376 | OK | [7 empty] | 5 | 300 | 305 | -5 | -0.069444 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_364A | Chifubu Sec. School | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | CK Works |  | 20 |  | 1027 | 1097 | 70 | 1103376 | OK | [7 empty] | 10 | 100 | 110 | -10 | -0.14286 | 4.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_233A | CHIPULUKUSU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Earth Technology |  | 15 |  | 5370 | 5396 | 26 | 1103376 | OK | [7 empty] | 59 | 250 | 309 | -59 | -2.2692 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_264A | NDOLA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Gen Logic |  | 16 |  | 6463 | 6533 | 70 | 1103376 | OK | [7 empty] | 87 | 150 | 237 | -87 | -1.2429 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_347A | Ndola International Airport | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Vitalgen |  | 20 |  | 9120 | 9184 | 64 | 1103376 | OK | [7 empty] | 98 | 200 | 298 | -98 | -1.5312 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_266A | KAWAMA Copperbelt | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Gen Logic |  | 16 |  | 1984 | 2160 | 176 | 1103376 | OK | [7 empty] | 35 | 200 | 235 | -35 | -0.19886 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_266A | KAWAMA Copperbelt | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Gen Logic |  | 16 |  | 2160 | 2161 | 1 | 1103376 | OK | [7 empty] | 232 | 100 | 332 | -232 | -232 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_347A | Ndola International Airport | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Vitalgen |  | 20 |  | 9184 | 9184 | 0 | 1103376 | OK | [7 empty] | 298 | 100 | 398 | -298 | #DIV/0! | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_361A | Mitengo TDRC | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | CK Works |  | 20 |  | 6148 | 6151 | 3 | 1103376 | OK | [7 empty] | 26 | 200 | 226 | -26 | -8.6667 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_361A | Mitengo TDRC | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | CK Works |  | 20 |  | 6151 | 6172 | 21 | 1103376 | OK | [7 empty] | 135 | 100 | 235 | -135 | -6.4286 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_112M | Kamtipa | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Gen Logic |  | 16 |  | 752 | 808 | 56 | 1103376 | OK | [7 empty] | 13 | 200 | 213 | -13 | -0.23214 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_114M | Kamatipa North | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | perkins |  | 15 |  | 1454 | 1511 | 57 | 1103376 | OK | [7 empty] | 97 | 200 | 297 | -97 | -1.7018 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_249A | BUCHI | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Gen Logic |  | 16 |  | 431 | 533 | 102 | 1103376 | OK | [7 empty] | 41 | 250 | 291 | -41 | -0.40196 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_235M | KAWAMA KCC (Chimwemwe rlf | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | CK Works |  | 20 |  | 9933 | 9990 | 57 | 1103376 | OK | [7 empty] | 45 | 200 | 245 | -45 | -0.78947 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_123M | Mukuba University | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | IMG |  | 15 |  | 11923 | 11986 | 63 | 1103376 | OK | [7 empty] | 23 | 300 | 323 | -23 | -0.36508 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_351A | Riverside Congo Way | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | CK Works |  | 20 |  | 6346 | 6421 | 75 | 1103376 | OK | [7 empty] | 41 | 200 | 241 | -41 | -0.54667 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_044M | Kafubu Block | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Yanmar |  | 16 |  | 18183 | 18258 | 75 | 1103376 | OK | [7 empty] | 20 | 200 | 220 | -20 | -0.26667 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_314A | KAFUBU BLOCK | GNM | Royd | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | CK Works |  | 20 |  | 7844 | 7907 | 63 | 1103376 | OK | [7 empty] | 104 | 200 | 304 | -104 | -1.6508 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_050M | Luanshya Town Center | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Gen Logic |  | 20 |  | 8629 | 8732 | 103 | 1103376 | OK | [7 empty] | 68 | 200 | 268 | -68 | -0.66019 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_064M | Finsansa Basic | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Yanmar |  | 16 |  | 8041 | 8086 | 45 | 1103376 | OK | [7 empty] | 67 | 200 | 267 | -67 | -1.4889 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_227M | LUANSHYA EAST | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | Generator City |  | 16 |  | 7806 | 7875 | 69 | 1103376 | OK | [7 empty] | 42 | 200 | 242 | -42 | -0.6087 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_319A | Nkanga Hill (Mumena_1) | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | GL Yanmar |  | 15 |  |  | FAULTY | #VALUE! | 1103376 | #VALUE! | [7 empty] | 60 | 200 | 260 | -60 | #VALUE! | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_137M | Nkanga Hills | GNM | Royd | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-13 |  |  |  | GL Yanmar |  | 16 |  | 5829 | 5913 | 84 | 1103376 | OK | [7 empty] | 25 | 200 | 225 | -25 | -0.29762 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_118M | Kamaronde | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | CK Works |  | 20 |  | 3693 | 3712 | 19 | 1103400 | OK | [7 empty] | 52 | 150 | 202 | -52 | -2.7368 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_238M | NAPSA Complex | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | MPMC |  | 15 |  | 9214 | 9262 | 48 | 1103400 | OK | [7 empty] | 61 | 200 | 261 | -61 | -1.2708 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_206A | KALULUSHI | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | IMG |  | 15 |  | 7876 | 7948 | 72 | 1103400 | OK | [7 empty] | 145 | 300 | 445 | -145 | -2.0139 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_267A | KALULUSHI EAST | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Gen Logic |  | 16 |  | 14228 | 14277 | 49 | 1103400 | OK | [7 empty] | 220 | 300 | 520 | -220 | -4.4898 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_132M | Kalulushi West | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Gen Logic |  | 20 |  | 6162 | 6226 | 64 | 1103400 | OK | [7 empty] | 89 | 300 | 389 | -89 | -1.3906 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_119M | Lumumba | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Gen Logic |  | 16 |  | 10138 | 10138 | 0 | 1103400 | OK | [7 empty] | 100 | 150 | 250 | -100 | #DIV/0! | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_301A | CHIBULUMA TOWN | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Gen Logic |  | 16 |  | 10254 | 10283 | 29 | 1103400 | OK | [7 empty] | 67 | 300 | 367 | -67 | -2.3103 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_117M | Chibote | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Gen Logic |  | 15 |  | 6397 | 6437 | 40 | 1103400 | OK | [7 empty] | 70 | 200 | 270 | -70 | -1.75 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_126M | Chibuluma | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Gen Logic |  | 20 |  | 4155 | 4200 | 45 | 1103400 | OK | [7 empty] | 328 | 200 | 528 | -328 | -7.2889 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_132M | Kalulushi West | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Gen Logic |  | 20 |  | 8901 | 8922 | 21 | 1103400 | OK | [7 empty] | 272 | 100 | 372 | -272 | -12.9524 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_167M | Kafubu | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | LISTER PETTER |  | 16 |  | FAULTY | FAULTY | #VALUE! | 1103400 | #VALUE! | [7 empty] | 20 | 300 | 320 | -20 | #VALUE! | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_239A | LUFWANYAMA ROAD | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Diesel Electric |  | 16 |  | FAULTY | FAULTY | #VALUE! | 1103400 | #VALUE! | [7 empty] | 68 | 200 | 268 | -68 | #VALUE! | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_218M | WUSAKILE POLICE CAMP | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Generator City |  | 16 |  | 7681 | 7716 | 35 | 1103400 | OK | [7 empty] | 107 | 300 | 407 | -107 | -3.0571 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_250A | SOB | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Gen Logic |  | 15 |  | FAULTY | FAULTY | #VALUE! | 1103400 | #VALUE! | [7 empty] | 20 | 250 | 270 | -20 | #VALUE! | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_092M | Nkana Stadium | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Gen Logic |  | 16 |  | 5885 | 5966 | 81 | 1103400 | OK | [7 empty] | 191 | 250 | 441 | -191 | -2.358 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_222A | CHAMBOLI | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Gen Logic |  | 30 |  | 534 | 630 | 96 | 1103400 | OK | [7 empty] | 133 | 400 | 533 | -133 | -1.3854 | 4.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_217A | MAPOSA | GNM | FACKSON | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Gen Logic |  | 30 |  | 304 | 304 | 0 | 1103400 | OK | [7 empty] | 158 | 400 | 558 | -158 | #DIV/0! | 4.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_334A | Miseshi Village | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Generator City |  | 16 |  | 3712 | 3802 | 90 | 1103400 | OK | [7 empty] | 28 | 300 | 328 | -28 | -0.31111 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_013M | Dola Hill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Himoinsa |  | 30 |  | 6170 | 6259 | 89 | 1103400 | OK | [7 empty] | 48 | 400 | 448 | -48 | -0.53933 | 4.5 | [5 empty] | 0 | [8 empty] | TOTAL |  | CAPTURED
IHS_CBT_219M | PETAUKE CRESCENT | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | CK Works |  | 20 |  | 4321 | 4407 | 86 | 1103400 | OK | [7 empty] | 107 | 300 | 407 | -107 | -1.2442 | 2.5 | [5 empty] | 0 | [8 empty] | TOTAL |  | CAPTURED
IHS_CBT_222M | TWAPIA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Generator City |  | 13 |  | 12030 | 12122 | 92 | 1103400 | OK | [7 empty] | 92 | 300 | 392 | -92 | -1 | 2 | [5 empty] | 0 | [8 empty] | TOTAL |  | CAPTURED
IHS_CBT_023M | Twapia | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Gen Logic |  | 15 |  | 7931 | 8060 | 129 | 1103400 | OK | [7 empty] | 24 | 200 | 224 | -24 | -0.18605 | 1.8 | [5 empty] | 0 | [8 empty] | TOTAL |  | CAPTURED
IHS_CBT_029M | Zafico | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Green Power |  | 15 |  | 3729 | 3772 | 43 | 1103400 | OK | [7 empty] | 40 | 250 | 290 | -40 | -0.93023 | 1.8 | [5 empty] | 0 | [8 empty] | TOTAL |  | CAPTURED
IHS_CBT_226M | CHIFUBU WEST | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Generator City |  | 13 |  | 19638 | 19744 | 106 | 1103400 | OK | [7 empty] | 89 | 200 | 289 | -89 | -0.83962 | 2 | [5 empty] | 0 | [8 empty] | TOTAL |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | GL Yanmar |  | 20 |  | 838 | 869 | 31 | 1103400 | OK | [7 empty] | 51 | 200 | 251 | -51 | -1.6452 | 2 | [5 empty] | 0 | [8 empty] | TOTAL |  | CAPTURED
IHS_CBT_364A | Chifubu Sec. School | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | CK Works |  | 20 |  | 1097 | 1115 | 18 | 1103400 | OK | [7 empty] | 16 | 150 | 166 | -16 | -0.88889 | 4.5 | [5 empty] | 0 | [8 empty] | TOTAL |  | CAPTURED
IHS_CBT_257A | TWAPIA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | CK Works |  | 20 |  | 13106 | 13169 | 63 | 1103400 | OK | [7 empty] | 142 | 300 | 442 | -142 | -2.254 | 2.5 | [5 empty] | 0 | [8 empty] | TOTAL |  | CAPTURED
IHS_CBT_018M | Nkwanzi | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | CK Works |  | 20 |  | 1938 | 1948 | 10 | 1103400 | OK | [7 empty] | 334 | 300 | 634 | -334 | -33.4 | 2.5 | [5 empty] | 0 | [8 empty] | TOTAL |  | CAPTURED
IHS_CBT_285A | KWACHA | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | CK Works |  | 20 |  | 5826 | 5922 | 96 | 1103400 | OK | [7 empty] | 11 | 300 | 311 | -11 | -0.11458 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_093M | Kwacha East | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Gen Logic |  | 30 |  | 405 | 414 | 9 | 1103400 | OK | [7 empty] | 277 | 300 | 577 | -277 | -30.7778 | 4.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_103M | Kwacha central | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Gen Logic |  | 16 |  | 1193 | 1263 | 70 | 1103400 | OK | [7 empty] | 13 | 300 | 313 | -13 | -0.18571 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_296A | KAMUNGA | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Gen Logic |  | 16 |  | 6770 | 6822 | 52 | 1103400 | OK | [7 empty] | 5 | 200 | 205 | -5 | -0.096154 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_235M | KAWAMA KCC (Chimwemwe rlf | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | CK Works |  | 20 |  | 9990 | 10002 | 12 | 1103400 | OK | [7 empty] | 185 | 100 | 285 | -185 | -15.4167 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_114M | Kamatipa North | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | perkins |  | 15 |  | 1511 | 1521 | 10 | 1103400 | OK | [7 empty] | 252 | 100 | 352 | -252 | -25.2 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_112M | Kamtipa | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Gen Logic |  | 16 |  | 808 | 814 | 6 | 1103400 | OK | [7 empty] | 189 | 100 | 289 | -189 | -31.5 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_115M | Mindolo | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Gen Logic |  | 16 |  | 7796 | 7852 | 56 | 1103400 | OK | [7 empty] | 188 | 200 | 388 | -188 | -3.3571 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_107M | Mindolo South | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | perkins |  | 20 |  | 9675 | 9737 | 62 | 1103400 | OK | [7 empty] | 48 | 200 | 248 | -48 | -0.77419 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_269A | SOSOLISO | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Jiuan |  | 15 |  | 5957 | 6045 | 88 | 1103400 | OK | [7 empty] | 123 | 250 | 373 | -123 | -1.3977 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_351A | Riverside Congo Way | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | CK Works |  | 20 |  | 6421 | 6441 | 20 | 1103400 | OK | [7 empty] | 141 | 100 | 241 | -141 | -7.05 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_369A | Buntungwa | #N/A | ISAAC | #N/A | #N/A | #N/A |  | #N/A | #N/A |  |  | #N/A |  | 2025-11-14 |  |  |  | #N/A |  | #N/A |  | 0 | 50 | 50 | 1103400 | OK | [7 empty] | 120 | 200 | 320 | -120 | -2.4 | #N/A | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_367A | Ibenge Girls | GNM | ISAAC | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | CK Works |  | 20 |  | 4956 | 5049 | 93 | 1103400 | OK | [7 empty] | 5 | 200 | 205 | -5 | -0.053763 | 22 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_224A | MASAITI | GNM | ISAAC | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Earth Technology |  | 20 |  | 15134 | 15139 | 5 | 1103400 | OK | [7 empty] | 91 | 100 | 191 | -91 | -18.2 | 4.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_076M | Masaiti | GNM | ISAAC | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | GL Yanmar |  | 16 |  | 2109 | 2120 | 11 | 1103400 | OK | [7 empty] | 71 | 100 | 171 | -71 | -6.4545 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_058M | Mikomfwa | GNM | ISAAC | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Gen Logic |  | 16 |  | 8262 | 8291 | 29 | 1103400 | OK | [7 empty] | 59 | 150 | 209 | -59 | -2.0345 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_230A | MIKOMFWA | GNM | ISAAC | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Earth technology |  | 15 |  | 1300 | 1339 | 39 | 1103400 | OK | [7 empty] | 111 | 200 | 311 | -111 | -2.8462 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_054M | Mikomfwa Market | GNM | ISAAC | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Yanmar |  | 16 |  | 12775 | 12799 | 24 | 1103400 | OK | [7 empty] | 171 | 150 | 321 | -171 | -7.125 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_049M | Mikomfwa East | GNM | ISAAC | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Gen Logic |  | 16 |  | 6907 | 6931 | 24 | 1103400 | OK | [7 empty] | 109 | 300 | 409 | -109 | -4.5417 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_307A | TVTC | GNM | ISAAC | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Gen Logic |  | 16 |  |  | FAULTY | #VALUE! | 1103400 | #VALUE! | [7 empty] | 45 | 200 | 245 | -45 | #VALUE! | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_047M | Kamirenda | GNM | ISAAC | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Gen Logic |  | 16 |  | 13528 | 13554 | 26 | 1103400 | OK | [7 empty] | 137 | 200 | 337 | -137 | -5.2692 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_062M | Roan Township | GNM | ISAAC | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | CK Works |  | 20 |  | 8558 | 8614 | 56 | 1103400 | OK | [7 empty] | 79 | 200 | 279 | -79 | -1.4107 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_210A | LUANSHYA | GNM | ISAAC | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | CK Works |  | 20 |  | 8208 | 8282 | 74 | 1103400 | OK | [7 empty] | 111 | 200 | 311 | -111 | -1.5 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_214A | NDOLA FRA SILOS | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Roof Top |  | 2025-11-14 |  |  |  | Lamasat |  | 20 |  | 13256 | 13369 | 113 | 1103400 | OK | [7 empty] | 131 | 300 | 431 | -131 | -1.1593 | 2.5 | [5 empty] | 0 | [8 empty] | TOTAL |  | CAPTURED
IHS_CBT_336A | Fatima Girls | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | perkins |  | 15 |  | 11638 | 11692 | 54 | 1103400 | OK | [7 empty] | 111 | 100 | 211 | -111 | -2.0556 | 1.8 | [5 empty] | 0 | [8 empty] | TOTAL |  | CAPTURED
IHS_CBT_085M | Dangote | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Earth technology |  | 13 |  | 8377 | 8410 | 33 | 1103400 | OK | [7 empty] | 10 | 200 | 210 | -10 | -0.30303 | 2.5 | [5 empty] | 0 | [8 empty] | TOTAL |  | CAPTURED
IHS_CBT_309A | NDOLA LIME | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Gen Logic |  | 15 |  | 9003 | 9061 | 58 | 1103400 | OK | [7 empty] | 30 | 200 | 230 | -30 | -0.51724 | 2.5 | [5 empty] | 0 | [8 empty] | TOTAL |  | CAPTURED
IHS_CBT_224M | SKYWAYS KAPIRI ROAD | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Generator City |  | 13 |  | 4627 | 4722 | 95 | 1103400 | OK | [7 empty] | 5 | 300 | 305 | -5 | -0.052632 | 2 | [5 empty] | 0 | [8 empty] | TOTAL |  | CAPTURED
IHS_CBT_293A | MUSAKASONKA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Gen Logic |  | 20 |  | 1562 | 1629 | 67 | 1103400 | OK | [7 empty] | 63 | 200 | 263 | -63 | -0.9403 | 2.5 | [5 empty] | 0 | [8 empty] | TOTAL |  | CAPTURED
IHS_CBT_010M | Kabushi | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | IMG |  | 15 |  | 8041 | 8147 | 106 | 1103400 | OK | [7 empty] | 23 | 300 | 323 | -23 | -0.21698 | 2.5 | [5 empty] | 0 | [8 empty] | TOTAL |  | CAPTURED
IHS_CBT_024M | Ndeke Township | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | CK Works |  | 30 |  | 1437 | 1502 | 65 | 1103400 | OK | [7 empty] | 31 | 400 | 431 | -31 | -0.47692 | 4.5 | [5 empty] | 0 | [8 empty] | TOTAL |  | CAPTURED
IHS_CBT_283A | MASALA | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | IMG |  | 20 |  | 8121 | 8189 | 68 | 1103400 | OK | [7 empty] | 76 | 200 | 276 | -76 | -1.1176 | 2.5 | [5 empty] | 0 | [8 empty] | TOTAL |  | CAPTURED
IHS_CBT_338A | Musa Kasonka_3_Rlf | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | CK Works |  | 20 |  | 11404 | 39820 | 28416 | 1103400 | OK | [7 empty] | 10 | 250 | 260 | -10 | -0.00035191 | 2.5 | [5 empty] | 0 | [8 empty] | TOTAL |  | CAPTURED
IHS_CBT_332A | Ndeke_Ndola | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Roof Top |  | 2025-11-14 |  |  |  | 0 |  | 15 |  |  | 1138 | 1138 | 1103400 | OK | [7 empty] | 10 | 300 | 310 | -10 | -0.0087873 | 1.5 | [5 empty] | 0 | [8 empty] | TOTAL |  | CAPTURED
IHS_CBT_008M | Masala | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | Generator City |  | 13 |  |  | 6908 | 6908 | 1103400 | OK | [7 empty] | 10 | 200 | 210 | -10 | -0.0014476 | 2 | [5 empty] | 0 | [8 empty] | TOTAL |  | CAPTURED
IHS_CBT_056M | Masangano | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | GL Yanmar |  | 16 |  | FAULTY |  | #VALUE! | 1103400 | #VALUE! | [7 empty] | 100 | 200 | 300 | -100 | #VALUE! | 2 | [5 empty] | 0 | [8 empty] | TOTAL |  | CAPTURED
IHS_CBT_045M | Tuckugan | GNM | Kasoma | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-14 |  |  |  | GL Yanmar |  | 16 |  |  | FAULTY | #VALUE! | 1103400 | #VALUE! | [7 empty] | 10 | 100 | 110 | -10 | #VALUE! | 2 | [5 empty] | 0 | [8 empty] | TOTAL |  | CAPTURED
IHS_CBT_217M | KITWE MAIN SCHOOL | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | Generator City |  | 16 |  | 16354 | 16466 | 112 | 1103424 | OK | [7 empty] | 65 | 200 | 265 | -65 | -0.58036 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_121M | Ichipe | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | IHS_CBT_121M |  | 15 |  | 14492 | 14554 | 62 | 1103424 | OK | [7 empty] | 183 | 150 | 333 | -183 | -2.9516 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_118M | Kamaronde | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | CK Works |  | 20 |  | 3693 | 3712 | 19 | 1103424 | OK | [7 empty] | 126 | 150 | 276 | -126 | -6.6316 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_266A | KAWAMA Copperbelt | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | Gen Logic |  | 16 |  | 14921 | 15046 | 125 | 1103424 | OK | [7 empty] | 11 | 200 | 211 | -11 | -0.088 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_089M | Valley View | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | ASCOT |  | 30 |  | 3458 | 3257 | -201 | 1103424 | OK | [7 empty] | 0 | 950 | 950 | 0 | 0 | 4.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_090M | Jambo Drive | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | Gen Logic |  | 16 |  | 9065 | 9112 | 47 | 1103424 | OK | [7 empty] | 51 | 200 | 251 | -51 | -1.0851 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_099M | Kitwe Town Center | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | CDP |  | 15 |  | 9313 | 9444 | 131 | 1103424 | OK | [7 empty] | 56 | 200 | 256 | -56 | -0.42748 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_368A | HIGHLAND SCHOOL | #N/A | FACKSON | #N/A | #N/A | #N/A |  | #N/A | #N/A |  |  | #N/A |  | 2025-11-15 |  |  |  | #N/A |  | #N/A |  | 10328 | 10390 | 62 | 1103424 | OK | [7 empty] | 104 | 300 | 404 | -104 | -1.6774 | #N/A | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_105M | Buntungwa | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | Gen Logic |  | 16 |  | 6204 | 6248 | 44 | 1103424 | OK | [7 empty] | 117 | 150 | 267 | -117 | -2.6591 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_228A | MINDOLO | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | Earth technology |  | 20 |  | 11815 | 11894 | 79 | 1103424 | OK | [7 empty] | 114 | 200 | 314 | -114 | -1.443 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_297A | KITWE POLICE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | Gen Logic |  | 16 |  | 8214 | 8284 | 70 | 1103424 | OK | [7 empty] | 108 | 300 | 408 | -108 | -1.5429 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_251A | Kitwe Railways | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | MPI |  | 20 |  | 6317 | 6396 | 79 | 1103424 | OK | [7 empty] | 92 | 300 | 392 | -92 | -1.1646 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_073M | Cedrics Farm | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | perkins |  | 15 |  | 17796 | 17892 | 96 | 1103424 | OK | [7 empty] | 78 | 200 | 278 | -78 | -0.8125 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_352A | Parklands TBN | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | CK Works |  | 20 |  | 8766 | 8859 | 93 | 1103424 | OK | [7 empty] | 125 | 250 | 375 | -125 | -1.3441 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_353A | Court Barrifs | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | CK Works |  | 20 |  | 10972 | 11016 | 44 | 1103424 | OK | [7 empty] | 159 | 150 | 309 | -159 | -3.6136 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_082M | Ndeke Extension | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | Gen Logic |  | 20 |  | 7819 | 7872 | 53 | 1103424 | OK | [7 empty] | 91 | 300 | 391 | -91 | -1.717 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_086M | Minsenshi-natwange | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | Gen Logic |  | 16 |  | FAULTY | FAULTY | #VALUE! | 1103424 | #VALUE! | [7 empty] | 79 | 150 | 229 | -79 | #VALUE! | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_088M | Geddis | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | CDP |  | 13 |  | 12609 | 12665 | 56 | 1103424 | OK | [7 empty] | 87 | 300 | 387 | -87 | -1.5536 | 1.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_083M | Nkana East | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | Gen Logic |  | 16 |  | 4334 | 4420 | 86 | 1103424 | OK | [7 empty] | 132 | 300 | 432 | -132 | -1.5349 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_305A | LUANGWA KAFUE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | Yanmar |  | 16 |  | 1394 | 1462 | 68 | 1103424 | OK | [7 empty] | 58 | 100 | 158 | -58 | -0.85294 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_014M | Lubuto | GNM | FACKSON | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | CK Works |  | 20 |  | 4985 | 5047 | 62 | 1103424 | OK | [7 empty] | 112 | 300 | 412 | -112 | -1.8065 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_223A | LUFWANYAMA | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | Gen Logic |  | 20 |  | 6678 | 6758 | 80 | 1103424 | OK | [7 empty] | 25 | 300 | 325 | -25 | -0.3125 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_203M | Lufwanyama | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | Gen Logic |  | 13 |  | 22012 | 22061 | 49 | 1103424 | OK | [7 empty] | 223 | 300 | 523 | -223 | -4.551 | 1.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_233A | CHIPULUKUSU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | Earth Technology |  | 15 |  | 5396 | 5445 | 49 | 1103424 | OK | [7 empty] | 64 | 300 | 364 | -64 | -1.3061 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_037M | Minsundu | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | GL Yanmar |  | 16 |  | FAULTY | FAULTY | #VALUE! | 1103424 | #VALUE! | [7 empty] | 10 | 300 | 310 | -10 | #VALUE! | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_264A | NDOLA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | Gen Logic |  | 16 |  | 6567 | 6576 | 9 | 1103424 | OK | [7 empty] | 76 | 300 | 376 | -76 | -8.4444 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_364A | Chifubu Sec. School | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | CK Works |  | 20 |  | 1115 | 1125 | 10 | 1103424 | OK | [7 empty] | 80 | 200 | 280 | -80 | -8 | 4.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_245A | NORTHRISE | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | Lamasat |  | 20 |  | 9098 | 9201 | 103 | 1103424 | OK | [7 empty] | 45 | 300 | 345 | -45 | -0.43689 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_359A | Cross Crescent | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | CK Works |  | 20 |  | 6021 | 6104 | 83 | 1103424 | OK | [7 empty] | 86 | 300 | 386 | -86 | -1.0361 | 4.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_005M | Premium Plaza | CCS | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Roof Top |  | 2025-11-15 |  |  |  | N/A |  | N/A |  | 9016 | 9056 | 40 | 1103424 | OK | [7 empty] | 179 | 300 | 479 | -179 | -4.475 | N/A | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_216M | COOL BANANAS | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | Generator City |  | 13 |  | 8246 | 8334 | 88 | 1103424 | OK | [7 empty] | 370 | 150 | 520 | -370 | -4.2045 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_029M | Zafico | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | Green Power |  | 15 |  | FAULTY | FAULTY | #VALUE! | 1103424 | #VALUE! | [7 empty] | 30 | 150 | 180 | -30 | #VALUE! | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_362A | Ndola Central Police | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | CK Works |  | 20 |  | FAULTY | FAULTY | #VALUE! | 1103424 | #VALUE! | [7 empty] | 10 | 100 | 110 | -10 | #VALUE! | 4.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_264A | NDOLA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | Gen Logic |  | 16 |  | 6533 | 6567 | 34 | 1103424 | OK | [7 empty] | 70 | 50 | 120 | -70 | -2.0588 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_306A | TUG-ARGAN | GNM | Royd | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | Yanmar |  | 16 |  | 13357 | 13456 | 99 | 1103424 | OK | [7 empty] | 79 | 200 | 279 | -79 | -0.79798 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_035M | Kaloko | GNM | Royd | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | Himoinsa |  | 30 |  | 9807 | 9892 | 85 | 1103424 | OK | [7 empty] | 20 | 200 | 220 | -20 | -0.23529 | 4.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_045M | Tuckugan | GNM | Royd | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | GL Yanmar |  | 16 |  |  | FAULTY | #VALUE! | 1103424 | #VALUE! | [7 empty] | 10 | 100 | 110 | -10 | #VALUE! | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_336A | Fatima Girls | GNM | Royd | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | perkins |  | 15 |  | 11692 | 11719 | 27 | 1103424 | OK | [7 empty] | 110 | 200 | 310 | -110 | -4.0741 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_232A | LUBUTO | GNM | Royd | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-15 |  |  |  | Gen Logic |  | 20 |  |  | 11433 | 11433 | 1103424 | OK | [7 empty] | 81 | 50 | 131 | -81 | -0.0070848 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_042M | Golden Lay | GNM | ISAAC | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | MPI |  | 15 |  | 8386 | 8391 | 5 | 1103448 | OK | [7 empty] | 90 | 100 | 190 | -90 | -18 | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_201A | BALUBA | GNM | ISAAC | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | Earth technology |  | 13 |  | 981 | 1087 | 106 | 1103448 | OK | [7 empty] | 63 | 200 | 263 | -63 | -0.59434 | 1.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_069M | Mpatamato West | GNM | ISAAC | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | Gen Logic |  | 16 |  | 16167 | 16224 | 57 | 1103448 | OK | [7 empty] | 20 | 200 | 220 | -20 | -0.35088 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_065M | Mpatamato East | GNM | ISAAC | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | Yanmar |  | 16 |  | 8798 | 8798 | 0 | 1103448 | OK | [7 empty] | 69 | 100 | 169 | -69 | #DIV/0! | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_215M | PHILIP FARM | GNM | ISAAC | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Solar-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | perkins |  | 15 |  | FAULTY | FAULTY | #VALUE! | 1103448 | #VALUE! | [7 empty] | 122 | 150 | 272 | -122 | #VALUE! | 1.8 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_161M | Mikata Mpongwe | GNM | ISAAC | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Solar-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | IMG |  | 20 |  | 10125 | 10227 | 102 | 1103448 | OK | [7 empty] | 10 | 150 | 160 | -10 | -0.098039 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_181M | Lukanga resettlement | GNM | ISAAC | Copperbelt | Mwenya Banda | Neddy Chiwasa |  | Outdoor | Solar-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | CK Works |  | 20 |  | 5865 | 6015 | 150 | 1103448 | OK | [7 empty] | 10 | 300 | 310 | -10 | -0.066667 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_291A | MWATAYANVWA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | Gen Logic |  | 20 |  | 4776 | 4832 | 56 | 1103448 | OK | [7 empty] | 76 | 100 | 176 | -76 | -1.3571 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_015M | Yengwe | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | CK Works |  | 20 |  | 5913 | 5937 | 24 | 1103448 | OK | [7 empty] | 236 | 300 | 536 | -236 | -9.8333 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_218A | PAMODZI | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | Gen Logic |  | 20 |  | 14107 | 14192 | 85 | 1103448 | OK | [7 empty] | 273 | 300 | 573 | -273 | -3.2118 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_025M | Pamozi Extension | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | GL Yanmar |  | 16 |  | FAULTY | FAULTY | #VALUE! | 1103448 | #VALUE! | [7 empty] | 15 | 200 | 215 | -15 | #VALUE! | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | GL Yanmar |  | 20 |  | 869 | 912 | 43 | 1103448 | OK | [7 empty] | 36 | 100 | 136 | -36 | -0.83721 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_252A | CHIFUBU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | Gen Logic |  | 30 |  | 4693 | 4769 | 76 | 1103448 | OK | [7 empty] | 30 | 100 | 130 | -30 | -0.39474 | 4.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_222M | TWAPIA OVERSPILL | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | Generator City |  | 13 |  | 12122 | 12168 | 46 | 1103448 | OK | [7 empty] | 189 | 100 | 289 | -189 | -4.1087 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_361A | Mitengo TDRC | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | CK Works |  | 20 |  | 6172 | 6225 | 53 | 1103448 | OK | [7 empty] | 7 | 250 | 257 | -7 | -0.13208 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_241M | Kagem mine | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | perkins |  | 20 |  | 14607 | 14733 | 126 | 1103448 | OK | [7 empty] | 15 | 250 | 265 | -15 | -0.11905 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_259A | KAMAKANGA I & II | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | perkins |  | 20 |  | 21843 | 21955 | 112 | 1103448 | OK | [7 empty] | 133 | 250 | 383 | -133 | -1.1875 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_129M | Emerald Mine Lufwanyama | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | Gen Logic |  | 15 |  | 25726 | 25847 | 121 | 1103448 | OK | [7 empty] | 132 | 300 | 432 | -132 | -1.0909 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_146M | Miku Mining | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | Gen Logic |  | 20 |  | 21124 | 21266 | 142 | 1103448 | OK | [7 empty] | 15 | 400 | 415 | -15 | -0.10563 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_118M | Kamaronde | GNM | SAMUEL | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | CK Works |  | 20 |  | 3712 | 3738 | 26 | 1103448 | OK | [7 empty] | 200 | 150 | 350 | -200 | -7.6923 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_079M | Ndeke | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | CK Works |  | 20 |  | 10457 | 10523 | 66 | 1103448 | OK | [7 empty] | 94 | 400 | 494 | -94 | -1.4242 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_356A | New Ndeke Village | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | CK Works |  | 20 |  | 1406 | 1500 | 94 | 1103448 | OK | [7 empty] | 58 | 400 | 458 | -58 | -0.61702 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_244A | NDEKE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | Earth technology |  | 15 |  | 4392 | 4469 | 77 | 1103448 | OK | [7 empty] | 105 | 300 | 405 | -105 | -1.3636 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_355A | Ndeke Sub. A | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Gen Only |  |  | Green Field |  | 2025-11-16 |  |  |  | CK Works |  | 20 |  | 15225 | 15291 | 66 | 1103448 | OK | [7 empty] | 77 | 250 | 327 | -77 | -1.1667 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_075M | Ndeke Changachanga | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | Gen Logic |  | 20 |  | 4154 | 4232 | 78 | 1103448 | OK | [7 empty] | 64 | 400 | 464 | -64 | -0.82051 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_345A | Ndeke Changachanga south 3G | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | Gen Logic |  | 20 |  | 13962 | 14058 | 96 | 1103448 | OK | [7 empty] | 33 | 300 | 333 | -33 | -0.34375 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_305A | LUANGWA KAFUE | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | Yanmar |  | 16 |  | 1462 | 1484 | 22 | 1103448 | OK | [7 empty] | 78 | 100 | 178 | -78 | -3.5455 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_274A | ZNS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | Gen Logic |  | 16 |  | 13554 | 13733 | 179 | 1103448 | OK | [7 empty] | 104 | 200 | 304 | -104 | -0.58101 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_084M | Kitwe ZNS | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | CDP |  | 15 |  | 18710 | 18788 | 78 | 1103448 | OK | [7 empty] | 25 | 200 | 225 | -25 | -0.32051 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_263A | NAKADOLI | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | Gen Logic |  | 16 |  | 7217 | 7316 | 99 | 1103448 | OK | [7 empty] | 5 | 200 | 205 | -5 | -0.050505 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_229A | CHIMWEMWE | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | Gen Logic |  | 20 |  | 859 | 919 | 60 | 1103448 | OK | [7 empty] | 76 | 300 | 376 | -76 | -1.2667 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_266A | KAWAMA Copperbelt | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | Gen Logic |  | 16 |  | 15046 | 15067 | 21 | 1103448 | OK | [7 empty] | 156 | 300 | 456 | -156 | -7.4286 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_113M | Green Belt | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | IMG |  | 20 |  | 10968 | 11065 | 97 | 1103448 | OK | [7 empty] | 41 | 300 | 341 | -41 | -0.42268 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_333A | Mindolo North | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | perkins |  | 15 |  | 9361 | 9386 | 25 | 1103448 | OK | [7 empty] | 184 | 200 | 384 | -184 | -7.36 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_087M | Lulamba School | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | perkins |  | 20 |  | 517 | 605 | 88 | 1103448 | OK | [7 empty] | 5 | 300 | 305 | -5 | -0.056818 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_296A | KAMUNGA | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | Gen Logic |  | 16 |  | 6822 | 6868 | 46 | 1103448 | OK | [7 empty] | 32 | 100 | 132 | -32 | -0.69565 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_080M | Kalambo | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | Gen Logic |  | 16 |  | 6861 | 6910 | 49 | 1103448 | OK | [7 empty] | 13 | 200 | 213 | -13 | -0.26531 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_033M | Bwana Mukubwa | GNM | Royd | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | GL Yanmar |  | 16 |  | 1365 | 1430 | 65 | 1103448 | OK | [7 empty] | 42 | 50 | 92 | -42 | -0.64615 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_024M | Ndeke Township | GNM | Royd | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | CK Works |  | 30 |  | 1434 | 1529 | 95 | 1103448 | OK | [7 empty] | 64 | 200 | 264 | -64 | -0.67368 | 4.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_027M | Kantolomba | GNM | Royd | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | CK Works |  | 20 |  | 6005 | 6094 | 89 | 1103448 | OK | [7 empty] | 47 | 300 | 347 | -47 | -0.52809 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_283A | MASALA | GNM | Royd | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | IMG |  | 20 |  | 8721 | 8217 | -504 | 1103448 | OK | [7 empty] | 10 | 300 | 310 | -10 | 0.019841 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_363A | Milemu Sec. School | GNM | Royd | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | CK Works |  | 20 |  | 10380 | 10420 | 40 | 1103448 | OK | [7 empty] | 145 | 200 | 345 | -145 | -3.625 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_293A | MUSAKASONKA | GNM | Royd | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | Gen Logic |  | 20 |  | 1562 | 1658 | 96 | 1103448 | OK | [7 empty] | 7 | 150 | 157 | -7 | -0.072917 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_008M | Masala | GNM | Royd | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | Generator City |  | 13 |  | 6843 | 6941 | 98 | 1103448 | OK | [7 empty] | 36 | 200 | 236 | -36 | -0.36735 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_360A | Hilcrest Extension | GNM | Royd | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | CK Works |  | 20 |  | 11032 | 11083 | 51 | 1103448 | OK | [7 empty] | 46 | 200 | 246 | -46 | -0.90196 | 5.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_040M | Seed Of Hope | GNM | Royd | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | Lamasat |  | 15 |  | 25422 | 25491 | 69 | 1103448 | OK | [7 empty] | 36 | 200 | 236 | -36 | -0.52174 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_124M | Kawama East | CCS | Royd | Copperbelt | Mwenya Banda | Panji Njovu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | perkins |  | 15 |  | 22088 | 22141 | 53 | 1103448 | OK | [7 empty] | 108 | 200 | 308 | -108 | -2.0377 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_227A | FIWALE | GNM | Royd | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | GNM |  | 15 |  | 5258 | 5319 | 61 | 1103448 | OK | [7 empty] | 10 | 150 | 160 | -10 | -0.16393 | 1.8 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_070M | Kauanga Basic | GNM | Royd | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | Earth technology |  | 20 |  | 12676 | 12703 | 27 | 1103448 | OK | [7 empty] | 122 | 100 | 222 | -122 | -4.5185 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_362A | Ndola Central Police | GNM | Royd | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | CK Works |  | 20 |  |  | 12598 | 12598 | 1103448 | OK | [7 empty] | 5 | 50 | 55 | -5 | -0.00039689 | 4.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_349A | Kafubu Mall | GNM | Royd | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | Gen Logic |  | 16 |  |  | 16765 | 16765 | 1103448 | OK | [7 empty] | 78 | 50 | 128 | -78 | -0.0046525 | 2 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_016M | Itawa | GNM | Royd | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-16 |  |  |  | Vitalgen |  | 30 |  |  | 5078 | 5078 | 1103448 | OK | [7 empty] | 117 | 50 | 167 | -117 | -0.023041 | 4.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_017M | Overspill | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-17 |  |  |  | Falcon |  | 20 |  | 9370 | 9468 | 98 | 1103472 | OK | [7 empty] | 22 | 200 | 128 | -78 | -0.79592 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_031M | Kawama | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-17 |  |  |  | GL Yanmar |  | 20 |  | 912 | 927 | 15 | 1103472 | OK | [7 empty] | 61 | 200 | 167 | -117 | -7.8 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_219M | PETAUKE CRESCENT | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-17 |  |  |  | CK Works |  | 20 |  | 4407 | 4467 | 60 | 1103472 | OK | [7 empty] | 107 | 100 | 207 | -107 | -1.7833 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_291A | MWATAYANVWA | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-17 |  |  |  | Gen Logic |  | 20 |  | 4832 | 4844 | 12 | 1103472 | OK | [7 empty] | 118 | 200 | 318 | -118 | -9.8333 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_252A | CHIFUBU | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-17 |  |  |  | Gen Logic |  | 30 |  | 4769 | 4792 | 23 | 1103472 | OK | [7 empty] | 19 | 300 | 319 | -19 | -0.82609 | 4.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_232A | LUBUTO | GNM | KAMBOLE | Copperbelt | Mwenya Banda | Elvis Mumba |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-17 |  |  |  | Gen Logic |  | 20 |  | 8060 | 8090 | 30 | 1103472 | OK | [7 empty] | 57 | 50 | 107 | -57 | -1.9 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_235M | KAWAMA KCC (Chimwemwe rlf | GNM | Jaula | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-17 |  |  |  | CK Works |  | 20 |  | 10002 | 10047 | 45 | 1103472 | OK | [7 empty] | 45 | 50 | 95 | -45 | -1 | 2.5 | [5 empty] | 0 | [8 empty] | MERU |  | CAPTURED
IHS_CBT_237A | NKANA WEST | CCS | FACKSON | COPPERBELT | Mwenya Banda | Chrispin Lindundu |  | Indoor | Grid-Gen |  |  | Green Field |  | 2025-11-17 |  |  |  | Earth technology |  | 20 |  | 12513 | 12598 | 85 | 1103472 | OK | [7 empty] | 23 | 100 | 123 | -23 | -0.27059 | 2.5 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
IHS_CBT_334A | Miseshi Village | GNM | FACKSON | Copperbelt | Mwenya Banda | Chrispin Lindundu |  | Outdoor | Grid-Gen |  |  | Green Field |  | 2025-11-17 |  |  |  | Generator City |  | 16 |  | 3802 | 3867 | 65 | 1103472 | OK | [7 empty] | 5 | 25 | 30 | -5 | -0.076923 | 2 | [5 empty] | 0 | [8 empty] | SAHARA |  | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED
[24 empty] | 0 | 0 | OK | [9 empty] | 0 | 0 | #DIV/0! | [6 empty] | 0 | [10 empty] | CAPTURED

## IHS DATABASE
# | Client ID | Site ID | Site Name | Longitude | Latitude | Region | Manufacturers CPH | State | District | Liquid Fiber (Y/N) | MTN Fiber (Y/N) | Airtel Fiber (Y/N) | Demo. Classification | Technology | Site Classification 2. (Platinum/Gold/Silver) | TIS Priority | TIS | Tower Status | Power Topology | Tower Type | Tower Height (m) | Site Configuration (Indoor/Outdoor) | zu | Maintenance Technician Inhouse | Refueling Technician Inhouse | MNO | RM | Subcon | Refuelling Subcon | Assembler | Gen Make | Gen Capacity (KVA) | Engine Brand | Engine Model | Alternator Brand | Alternator Model | Tank Size (L) | Rectifier Brand | Rectifier Model | Rectifier Capacity (A) | Battery Brand | Site Battery Capcity | One Battery Voltage (V) | One Battery Amperage (AH) | Number of batteries | Aircon 1 Brand | Aircon 2 Brand | Capacity (BTU) ac1 | Capacity (BTU)ac2 | Number of Aircons | Total DC loads (A) | Total DC load (KW) | No. of tenants on site | Tenants on site | MTN Site ID | AIRTEL Site ID | Fire Extinguisher (yes/No) | Fire Extinguisher service date | Security light(working/not working) | palisade/mesh | Inala/Netco | Date Updated | BUB requirements | BUB allocated | Idle BUB | BUB collected | region offices | Remarks | status | BUB installation Date | Mains Rectifier | hauwei solar | DG Swaps | Idle DGs | DGs collected | Allocation | Reccommended DG capacity ( KVA ) | date installed | Status | Average Solar/Hybrid Running Hours (hrs per day, for last quarter period) | Average Grid (hrs per day, for last quarter period) | Average Generator Running Hours (hrs per day, for last quarter period) | Remarks | Comment
1 |  | IHS_LSK_477A | New Kenneth Kaunda International Airport | 28.4493 | -15.3257 | Lusaka | #N/A | Lusaka | Lusaka | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid only | Green Field | RT | Outdoor | Kennedy Mwansa | N/A | N/A | Airtel | Evans Ngonga | In House | In House | perkins | [6 empty] | N/A | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 32 | [32 empty] | IHS_LSK_477A
624 | T3299 | IHS_CBT_001M | Kanini | 28.6277 | -12.9762 | Copperbelt | 2.5 | COPPERBELT | NDOLA | Yes | Yes | No | Urban | 2G 3G 4G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | IMG | IMG | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | n/a | N/A | 116.4 | 0 | 3 | MTNAirtelLiquid Telecom | T3299 | ZM6957 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_001M
408 | T3202 | IHS_CBT_002M | Hillcrest | 28.6193 | -12.9801 | Copperbelt | 2.5 | COPPERBELT | NDOLA | Yes | Yes | No | Urban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | GL Yanmar | GL Yanmar | 20 | Yanmar | 4TNE | Mecc Alte | 0 | 750 | Delta | DPS 2400B-48-5 | 250 | Wolong | 600 | 2 | 600 | 24 | samsung | samsung | 18000 | 18000 | 2 | 68.2 | 0 | 2 | MTNAirtel | T3202 | ZM0404 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_002M
1721 | T3023 | IHS_CBT_003M | Swimming Pool | 28.6388 | -12.9733 | Copperbelt | 4.5 | COPPERBELT | NDOLA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BB | On Air | Grid-Gen | Green Field | 60 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | CK Works | CK Works | 30 | perkins | DJ83400S | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 135 | 0 | 2 | MTNAir-link | T3023 | 0 | yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_003M
1420 | T3323 | IHS_CBT_004M | Ndola T. Centre | 28.6396 | -12.9645 | Copperbelt | 2.5 | COPPERBELT | NDOLA | Yes | No | No | Urban | 2G 3G 4G | P2 | BTS | HUB | On Air | Grid-Gen | Green Field | 36 | Outdoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Falcon | Falcon | 20 | perkins | GV 51790V | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 98 | 0 | 3 | MTNAirtelLiquid Telecom | T3323 | ZM0243 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_004M
1548 | T3022 | IHS_CBT_005M | Premium Plaza | 28.6305 | -12.9586 | Copperbelt | N/A | COPPERBELT | NDOLA | Yes | No | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On Air | Grid-Gen | Roof Top | RT | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | CCS | In House | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Delta | DPS 2400B-48-5 | 250 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 66 | 0 | 2 | MTNLiquid Telecom | T3022 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_005M
872 | T3352 | IHS_CBT_006M | Lubuto Central | 28.6205 | -12.996 | Copperbelt | 1.8 | COPPERBELT | NDOLA | No | Yes | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Lamasat | Lamasat | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-HA1-C10 | 250 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | n/a | N/A | 88 | 0 | 1 | MTN | T3352 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_006M
1153 | T3218 | IHS_CBT_007M | Mpelembe House | 28.6497 | -12.9682 | Copperbelt | 1.8 | COPPERBELT | NDOLA | No | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On Air | Grid-Gen | Roof Top | RT | Outdoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Lamasat | Lamasat | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Emerson | 701 IG4 | 300 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | n/a | N/A | 58 | 0 | 1 | MTN | T3218 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_007M
1028 | T3198 | IHS_CBT_008M | Masala | 28.6447 | -12.9942 | Copperbelt | 2 | COPPERBELT | NDOLA | Yes | No | No | Suburban | 2G 3G 4G | P1 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Generator City | Generator City | 13 | Yanmar | 3TNE88-G1A | ALPHAGEN | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 110 | 0 | 1 | MTN | T3198 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_008M
1730 | T3024 | IHS_CBT_009M | Tazama Building | 28.652 | -12.9693 | Copperbelt | 2 | COPPERBELT | NDOLA | No | No | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On Air | Grid-Gen | Roof Top | RT | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | IMG | IMG | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 80 | 0 | 1 | MTN | T3024 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_009M
488 | T3084 | IHS_CBT_010M | Kabushi | 28.6285 | -13.0017 | Copperbelt | 2.5 | COPPERBELT | NDOLA | No | Yes | No | Suburban | 2G 3G | P1 | BTS | BB | On Air | Grid-Gen | Green Field | 54 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | IMG | IMG | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 125 | 0 | 1 | MTN | T3084 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_010M
1132 | T3353 | IHS_CBT_011M | Monkey Mountain | 28.602 | -12.9774 | Copperbelt | 2 | COPPERBELT | NDOLA | Yes | No | No | Urban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 40 | Outdoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Green Power | Green Power | 16 | perkins | 0 | Mecc Alte | 0 | 600 | Power cube | ICC330-HA1-C10 | 250 | Power safe | 1200 | 2 | 1200 | 24 | N/A | N/A | N/A | n/a | N/A | 118 | 0 | 3 | MTNAirtelLiquid Telecom | T3353 | ZM0403 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_011M
440 | T3354 | IHS_CBT_012M | Itawa West | 28.6533 | -12.9835 | Copperbelt | 2.5 | COPPERBELT | NDOLA | No | Yes | No | Urban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Lamasat | Lamasat | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Wolong | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 70 | 0 | 1 | MTN | T3354 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_012M
337 | T3211 | IHS_CBT_013M | Dola Hill | 28.6059 | -12.9573 | Copperbelt | 4.5 | COPPERBELT | NDOLA | Yes | Yes | No | Urban | 2G 3G 4G | P3 | HUB | BB | On Air | Grid-Gen | Green Field | 80 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Himoinsa | Himoinsa | 30 | Yanmar | 4TNV | HIMOINSA | SK 160 LB | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 175 | 0 | 2 | MTNAirtel | T3211 | ZM3962 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_013M
870 | T3201 | IHS_CBT_014M | Lubuto | 28.6121 | -13.004 | Copperbelt | 2.5 | COPPERBELT | NDOLA | Yes | Yes | No | Suburban | 2G 3G 4G | P2 | BTS | HUB | On Air | Grid-Gen | Green Field | 42 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | CK Works | CK Works | 20 | perkins | U 988804 C | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 18000 | 18000 | 2 | 112 | 0 | 2 | MTNLiquid Telecom | T3201 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_014M
1786 | T3055 | IHS_CBT_015M | Yengwe | 28.6484 | -12.9483 | Copperbelt | 2.5 | COPPERBELT | NDOLA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Power safe | 1200 | 2 | 1200 | 24 | LG | LG | 18000 | 18000 | 2 | 194 | 0 | 3 | MTNAirtelLiquid Telecom | T3055 | ZM6740 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_015M
439 | T3083 | IHS_CBT_016M | Itawa | 28.6651 | -12.9853 | Copperbelt | 4.5 | COPPERBELT | NDOLA | No | Yes | No | Urban | 2G 3G 4G | P3 | BTS | BB | On Air | Grid-Gen | Green Field | 54 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Vitalgen | Vitalgen | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 117 | 0 | 2 | MTNAirtel | T3083 | ZM6838 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_016M
1516 | T3324 | IHS_CBT_017M | Overspill | 28.6269 | -12.9363 | Copperbelt | 2.5 | COPPERBELT | NDOLA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Falcon | Falcon | 20 | perkins | GN66044U | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | n/a | N/A | 85 | 0 | 1 | MTN | T3324 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_017M
1474 | T3204 | IHS_CBT_018M | Nkwanzi | 28.6403 | -12.9367 | Copperbelt | 2.5 | COPPERBELT | NDOLA | Yes | Yes | No | Suburban | 2G 3G | P2 | BTS | HUB | On Air | Grid-Gen | Green Field | 42 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 138 | 0 | 2 | MTNAirtel | T3204 | ZM6785 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_018M
1288 | T3203 | IHS_CBT_020M | Mushili | 28.6305 | -13.0188 | Copperbelt | 4.5 | COPPERBELT | NDOLA | No | Yes | No | Suburban | 2G 3G | P2 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | CK Works | CK Works | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HA1-C10 | 750 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 144 | 0 | 2 | MTNAirtel | T3203 | ZM3468 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_020M
1669 | T3229 | IHS_CBT_021M | Sky ways | 28.6 | -13.0092 | Copperbelt | 2.5 | COPPERBELT | NDOLA | No | No | No | Urban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | CK Works | CK Works | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 126 | 0 | 4 | MTNAirtelINQLiquid Telecom | T3229 | ZM6582 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_CBT_021M
694 | T3077 | IHS_CBT_022M | Kasembo | 28.6439 | -13.0163 | Copperbelt | 2.5 | COPPERBELT | NDOLA | Yes | Yes | No | Suburban | 2G 3G 4G | P2 | BTS | BTS | On Air | Grid-Gen | Green Field | 50 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 18000 | 18000 | 2 | 125 | 0 | 3 | MTNAirtelLiquid Telecom | T3077 | ZM3293 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_022M
1750 | T3054 | IHS_CBT_023M | Twapia | 28.5835 | -12.9855 | Copperbelt | 1.8 | COPPERBELT | NDOLA | No | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 50 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 15 | perkins | 0 | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 18000 | 18000 | 2 | 51 | 0 | 1 | MTN | T3054 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_023M
1409 | T3233 | IHS_CBT_024M | Ndeke Township | 28.6632 | -13.0066 | Copperbelt | 4.5 | COPPERBELT | NDOLA | No | Yes | No | Suburban | 2G 3G | P2 | BTS | BB | On Air | Grid-Gen | Green Field | 30 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | CK Works | CK Works | 30 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 18000 | 18000 | 2 | 185 | 0 | 2 | MTNAirtel | T3233 | ZM6959 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_024M
1520 | T3205 | IHS_CBT_025M | Pamozi Extension | 28.6238 | -12.9262 | Copperbelt | 2 | COPPERBELT | NDOLA | Yes | Yes | No | Suburban | 2G 3G 4G | P2 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | GL Yanmar | GL Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Power cube | ICC330-HA1-C10 | 250 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 72.4 | 0 | 1 | MTN | T3205 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_025M
634 | T3351 | IHS_CBT_027M | Kantolomba | 28.6337 | -13.0295 | Copperbelt | 2.5 | COPPERBELT | NDOLA | No | Yes | No | Suburban | 2G 3G | P2 | BTS | BTS | On Air | Grid-Gen | Green Field | 30 | Outdoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 154 | 0 | 2 | MTNAirtel | T3351 | ZM0237 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_027M
1788 | T3355 | IHS_CBT_029M | Zafico | 28.5695 | -12.9728 | Copperbelt | 1.8 | COPPERBELT | NDOLA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Green Power | Green Power | 15 | perkins | 0 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 56 | 0 | 2 | MTNAirtel | T3355 | ZM6868 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_029M
1416 | T3274 | IHS_CBT_030M | Ndola Industrial | 28.6642 | -13.0234 | Copperbelt | 2.5 | COPPERBELT | NDOLA | Yes | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | MPI | MPI | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 89 | 0 | 1 | MTN | T3274 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_030M
745 | T3102 | IHS_CBT_031M | Kawama | 28.6187 | -12.9161 | Copperbelt | 2 | COPPERBELT | NDOLA | No | Yes | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 48 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | GL Yanmar | GL Yanmar | 20 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | C&D True | 704 | 12 | 176 | 16 | LG | LG | 18000 | 18000 | 2 | 48.6 | 0 | 1 | MTN | T3102 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_031M
314 | T3197 | IHS_CBT_032M | Cleveland | 28.6906 | -12.9783 | Copperbelt | 2.5 | COPPERBELT | NDOLA | No | No | No | Suburban | 2G 3G | P4 | BTS | HUB | On Air | Grid-Gen | Green Field | 42 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 50 | 0 | 2 | MTNAirtel | T3197 | ZM3966 | yes |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_032M
58 | T3209 | IHS_CBT_033M | Bwana Mukubwa | 28.6958 | -13.0175 | Copperbelt | 2 | COPPERBELT | NDOLA | No | No | No | Suburban | 2G 3G | P4 | BTS | HUB | On Air | Grid-Gen | Green Field | 36 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | GL Yanmar | GL Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 56.7 | 0 | 2 | MTNAirtel | T3209 | ZM6730 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_033M
1289 | T3199 | IHS_CBT_034M | Mushili Baracks | 28.6232 | -13.0561 | Copperbelt | 1.8 | COPPERBELT | NDOLA | No | No | No | Suburban | 2G 3G | P4 | BTS | Hub | On Air | Grid-Gen | Green Field | 48 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | GL Yanmar | GL Yanmar | 15 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 48.7 | 0 | 1 | MTN | T3199 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_034M
555 | T3005 | IHS_CBT_035M | Kaloko | 28.6723 | -13.0483 | Copperbelt | 4.5 | COPPERBELT | NDOLA | Yes | Yes | No | Suburban | 2G 3G 4G | P2 | BB | Hub | On Air | Grid-Gen | Green Field | 60 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Himoinsa | Himoinsa | 30 | Yanmar | 4TNV | HIMOINSA | SK 160 LB | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 600 | 48 | 100 | 6 | LG | LG | 18000 | 18000 | 2 | 160 | 0 | 6 | MTNLiquid( Former Hai)Paratus TelecomGo tvKNCAir-link | T3005 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_035M
863 | T3208 | IHS_CBT_036M | Lubendo | 28.7105 | -12.95 | Copperbelt | 2 | COPPERBELT | NDOLA | Yes | No | No | Rural | #N/A | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | GL Yanmar | GL Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Amaron | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 45 | 0 | 1 | Airtel | T3208 | ZM6590 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_036M
1111 | T3207 | IHS_CBT_037M | Minsundu | 28.6317 | -12.8732 | Copperbelt | 2 | COPPERBELT | NDOLA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 70 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | GL Yanmar | GL Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Power safe | 1200 | 2 | 1200 | 24 | LG | LG | 18000 | 18000 | 2 | 96.6 | 0 | 2 | MTNAirtel | T3207 | ZM3964 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_037M
1027 | T3196 | IHS_CBT_039M | Masaiti/ ChIwala Basic | 28.7396 | -12.9993 | Copperbelt | 2.5 | COPPERBELT | MASAITI | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 48 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 29 | 0 | 1 | MTN | T3196 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_039M
1594 | T3350 | IHS_CBT_040M | Seed Of Hope | 28.7014 | -13.0753 | Copperbelt | 1.8 | COPPERBELT | NDOLA | No | Yes | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Lamasat | Lamasat | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-HA1-C10 | 750 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | n/a | N/A | 47.8 | 0 | 2 | MTNAirtel | T3350 | ZM0431 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_040M
623 | T3200 | IHS_CBT_041M | Kaniki | 28.5415 | -12.8763 | Copperbelt | 2 | COPPERBELT | NDOLA | No | No | No | Rural | 2G 3G | P4 | HUB | HUB | On Air | Grid-Gen | Green Field | 80 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | GL Yanmar | GL Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | C&D True | 1056 | 12 | 176 | 48 | LG | LG | 18000 | 18000 | 2 | 42 | 0 | 1 | MTN | T3200 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_041M
385 | T3360 | IHS_CBT_042M | Golden Lay | 28.4552 | -13.0077 | Copperbelt | 1.8 | COPPERBELT | LUANSHYA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | MPI | MPI | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | C&D True | 1056 | 12 | 176 | 24 | N/A | N/A | N/A | n/a | N/A | 37 | 0 | 2 | MTNGoldenLay | T3360 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_042M
358 | T3031 | IHS_CBT_043M | Fisenge | 28.4632 | -13.0461 | Copperbelt | 2 | COPPERBELT | LUANSHYA | No | No | No | Rural | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 70 | Indoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 36 | 0 | 1 | MTN | T3031 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_043M
509 | T3189 | IHS_CBT_044M | Kafubu Block | 28.5307 | -13.154 | Copperbelt | 2 | COPPERBELT | LUANSHYA | No | No | No | Rural | 2G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 54 | Indoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Yanmar | Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 40 | 0 | 1 | MTN | T3189 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_044M
1744 | T3210 | IHS_CBT_045M | Tuckugan | 28.779 | -13.1146 | Copperbelt | 2 | COPPERBELT | NDOLA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 42 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | GL Yanmar | GL Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Amaron | 600 | 2 | 600 | 24 | samsung | samsung | 18000 | 18000 | 2 | 37 | 0 | 1 | MTN | T3210 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_045M
1017 | T3042 | IHS_CBT_046M | Maposa | 28.4042 | -12.9775 | Copperbelt | 2 | COPPERBELT | NDOLA | No | No | No | Rural | 2G 3G | P4 | BB | HUB | On Air | Grid-Gen | Green Field | 80 | Indoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 61 | 0 | 1 | MTN | T3042 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | Done |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_046M
593 | T3187 | IHS_CBT_047M | Kamirenda | 28.4365 | -13.1271 | Copperbelt | 2 | COPPERBELT | LUANSHYA | No | No | No | Urban | Gold | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 60 | 0 | 1 | MTN | T3187 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_047M
594 | T3238 | IHS_CBT_048M | Kamirenda Extension | 28.4263 | -13.1195 | Copperbelt | 2.5 | COPPERBELT | LUANSHYA | No | No | No | Suburban | Gold | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 40 | Outdoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Vitalgen | Vitalgen | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | 0 | N/A | 59 | 0 | 2 | MTNAirtel | T3238 | ZM6864 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_048M
1093 | T3321 | IHS_CBT_049M | Mikomfwa East | 28.4416 | -13.1503 | Copperbelt | 2 | COPPERBELT | LUANSHYA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 70.5 | 0 | 2 | MTNAirtel | T3321 | ZM6781 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_049M
860 | T3402 | IHS_CBT_050M | Luanshya Town Center | 28.4168 | -13.1286 | Copperbelt | 2.5 | COPPERBELT | LUANSHYA | Yes | No | No | Urban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | n/a | N/A | 67 | 0 | 4 | MTNAirtelINQLiquid Telecom | T3402 | ZM6815 | yes |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | Done |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_050M
854 | T3011 | IHS_CBT_051M | Luanshya | 28.4217 | -13.1352 | Copperbelt | 4.5 | COPPERBELT | LUANSHYA | No | Yes | No | Urban | 2G 3G 4G | P2 | HUB | HUB | On Air | Grid-Gen | Green Field | 50 | Indoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 600 | 48 | 100 | 6 | LG | LG | 18000 | 18000 | 2 | 115 | 0 | 3 | MTNParatus TelecomSmartnet | T3011 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_051M
859 | T3186 | IHS_CBT_052M | Luanshya New Town | 28.4052 | -13.1129 | Copperbelt | 2 | COPPERBELT | LUANSHYA | No | No | No | Suburban | 2G 3G 4G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 56 | 0 | 1 | MTN | T3186 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_052M
1584 | T3052 | IHS_CBT_053M | Sakania | 28.4827 | -12.7538 | Copperbelt | 2 | COPPERBELT | NDOLA | No | No | No | Rural | 2G 3G | P4 | HUB | HUB | On Air | Grid-Gen | Green Field | 70 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | GL Yanmar | GL Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Power safe | 1200 | 2 | 1200 | 24 | LG | LG | 18000 | 18000 | 2 | 32.9 | 0 | 1 | MTN | T3052 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_053M
1094 | T3277 | IHS_CBT_054M | Mikomfwa Market | 28.4282 | -13.1519 | Copperbelt | 2 | COPPERBELT | LUANSHYA | No | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Yanmar | Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 600 | 48 | 100 | 6 | N/A | N/A | N/A | n/a | N/A | 75 | 0 | 2 | MTNAirtel | T3277 | ZM6733 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_054M
207 | T3257 | IHS_CBT_055M | Chinese Colony | 28.4069 | -13.1266 | Copperbelt | 2.5 | COPPERBELT | LUANSHYA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Roof Top | RT | Outdoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | CCS | In House | No DG | No DG | 20 | N/A | N/A | N/A | 0 | N/A | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 45 | 0 | 1 | MTN | T3257 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_055M
1030 | T3043 | IHS_CBT_056M | Masangano | 28.6777 | -13.2439 | Copperbelt | 2 | COPPERBELT | NDOLA | No | Yes | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 70 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | GL Yanmar | GL Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Amaron | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 56 | 0 | 2 | MTNZambia Railways | T3043 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_056M
857 | T3188 | IHS_CBT_057M | Luanshya Industrial Area | 28.4132 | -13.1489 | Copperbelt | 2 | COPPERBELT | LUANSHYA | No | No | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 65 | 0 | 1 | MTN | T3188 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_057M
1091 | T3044 | IHS_CBT_058M | Mikomfwa | 28.4208 | -13.1611 | Copperbelt | 2 | COPPERBELT | LUANSHYA | No | No | No | Suburban | 2G 3G | P2 | BTS | BB | On Air | Grid-Gen | Green Field | 50 | Indoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | GREE | GREE | 18000 | 18000 | 2 | 64 | 0 | 1 | MTN | T3044 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_058M
858 | T3184 | IHS_CBT_059M | Luanshya Mine | 28.396 | -13.1333 | Copperbelt | 2 | COPPERBELT | LUANSHYA | Yes | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 42 | Indoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 70 | 0 | 2 | MTNAirtel | T3184 | ZM0249 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | Done |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_059M
629 | T3038 | IHS_CBT_060M | Kansafu | 28.8335 | -13.1745 | Copperbelt | 2 | COPPERBELT | NDOLA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 50 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Falcon | Falcon | 16 | perkins | 0 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 53 | 0 | 2 | MTNParatus Telecom | T3038 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_060M
1336 | T3093 | IHS_CBT_061M | Mwekera | 28.3583 | -12.8539 | Copperbelt | 2.5 | COPPERBELT | KITWE | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 50 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Wolong | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 45 | 0 | 2 | MTNAirtel | T3093 | ZM6862 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_061M
1565 | T3094 | IHS_CBT_062M | Roan Township | 28.3699 | -13.1322 | Copperbelt | 2.5 | COPPERBELT | LUANSHYA | Yes | Yes | No | Suburban | 2G 3G | P2 | BTS | HUB | On Air | Grid-Gen | Green Field | 48 | Indoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | CK Works | CK Works | 20 | perkins | 4TNE | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 18000 | 18000 | 2 | 79 | 0 | 1 | MTN | T3094 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_062M
23 | T3087 | IHS_CBT_063M | Baluba | 28.3358 | -14.0161 | Copperbelt | 2 | COPPERBELT | LUANSHYA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Indoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Yanmar | Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | C&D True | 1056 | 12 | 176 | 24 | LG | LG | 18000 | 18000 | 2 | 89 | 0 | 1 | MTN | T3087 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_063M
357 | T3320 | IHS_CBT_064M | Finsansa Basic | 28.3594 | -13.1283 | Copperbelt | 2 | COPPERBELT | LUANSHYA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 30 | Outdoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Yanmar | Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | n/a | N/A | 42 | 0 | 2 | MTNAirtel | T3320 | ZM6808 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_064M
1149 | T3247 | IHS_CBT_065M | Mpatamato East | 28.3328 | -13.1071 | Copperbelt | 2 | COPPERBELT | LUANSHYA | No | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Yanmar | Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | GREE | GREE | 18000 | 18000 | 2 | 90 | 0 | 2 | MTNAirtel | T3247 | ZM0248 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_065M
1246 | T3282 | IHS_CBT_066M | Mulyashi | 28.3163 | -13.0622 | Copperbelt | 2 | COPPERBELT | LUANSHYA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Yanmar | Yanmar | 15 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | C&D True | 1056 | 12 | 176 | 24 | N/A | N/A | N/A | n/a | N/A | 49 | 0 | 1 | MTN | T3282 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_066M
1147 | T3014 | IHS_CBT_067M | Mpatamato | 28.3253 | -13.0987 | Copperbelt | 2 | COPPERBELT | LUANSHYA | No | No | No | Suburban | 2G 3G | P3 | BTS | Hub | On Air | Grid-Gen | Green Field | 60 | Indoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 55 | 0 | 1 | MTN | T3014 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_067M
1148 | T3364 | IHS_CBT_068M | Mpatamato Central | 28.3092 | -13.1021 | Copperbelt | 1.8 | COPPERBELT | LUANSHYA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | perkins | perkins | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | n/a | N/A | 51.3 | 0 | 1 | MTN | T3364 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_068M
1150 | T3185 | IHS_CBT_069M | Mpatamato West | 28.31 | -13.1208 | Copperbelt | 2 | COPPERBELT | LUANSHYA | No | No | No | Suburban | 2G 3G | P4 | HUB | BTS | On Air | Grid-Gen | Green Field | 80 | Indoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 65 | 0 | 2 | MTNAirtel | T3185 | ZM6151 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_069M
740 | T3295 | IHS_CBT_070M | Kauanga Basic | 28.7504 | -13.312 | Copperbelt | 2.5 | Central | KAPIRI | No | No | No | Rural | 2G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Earth Technology | Earth technology | 20 | perkins | 0 | Leroy Sommer | 0 | 400 | Delta | DPS 2400B-48-5 | 250 | C&D True | 1056 | 12 | 176 | 24 | N/A | N/A | N/A | n/a | N/A | 56 | 0 | 1 | MTN | T3295 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_070M
1026 | T3212 | IHS_CBT_071M | Masaiti Council | 28.405 | -13.2614 | Copperbelt | 2 | COPPERBELT | MASAITI | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 48 | Indoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | GL Yanmar | GL Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 46 | 0 | 2 | MTNAirtel | T3212 | ZM3761 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_071M
1753 | T3155 | IHS_CBT_072M | Twasekela Basic | 28.4102 | -12.6746 | Copperbelt | 2.5 | COPPERBELT | MUFULIRA | No | No | No | Rural | 2G 3G | P4 | BTS | HUB | On Air | Grid-Gen | Green Field | 48 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Ghadder | Ghadder | 20 | perkins | 0 | Leroy Sommer | 0 | 750 | Power cube | ICC330-HA1-C10 | 0 | Lithium | 200 | 48 | 100 | 2 | LG | LG | 18000 | 18000 | 2 | 35 | 0 | 1 | MTN | T3155 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_072M
68 | T3347 | IHS_CBT_073M | Cedrics Farm | 28.2563 | -12.906 | Copperbelt | 1.8 | COPPERBELT | KITWE | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 40 | Outdoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | perkins | perkins | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 89 | 0 | 2 | MTNAirtel | T3347 | ZM6869 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_073M
843 | T3178 | IHS_CBT_074M | Luangwa | 28.245 | -12.8756 | Copperbelt | 2 | COPPERBELT | KITWE | Yes | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 48 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 75 | 0 | 1 | MTN | T3178 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_074M
1405 | T3245 | IHS_CBT_075M | Ndeke Changachanga | 28.2486 | -12.8582 | Copperbelt | 2.5 | COPPERBELT | KITWE | Yes | Yes | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 20 | Yanmar | 0 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 18000 | 18000 | 2 | 110 | 0 | 1 | MTN | T3245 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_075M
1024 | T3012 | IHS_CBT_076M | Masaiti | 28.419 | -13.3241 | Copperbelt | 2 | COPPERBELT | MASAITI | No | No | No | Rural | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 48 | Indoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | GL Yanmar | GL Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 37 | 0 | 1 | MTN | T3012 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_076M
1152 | T3015 | IHS_CBT_077M | Mpelembe | 28.2512 | -12.818 | Copperbelt | 2 | COPPERBELT | KITWE | Yes | Yes | No | Urban | 2G 3G 4G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 89.1 | 0 | 2 | MTNLiquid Telecom | T3015 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_077M
51 | T3325 | IHS_CBT_078M | Bupe | 28.2351 | -12.8637 | Copperbelt | 2 | COPPERBELT | KITWE | No | No | No | Suburban | 2G 3G | P2 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Wolong | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 153 | 0 | 1 | MTN | T3325 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_078M
1404 | T3121 | IHS_CBT_079M | Ndeke | 28.2385 | -12.8462 | Copperbelt | 2.5 | COPPERBELT | KITWE | Yes | Yes | No | Suburban | 2G 3G 4G | P2 | BTS | BB | On Air | Grid-Gen | Green Field | 54 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 600 | 48 | 100 | 6 | Energy star | Energy star | 18000 | 18000 | 2 | 101 | 0 | 2 | MTNAirtel | T3121 | ZM0254 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_079M
540 | T3169 | IHS_CBT_080M | Kalambo | 28.2486 | -12.8006 | Copperbelt | 2 | COPPERBELT | KITWE | Yes | Yes | No | Suburban | 2G 3G 4G | P1 | BTS | BTS | On Air | Grid-Gen | Green Field | 42 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 78.5 | 0 | 2 | MTNLiquid Telecom | T3169 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_080M
103 | T3028 | IHS_CBT_081M | Chamboli | 28.2256 | -12.8606 | Copperbelt | 2 | COPPERBELT | KITWE | Yes | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Amaron | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 86.5 | 0 | 1 | MTN | T3028 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_081M
1407 | T3235 | IHS_CBT_082M | Ndeke Extension | 28.2323 | -12.8371 | Copperbelt | 2.5 | COPPERBELT | KITWE | Yes | Yes | No | Suburban | 2G 3G 4G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 20 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Amaron | 600 | 2 | 600 | 24 | Energy star | Energy star | 18000 | 18000 | 2 | 153 | 0 | 2 | MTNAirtel | T3235 | ZM6786 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | Pending | 30 |  | Pending |  |  |  |  | IHS_CBT_082M
1458 | T3171 | IHS_CBT_083M | Nkana East | 28.2365 | -12.8217 | Copperbelt | 2 | COPPERBELT | KITWE | Yes | Yes | No | Urban | 2G 3G 4G | P2 | BTS | HUB | On Air | Grid-Gen | Green Field | 36 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 250 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 75 | 0 | 2 | MTNLiquid Telecom | T3171 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_083M
779 | T3092 | IHS_CBT_084M | Kitwe ZNS | 28.2049 | -12.944 | Copperbelt | 1.8 | COPPERBELT | KITWE | No | No | No | Rural | 2G 3G | P4 | HUB | HUB | On Air | Grid-Gen | Green Field | 70 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | CDP | CDP | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | C&D True | 1056 | 12 | 176 | 24 | LG | LG | 18000 | 18000 | 2 | 35 | 0 | 1 | MTN | T3092 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_084M
329 | T3384 | IHS_CBT_085M | Dangote | 28.245 | -12.7913 | Copperbelt | 2.5 | COPPERBELT | NDOLA | No | No | No | Rural | 2G 3G 4G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 54 | Outdoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Earth Technology | Earth technology | 13 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | n/a | N/A | 90 | 0 | 2 | MTNAirtel | T3246 | ZM6634 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_085M
1110 | T3179 | IHS_CBT_086M | Minsenshi-natwange | 28.2234 | -12.8436 | Copperbelt | 2 | COPPERBELT | KITWE | Yes | No | No | Suburban | 2G 3G 4G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Exciss | 460 | 12 | 230 | 8 | LG | LG | 18000 | 18000 | 2 | 65 | 0 | 1 | MTN | T3179 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_086M
892 | T3343 | IHS_CBT_087M | Lulamba School | 28.2468 | -12.7741 | Copperbelt | 2.5 | COPPERBELT | KITWE | No | Yes | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | perkins | perkins | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | n/a | N/A | 76 | 0 | 2 | MTNAirtel | T3343 | ZM6809 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_087M
378 | T3291 | IHS_CBT_088M | Geddis | 28.2215 | -12.8248 | Copperbelt | 1.5 | COPPERBELT | KITWE | Yes | No | No | Urban | 2G 3G 4G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | CDP | CDP | 13 | perkins | 0 | Leroy Sommer | 0 | 500 | Delta | DPS 2400B-48-5 | 250 | Amaron | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 55 | 0 | 1 | MTN | T3291 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_088M
1769 | T3026 | IHS_CBT_089M | Valley View | 28.2355 | -12.7906 | Copperbelt | 4.5 | COPPERBELT | KITWE | Yes | Yes | No | Urban | 2G 3G 4G | P2 | HUB | BB | On Air | Grid-Gen | Green Field | 50 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | ASCOT | ASCOT | 30 | Deutz | 0 | Mecc Alte | 0 | 2000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 700 | 48 | 100 | 7 | LG | LG | 18000 | 18000 | 2 | 110 | 0 | 2 | MTNLiquid Telecom | T3026 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_089M
447 | T3173 | IHS_CBT_090M | Jambo Drive | 28.2295 | -12.8029 | Copperbelt | 2 | COPPERBELT | KITWE | No | Yes | No | Urban | 2G 3G 4G | P2 | BTS | Hub | On Air | Grid-Gen | Green Field | 36 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 80.8 | 0 | 2 | MTNAirtel | T3173 | ZM0256 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_090M
537 | T3004 | IHS_CBT_091M | Kalalangabo | 28.675 | -13.4083 | Copperbelt | 2 | COPPERBELT | MASAITI | No | Yes | No | Rural | 2G 3G | P4 | BTS | HUB | On Air | Grid-Gen | Green Field | 80 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | GL Yanmar | GL Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 67 | 0 | 1 | MTN | T3004 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_091M
1459 | T3234 | IHS_CBT_092M | Nkana Stadium | 28.2122 | -12.8469 | Copperbelt | 2 | COPPERBELT | KITWE | No | No | No | Suburban | 2G 3G 4G | P2 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Amaron | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 75 | 0 | 2 | MTNAirtel | T3234 | ZM6882 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_092M
797 | T3166 | IHS_CBT_093M | Kwacha East | 28.2349 | -12.7787 | Copperbelt | 4.5 | COPPERBELT | KITWE | No | Yes | No | Suburban | 2G 3G 4G | P1 | BTS | BTS | On Air | Grid-Gen | Green Field | 42 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HA1-C10 | 250 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 18000 | 18000 | 2 | 204 | 0 | 2 | MTNAirtel | T3166 | ZM0281 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_093M
776 | T3050 | IHS_CBT_094M | Kitwe Primary | 28.2168 | -12.8137 | Copperbelt | 2 | COPPERBELT | KITWE | Yes | No | No | Urban | 2G 3G 4G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 54 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 18000 | 18000 | 2 | 56 | 0 | 2 | MTNLiquid Telecom | T3050 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_094M
773 | T3010 | IHS_CBT_095M | Kitwe MTSO | 28.2119 | -12.8212 | Copperbelt | 0 | COPPERBELT | KITWE | Yes | Yes | No | Urban | 2G 3G 4G | P1 | HUB | HUB | On Air | Grid-Gen | Green Field | 80 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | In House | In House | No DG | No DG | 0 | N/A | N/A | N/A | 0 | N/A | Delta | DPS 2400B-48-5 | 250 | C&D True | 1056 | 12 | 176 | 24 | LG | LG | 18000 | 18000 | 2 | 76 | 0 | 2 | MTNParatus Telecom | T3010 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_095M
1461 | T3317 | IHS_CBT_096M | Nkana West 9th Street | 28.2093 | -12.8271 | Copperbelt | 2.5 | COPPERBELT | KITWE | Yes | Yes | No | Urban | 2G 3G 4G | P3 | BTS | HUB | On Air | Grid-Gen | Green Field | 36 | Outdoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 20 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 64 | 0 | 2 | MTNLiquid Telecom | T3317 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_096M
45 | T3027 | IHS_CBT_098M | Bulangililo | 28.2282 | -12.7691 | Copperbelt | 2 | COPPERBELT | KITWE | No | Yes | No | Suburban | 2G 3G 4G | P2 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 500 | Delta | DPS 2400B-48-5 | 250 | Power safe | 1200 | 2 | 1200 | 24 | LG | LG | 18000 | 18000 | 2 | 62 | 0 | 1 | MTN | T3027 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_098M
778 | T3326 | IHS_CBT_099M | Kitwe Town Center | 28.2085 | -12.8125 | Copperbelt | 1.8 | COPPERBELT | KITWE | Yes | No | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | CDP | CDP | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Wolong | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 65 | 0 | 1 | MTN | T3326 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_099M
43 | T3025 | IHS_CBT_100M | Buchi | 28.215 | -12.7938 | Copperbelt | 2 | COPPERBELT | KITWE | No | Yes | No | Suburban | 2G 3G | P2 | BTS | BB | On Air | Grid-Gen | Green Field | 48 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 68 | 0 | 2 | MTNAirtel | T3025 | ZM0152 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_100M
265 | T3223 | IHS_CBT_101M | Chisokone | 28.2056 | -12.8166 | Copperbelt | N/A | COPPERBELT | KITWE | No | Yes | No | Urban | 2G 3G 4G | P1 | BTS | BTS | On Air | Grid Only | Roof Top | RT | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | In House | In House | No DG | No DG | N/A | N/A | N/A | N/A | N/A | N/A | Power cube | ICC330-H1-C1 | 400 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 18000 | 18000 | 2 | 82 | 0 | 1 | MTN | T3223 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_101M
1558 | T3181 | IHS_CBT_102M | Richmond | 28.2079 | -12.8062 | Copperbelt | 2 | COPPERBELT | KITWE | Yes | No | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 68 | 0 | 2 | MTNLiquid Telecom | T3181 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_102M
796 | T3167 | IHS_CBT_103M | Kwacha central | 28.2186 | -12.7763 | Copperbelt | 2 | COPPERBELT | KITWE | No | Yes | No | Suburban | 2G 3G | P2 | BTS | BTS | On Air | Grid-Gen | Green Field | 42 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 71 | 0 | 1 | MTN | T3167 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_103M
1755 | T3180 | IHS_CBT_104M | Twibukishe | 28.197 | -12.8186 | Copperbelt | 2 | COPPERBELT | KITWE | Yes | Yes | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 75 | 0 | 1 | MTN | T3180 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_104M
50 | T3035 | IHS_CBT_105M | Buntungwa | 28.1945 | -12.7997 | Copperbelt | 2 | COPPERBELT | KITWE | Yes | Yes | No | Suburban | 2G 3G 4G | P3 | BTS | HUB | On Air | Grid-Gen | Green Field | 40 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 18000 | 18000 | 2 | 92 | 0 | 1 | MTN | T3035 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_105M
394 | T3380 | IHS_CBT_106M | Grizzly Mining | 28.1618 | -13.0438 | Copperbelt | 2.5 | COPPERBELT | KALULUSHI | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Solar-Gen | Green Field | 60 | Outdoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Earth Technology | Earth technology | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-HA1-C10 | 750 | Lithium | 500 | 48 | 100 | 5 | N/A | N/A | N/A | n/a | N/A | 71 | 0 | 2 | MTNAirtel | T3380 | ZM6874 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_106M
1108 | T3342 | IHS_CBT_107M | Mindolo South | 28.1953 | -12.7887 | Copperbelt | 2.5 | COPPERBELT | KITWE | No | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | perkins | perkins | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 500 | 48 | 100 | 5 | N/A | N/A | N/A | n/a | N/A | 72 | 0 | 2 | MTNAirtel | T3342 | ZM6772 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_107M
71 | T3341 | IHS_CBT_108M | Chachacha | 28.1877 | -12.8047 | Copperbelt | 2.5 | COPPERBELT | KITWE | No | Yes | No | Suburban | 2G 3G 4G | P2 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Vital Gen | perkins | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 109 | 0 | 2 | MTNAirtel | T3341 | ZM0270 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | Done | 2019-07-09 | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_108M
204 | T3219 | IHS_CBT_109M | Chimwemwe | 28.2011 | -12.7722 | Copperbelt | 2.5 | COPPERBELT | KITWE | Yes | Yes | No | Suburban | 2G 3G 4G | P1 | BTS | BTS | On Air | Grid-Gen | Roof Top | RT | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | GL (EMK) | GL (EMK) | 20 | perkins | GN65732U | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 18000 | 18000 | 2 | 78 | 0 | 2 | MTNLiquid Telecom | T3219 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_109M
1309 | T3195 | IHS_CBT_110M | Mutundu | 28.349 | -12.5927 | Copperbelt | 2 | COPPERBELT | MUFULIRA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 48 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | coslight | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 65 | 0 | 1 | MTN | T3195 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_110M
206 | T3285 | IHS_CBT_111M | Chimwemwe Nakadoli | 28.1945 | -12.781 | Copperbelt | 1.8 | COPPERBELT | KITWE | No | No | No | Suburban | 2G 3G 4G | P1 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | GNM | GNM | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | coslight | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 65 | 0 | 1 | MTN | T3285 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_111M
601 | T3099 | IHS_CBT_112M | Kamtipa | 28.2041 | -12.7529 | Copperbelt | 2 | COPPERBELT | KITWE | No | No | No | Suburban | 2G 3G | P2 | BTS | BTS | On Air | Grid-Gen | Green Field | 48 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 70 | 0 | 1 | MTN | T3099 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_112M
391 | T3009 | IHS_CBT_113M | Green Belt | 28.1894 | -12.772 | Copperbelt | 2.5 | COPPERBELT | KITWE | No | Yes | No | Suburban | 2G 3G | P3 | HUB | HUB | On Air | Grid-Gen | Green Field | 50 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | IMG | IMG | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 18000 | 18000 | 2 | 115 | 0 | 1 | MTN | T3009 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_113M
586 | T3371 | IHS_CBT_114M | Kamatipa North | 28.1972 | -12.7445 | Copperbelt | 1.8 | COPPERBELT | KITWE | Yes | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | perkins | perkins | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 60 | 0 | 3 | MTNAirtelLiquid Telecom | T3371 | ZM0401 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_114M
1105 | T3168 | IHS_CBT_115M | Mindolo | 28.1764 | -12.7844 | Copperbelt | 2 | COPPERBELT | KITWE | Yes | No | No | Suburban | 2G 3G 4G | P2 | BTS | BTS | On Air | Grid-Gen | Green Field | 40 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 68 | 0 | 1 | MTN | T3168 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_115M
1754 | T3174 | IHS_CBT_116M | Twatacha | 28.1812 | -12.755 | Copperbelt | 2 | COPPERBELT | KITWE | Yes | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 48 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Power safe | 1200 | 2 | 1200 | 24 | LG | LG | 18000 | 18000 | 2 | 65 | 0 | 2 | MTNAirtel | T3174 | ZM6721 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_116M
143 | T3177 | IHS_CBT_117M | Chibote | 28.14 | -12.8652 | Copperbelt | 1.8 | COPPERBELT | KITWE | No | No | No | Suburban | 2G 3G | P4 | BTS | HUB | On Air | Grid-Gen | Green Field | 36 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 15 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 52 | 0 | 2 | MTNAirtel | T3177 | ZM6783 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_117M
585 | T3176 | IHS_CBT_118M | Kamaronde | 28.1421 | -12.8289 | Copperbelt | 2.5 | COPPERBELT | KITWE | Yes | No | No | Suburban | 2G 3G | P4 | BTS | BB/HUB | On Air | Grid-Gen | Green Field | 36 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HA1-C10 | 750 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 18000 | 18000 | 2 | 118 | 0 | 3 | MTNAirtelLiquid Telecom | T3176 | ZM3510 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_118M
897 | T3175 | IHS_CBT_119M | Lumumba | 28.135 | -12.8508 | Copperbelt | 2 | COPPERBELT | KALULUSHI | Yes | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 42 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 45 | 0 | 1 | MTN | T3175 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_119M
377 | T3033 | IHS_CBT_120M | Garneton | 28.1743 | -12.7323 | Copperbelt | 2 | COPPERBELT | KITWE | No | No | No | Suburban | 2G 3G | P3 | BTS | Hub | On Air | Grid-Gen | Green Field | 60 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 48 | 0 | 1 | MTN | T3033 | 0 | Yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_120M
415 | T3344 | IHS_CBT_121M | Ichipe | 28.1603 | -12.7547 | Copperbelt | 1.8 | COPPERBELT | KITWE | No | Yes | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | IHS_CBT_121M | IHS_CBT_121M | 15 | perkins | 0 | Leroy Sommer | 0 | 500 | Delta | DPS 2400B-48-5 | 250 | Wolong | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 64 | 0 | 2 | MTNAirtel | T3344 | ZM6870 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_121M
1737 | T3214 | IHS_CBT_122M | Theka Farms | 28.795 | -13.4725 | Copperbelt | 2 | COPPERBELT | MASAITI | No | No | No | Rural | 2G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | GL Yanmar | GL Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 750 | Delta | DPS 2400B-48-5 | 250 | Power safe | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 75 | 0 | 1 | MTN | T3214 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_122M
1219 | T3345 | IHS_CBT_123M | Mukuba University | 28.1544 | -12.7234 | Copperbelt | 1.8 | COPPERBELT | KITWE | No | No | No | Urban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | IMG | IMG | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | n/a | N/A | 71.3 | 0 | 2 | MTNAirtel | T3345 | ZM6866 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_123M
747 | T3358 | IHS_CBT_124M | Kawama East | 28.2704 | -12.5745 | Copperbelt | 1.8 | COPPERBELT | MUFULIRA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | perkins | perkins | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | n/a | N/A | 85.7 | 0 | 2 | MTNAirtel | T3358 | ZM6787 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_124M
343 | T3328 | IHS_CBT_125M | Eastlea | 28.2787 | -12.5622 | Copperbelt | 1.5 | COPPERBELT | MUFULIRA | No | No | No | Urban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 54 | Outdoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 11 | Yanmar | 3TNE88-G1A | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Amaron | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 69 | 0 | 3 | MTNAirtelCC Systems | T3328 | ZM6819 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_125M
146 | T3088 | IHS_CBT_126M | Chibuluma | 28.0907 | -12.8796 | Copperbelt | 2.5 | COPPERBELT | LUFWANYAMA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 54 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 20 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | C&D True | 1056 | 12 | 176 | 24 | LG | LG | 18000 | 18000 | 2 | 50 | 0 | 1 | MTN | T3088 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_126M
566 | T3006 | IHS_CBT_127M | Kalulushi | 28.0946 | -12.8423 | Copperbelt | 4.5 | COPPERBELT | KALULUSHI | Yes | Yes | No | Urban | 2G 3G 4G | P2 | HUB | HUB | On Air | Grid-Gen | Green Field | 60 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Himoinsa | Himoinsa | 30 | Yanmar | 4TNV | HIMOINSA | SK 160 LB | 1000 | Power cube | ICC330-H1-C1 | 250 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 92.7 | 0 | 2 | MTNLiquid Telecom | T3006 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_127M
603 | T3193 | IHS_CBT_128M | Kamuchanga | 28.2449 | -12.58 | Copperbelt | 2.5 | COPPERBELT | MUFULIRA | No | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Earth Technology | Earth technology | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-HA1-C10 | 250 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 67 | 0 | 2 | MTNAirtel | T3193 | ZM6788 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_128M
345 | T3030 | IHS_CBT_129M | Emerald Mine Lufwanyama | 28.0941 | -13.1149 | Copperbelt | 1.8 | COPPERBELT | LUFWANYAMA | No | No | No | Rural | 2G 3G | P3 | HUB | HUB | On Air | Grid-Gen | Green Field | 80 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 59 | 0 | 1 | MTN | T3030 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_129M
1646 | T3192 | IHS_CBT_130M | Sikalangwe Police | 28.2643 | -12.5606 | Copperbelt | 2 | COPPERBELT | MUFULIRA | No | No | No | Suburban | 2G 3G 4G | P3 | BTS | HUB | On Air | Grid-Gen | Green Field | 42 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | coslight | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 89.8 | 0 | 2 | MTNAirtel | T3192 | ZM0273 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_130M
1740 | T3053 | IHS_CBT_131M | Top Shops | 28.2713 | -12.5544 | Copperbelt | 1.8 | COPPERBELT | MUFULIRA | No | No | No | Urban | 2G 3G 4G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 48 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Lamasat | Lamasat | 15 | perkins | 0 | Leroy Sommer | 0 | 400 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 45.6 | 0 | 1 | MTN | T3053 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_131M
570 | T3224 | IHS_CBT_132M | Kalulushi West | 28.0891 | -12.8526 | Copperbelt | 2.5 | COPPERBELT | KALULUSHI | No | Yes | No | Suburban | 2G 3G | P2 | BTS | BTS | On Air | Grid-Gen | Green Field | 54 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 109.7 | 0 | 2 | MTNLiquid Telecom | T3224 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_132M
147 | T3183 | IHS_CBT_133M | Chibuluma Golf Club | 28.0891 | -12.8309 | Copperbelt | 1.5 | COPPERBELT | KALULUSHI | Yes | No | No | Suburban | 2G 3G 4G | P2 | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Powerol | Powerol | 13 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Amaron | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 65 | 0 | 1 | MTN | T3183 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_133M
568 | T3276 | IHS_CBT_134M | Kalulushi East | 28.082 | -12.85 | Copperbelt | 2.5 | COPPERBELT | KALULUSHI | Yes | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-HA1-C10 | 750 | Lithium | 500 | 48 | 100 | 5 | N/A | N/A | N/A | n/a | N/A | 50 | 0 | 3 | MTNAirtelLiquid Telecom | T3276 | ZM6775 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_134M
1199 | T3242 | IHS_CBT_135M | Mufulira Central | 28.2615 | -12.55 | Copperbelt | 2 | COPPERBELT | MUFULIRA | Yes | No | No | Urban | 2G 3G | P4 | HUB | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Yanmar | Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 91.5 | 0 | 4 | MTNAirtelLiquid( Former Hai)Liquid Telecom | T3242 | ZM6762 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_135M
1363 | T3359 | IHS_CBT_136M | Nalikwanda Street | 28.2479 | -12.5619 | Copperbelt | 1.8 | COPPERBELT | MUFULIRA | No | Yes | No | Suburban | 2G 3G | P3 | BTS | BB | On Air | Grid-Gen | Green Field | 36 | Outdoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | IMG | IMG | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 75.2 | 0 | 1 | MTN | T3359 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_136M
1463 | T3213 | IHS_CBT_137M | Nkanga Hills | 28.2618 | -13.4069 | Copperbelt | 2 | COPPERBELT | MASAITI | No | No | No | Rural | 2G 3G | P4 | BTS | BB | On Air | Grid-Gen | Green Field | 36 | Indoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | GL Yanmar | GL Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 29 | 0 | 1 | MTN | T3213 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_137M
720 | T3039 | IHS_CBT_138M | Kasunswa | 28.2048 | -12.6001 | Copperbelt | 2.5 | COPPERBELT | MUFULIRA | No | Yes | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 40 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Mecc Alte | 0 | 600 | Power cube | ICC330-H1-C10 | 750 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 55 | 0 | 2 | MTNAirtel | T3039 | ZM6584 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_138M
1197 | T3019 | IHS_CBT_140M | Mufulira | 28.2496 | -12.5503 | Copperbelt | 4.5 | COPPERBELT | MUFULIRA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | HUB | BB | On Air | Grid-Gen | Green Field | 70 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Himoinsa | Himoinsa | 30 | HIMOISA | 4TNV | HIMOINSA | SK 160 LB | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 18000 | 18000 | 2 | 165 | 0 | 2 | MTNLiquid Telecom | T3019 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_140M
605 | T3357 | IHS_CBT_141M | Kamuchanga North | 28.2281 | -12.5669 | Copperbelt | 1.8 | COPPERBELT | MUFULIRA | No | Yes | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 50 | 0 | 1 | MTN | T3357 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_141M
1581 | T3051 | IHS_CBT_142M | Sabina | 28.1182 | -12.712 | Copperbelt | 2 | COPPERBELT | KITWE | No | Yes | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Yanmar | Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Wolong | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 48.6 | 0 | 1 | MTN | T3051 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_142M
633 | T3190 | IHS_CBT_143M | Kantashi | 28.2367 | -12.5541 | Copperbelt | 2 | COPPERBELT | MUFULIRA | No | No | No | Suburban | 2G 3G 4G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | coslight | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 56.4 | 0 | 1 | MTN | T3190 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_143M
1141 | T3225 | IHS_CBT_144M | Mopani | 28.2484 | -12.5416 | Copperbelt | 2 | COPPERBELT | MUFULIRA | No | No | No | Suburban | 2G 3G 4G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 42 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Yanmar | Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 56.7 | 0 | 1 | MTN | T3225 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_144M
1104 | T3194 | IHS_CBT_145M | Minambe | 28.2875 | -12.5064 | Copperbelt | 2 | COPPERBELT | MUFULIRA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 42 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Amaron | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 54.6 | 0 | 2 | MTNAirtel | T3194 | ZM6152 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_145M
1095 | T3383 | IHS_CBT_146M | Miku Mining | 28.0529 | -13.0719 | Copperbelt | 2.5 | COPPERBELT | LUFWANYAMA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | Wolong | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 44 | 0 | 1 | MTN | T3383 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_146M
1281 | T3356 | IHS_CBT_147M | Murundu | 28.3132 | -12.4847 | Copperbelt | 1.8 | COPPERBELT | MUFULIRA | No | No | No | Suburban | 2G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | C&D True | 1056 | 12 | 176 | 24 | N/A | N/A | N/A | n/a | N/A | 60.2 | 0 | 2 | MTNAirtel | T3356 | ZM6871 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_147M
557 | T3296 | IHS_CBT_148M | Kaloko Trust | 28.5252 | -13.5521 | Copperbelt | 2 | COPPERBELT | MPONGWE | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 56 | Outdoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Yanmar | Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Wolong | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 32 | 0 | 1 | MTN | T3296 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_148M
1628 | T3243 | IHS_CBT_149M | Shinde Stadium | 28.2325 | -12.5436 | Copperbelt | 2 | COPPERBELT | MUFULIRA | No | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | coslight | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 53.5 | 0 | 1 | MTN | T3243 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_149M
101 | T3336 | IHS_CBT_150M | Chambishi Economic Zone | 28.1192 | -12.6785 | Copperbelt | 2.5 | COPPERBELT | KALULUSHI | No | Yes | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | IMG | IMG | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | n/a | N/A | 50 | 0 | 2 | MTNAir-link | T3336 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_150M
354 | T3362 | IHS_CBT_151M | Fifteen NMCC Chambishi | 28.1383 | -12.6457 | Copperbelt | 2.5 | COPPERBELT | KALULUSHI | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Vitalgen | Vitalgen | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | n/a | N/A | 56.5 | 0 | 2 | MTNAirtel | T3362 | ZM0421 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_151M
1201 | T3048 | IHS_CBT_152M | Mufulira West | 28.2273 | -12.5331 | Copperbelt | 2 | COPPERBELT | MUFULIRA | No | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 40 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 400 | Delta | DPS 2400B-48-5 | 250 | coslight | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 48.3 | 0 | 1 | MTN | T3048 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_152M
1124 | T3085 | IHS_CBT_153M | Mokambo | 28.3391 | -12.4418 | Copperbelt | 2 | COPPERBELT | MUFULIRA | No | No | No | Rural | 2G 3G | P4 | BTS | BB | On Air | Grid-Gen | Green Field | 60 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 56.5 | 0 | 2 | MTNAirtel | T3085 | ZM0259 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_153M
319 | T3157 | IHS_CBT_154M | Copper smelter | 28.1036 | -12.6542 | Copperbelt | 2.5 | COPPERBELT | KITWE | Yes | Yes | No | Suburban | 2G 3G 4G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 48 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | IMG | IMG | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 69.5 | 0 | 1 | MTN | T3157 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_154M
1704 | T3091 | IHS_CBT_155M | St. Joseph | 28.0125 | -12.8925 | Copperbelt | 2 | COPPERBELT | LUFWANYAMA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 54 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Power safe | 1200 | 2 | 1200 | 24 | LG | LG | 18000 | 18000 | 2 | 42 | 0 | 1 | MTN | T3091 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_155M
1170 | T3047 | IHS_CBT_156M | Mpongwe Turnoff | 28.6227 | -13.5992 | Copperbelt | 4.5 | COPPERBELT | NDOLA | No | Yes | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 70 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Himoinsa | Himoinsa | 30 | Yanmar | 4TNV | HIMOINSA | SK 160 LB | 1000 | Delta | DPS 2400B-48-5 | 250 | Power safe | 1200 | 2 | 1200 | 24 | LG | LG | 18000 | 18000 | 2 | 29 | 0 | 2 | MTNAirtel | T3047 | ZM3582 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_156M
55 | T3191 | IHS_CBT_157M | Butondo | 28.1896 | -12.5106 | Copperbelt | 2 | COPPERBELT | MUFULIRA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | coslight | 600 | 2 | 600 | 24 | Energy star | Energy star | 18000 | 18000 | 2 | 45 | 0 | 1 | MTN | T3191 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_157M
99 | T3156 | IHS_CBT_158M | Chambeshi Stadium | 28.0636 | -12.6369 | Copperbelt | 2 | COPPERBELT | KALULUSHI | No | No | No | Suburban | 2G 3G | P2 | BTS | BTS | On Air | Grid-Gen | Green Field | 48 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Yanmar | Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Amaron | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 43.8 | 0 | 1 | MTN | T3156 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_158M
129 | T3182 | IHS_CBT_159M | Chembe South | 27.9807 | -12.8369 | Copperbelt | 2.5 | COPPERBELT | KALULUSHI | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 48 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 20 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 53 | 0 | 1 | MTN | T3182 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_159M
96 | T3000 | IHS_CBT_160M | Chambeshi | 28.0491 | -12.6536 | Copperbelt | 2 | COPPERBELT | KALULUSHI | No | No | No | Suburban | 2G 3G | P3 | BTS | BB | On Air | Grid-Gen | Green Field | 50 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Yanmar | Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 98.3 | 0 | 2 | MTNAirtel | T3000 | ZM0006 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_160M
1090 | T3304 | IHS_CBT_161M | Mikata Mpongwe | 28.384 | -13.614 | Copperbelt | 2.5 | COPPERBELT | MPONGWE | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Solar-Gen | Green Field | 60 | Outdoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | IMG | IMG | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-HA1-C10 | 750 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 87 | 0 | 2 | MTNAirtel | T3304 | ZM0955 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_161M
1171 | T3046 | IHS_CBT_162M | Mpongweboma | 28.1614 | -13.5105 | Copperbelt | 2 | COPPERBELT | MPONGWE | No | No | No | Suburban | 2G 3G | P2 | BTS | BB | On Air | Grid-Gen | Green Field | 70 | Indoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Yanmar | Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 58 | 0 | 2 | MTNINQ | T3046 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_162M
1743 | T3279 | IHS_CBT_163M | Tripple Farm | 28.0783 | -12.5149 | Copperbelt | 2 | COPPERBELT | KALULUSHI | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 48 | Outdoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Yanmar | Yanmar | 15 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 40 | 0 | 1 | MTN | T3279 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_163M
705 | T3057 | IHS_CBT_164M | Kashitu | 28.6294 | -13.7001 | Copperbelt | 2 | COPPERBELT | NDOLA | No | Yes | No | Rural | 2G | P4 | HUB | BTS | On Air | Grid-Gen | Green Field | 80 | Indoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Falcon | Falcon | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 56 | 0 | 1 | MTN | T3057 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | Done |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_164M
1112 | T3045 | IHS_CBT_165M | Misenga | 27.9551 | -12.5941 | Copperbelt | 1.8 | COPPERBELT | CHINGOLA | No | Yes | No | Rural | 2G 3G | P3 | HUB | BB | On Air | Grid-Gen | Green Field | 70 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | ELCOS | ELCOS | 15 | perkins | 0 | Leroy Sommer | 0 | 400 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 44.8 | 0 | 1 | MTN | T3045 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_165M
598 | T3298 | IHS_CBT_166M | Kampoya | 28.6451 | -13.7706 | Copperbelt | 1.8 | Central | KAPIRI | No | Yes | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Lamasat | Lamasat | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | C&D True | 1056 | 12 | 176 | 24 | N/A | N/A | N/A | n/a | N/A | 26 | 0 | 1 | MTN | T3298 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_166M
508 | T3037 | IHS_CBT_167M | Kafubu | 27.8316 | -12.8432 | Copperbelt | 2 | COPPERBELT | KALULUSHI | No | No | No | Urban | 2G 3G | P4 | BTS | HUB | On Air | Grid-Gen | Green Field | 60 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | LISTER PETTER | LISTER PETTER | 16 | Lister petter | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 40.1 | 0 | 1 | MTN | T3037 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_167M
1168 | T3017 | IHS_CBT_168M | Mpongwe | 28.0672 | -13.5734 | Copperbelt | 2 | COPPERBELT | MPONGWE | No | No | No | Rural | 2G 3G | P4 | HUB | BB | On Air | Grid-Gen | Green Field | 80 | Indoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | GL Yanmar | GL Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Power safe | 1200 | 2 | 1200 | 24 | GREE | GREE | 18000 | 18000 | 2 | 45.3 | 0 | 3 | MTNAirtelLiquid Telecom | T3017 | ZM0062 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_168M
708 | T3162 | IHS_CBT_169M | Kasompe | 27.8924 | -12.5884 | Copperbelt | 2 | COPPERBELT | CHINGOLA | Yes | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 54 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 45 | 0 | 1 | MTN | T3162 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_169M
355 | T3126 | IHS_CBT_170M | Filando | 27.8038 | -12.8488 | Copperbelt | 1.5 | COPPERBELT | KALULUSHI | No | No | No | Rural | 2G 3G | P4 | BTS | BB | On Air | Grid-Gen | Green Field | 66 | Indoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 13 | Yanmar | 3TNE88-G1A | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 35 | 0 | 1 | MTN | T3126 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_170M
1790 | T3258 | IHS_CBT_171M | Zalawi | 27.8969 | -12.5708 | Copperbelt | 2.5 | COPPERBELT | CHINGOLA | No | Yes | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | IMG | IMG | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 76.7 | 0 | 2 | MTNAirtel | T3258 | ZM6840 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_171M
1700 | T3370 | IHS_CBT_172M | ST. Anthony | 27.9332 | -13.4569 | Copperbelt | 2.5 | COPPERBELT | MPONGWE | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Wolong | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 41.7 | 0 | 1 | MTN | T3370 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_172M
53 | T3160 | IHS_CBT_173M | Bupililo | 27.9011 | -12.5427 | Copperbelt | 1.8 | COPPERBELT | CHINGOLA | Yes | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 42 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 400 | Delta | DPS 2400B-48-5 | 250 | coslight | 600 | 2 | 600 | 24 | GREE | GREE | 18000 | 18000 | 2 | 84.1 | 0 | 2 | MTNAirtel | T3160 | ZM6852 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_173M
1560 | T3330 | IHS_CBT_174M | River Side Extension | 27.8939 | -12.5479 | Copperbelt | 1.8 | COPPERBELT | CHINGOLA | Yes | Yes | No | Urban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | IMG | IMG | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | n/a | N/A | 75.8 | 0 | 3 | MTNAirtelLiquid Telecom | T3330 | ZM6791 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_174M
668 | T3164 | IHS_CBT_175M | Kapisha | 27.9045 | -12.5261 | Copperbelt | 2 | COPPERBELT | CHINGOLA | Yes | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 42 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | coslight | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 77.8 | 0 | 2 | MTNAirtel | T3164 | ZM6792 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_175M
669 | T3329 | IHS_CBT_176M | Kapisha Central | 27.8976 | -12.5331 | Copperbelt | 1.8 | COPPERBELT | CHINGOLA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 75 | 0 | 2 | MTNAirtel | T3329 | ZM0284 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_176M
947 | T3165 | IHS_CBT_177M | Magoye court | 27.8867 | -12.5401 | Copperbelt | 2 | COPPERBELT | CHINGOLA | No | No | No | Urban | 2G 3G 4G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 42 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | coslight | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 65 | 0 | 1 | MTN | T3165 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_177M
484 | T3036 | IHS_CBT_178M | Kabundi | 27.8898 | -12.5279 | Copperbelt | 2.5 | COPPERBELT | CHINGOLA | No | Yes | No | Suburban | 2G 3G 4G | P3 | BTS | HUB | On Air | Grid-Gen | Green Field | 40 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | coslight | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 72 | 0 | 1 | MTN | T3036 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_178M
347 | T3289 | IHS_CBT_179M | ETC Bio Energy Farm | 27.9544 | -13.5206 | Copperbelt | 1.8 | COPPERBELT | MPONGWE | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 56 | Outdoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | C&D True | 1056 | 12 | 176 | 24 | N/A | N/A | N/A | n/a | N/A | 22 | 0 | 1 | MTN | T3289 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_179M
658 | T3163 | IHS_CBT_180M | Kapale | 27.8674 | -12.5541 | Copperbelt | 2.5 | COPPERBELT | CHINGOLA | No | No | No | Suburban | 2G 3G | P3 | BTS | HUB | On Air | Grid-Gen | Green Field | 42 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Earth Technology | Earth technology | 20 | perkins | 0 | Leroy Sommer | 0 | 400 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 43 | 0 | 1 | MTN | T3163 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_180M
882 | T3372 | IHS_CBT_181M | Lukanga resettlement | 28.1864 | -13.7259 | Copperbelt | 2.5 | COPPERBELT | MPONGWE | No | No | No | Rural | 2G | P4 | BTS | BTS | On Air | Solar-Gen | Green Field | 60 | Outdoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | EPW30-48A | 300 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 23 | 0 | 1 | MTN | T3372 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_181M
487 | T3256 | IHS_CBT_182M | Kabundi Park | 27.8851 | -12.5221 | Copperbelt | 2 | COPPERBELT | CHINGOLA | No | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 0 | 0 | 0 | 600 | Power cube | ICC330-HA1-C10 | 750 | coslight | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 65 | 0 | 2 | MTNAirtel | T3256 | ZM0288 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_182M
485 | T3241 | IHS_CBT_183M | Kabundi Central | 27.8776 | -12.5324 | Copperbelt | 1.8 | COPPERBELT | CHINGOLA | Yes | Yes | No | Suburban | 2G 3G | P4 | BTS | BB | On Air | Grid-Gen | Green Field | 40 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | Yanmar | 0 | Leroy Sommer | 0 | 400 | Power cube | ICC330-HA1-C10 | 750 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 104 | 0 | 2 | MTNLiquid Telecom | T3241 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_183M
890 | T3041 | IHS_CBT_184M | Lulamba | 27.8509 | -12.5732 | Copperbelt | 2 | COPPERBELT | CHINGOLA | No | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 54 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1A-C10 | 750 | coslight | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 48 | 0 | 1 | MTN | T3041 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_184M
210 | T3002 | IHS_CBT_185M | Chingola | 27.865 | -12.5414 | Copperbelt | 4.5 | COPPERBELT | CHINGOLA | Yes | Yes | No | Urban | 2G 3G 4G | P1 | HUB | Hub | On Air | Grid-Gen | Green Field | 70 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | CK Works | CK Works | 30 | perkins | DJ83400S | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 235 | 0 | 5 | MTNLiquid( Former Hai)Liquid TelecomParatus TelecomSmartnet | T3002 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_185M
1398 | T3049 | IHS_CBT_186M | Nchanga North | 27.8752 | -12.5191 | Copperbelt | 2 | COPPERBELT | CHINGOLA | No | No | No | Urban | 2G 3G 4G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 48 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | Amaron | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 48 | 0 | 1 | MTN | T3049 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_186M
891 | T3260 | IHS_CBT_187M | Lulamba North | 27.8439 | -12.5657 | Copperbelt | 2 | COPPERBELT | CHINGOLA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | coslight | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 58.9 | 0 | 1 | MTN | T3260 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_187M
1397 | T3161 | IHS_CBT_188M | Nchanga Mine | 27.8593 | -12.5331 | Copperbelt | 1.8 | COPPERBELT | CHINGOLA | No | No | No | Suburban | 2G 3G 4G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 42 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | Yanmar | 0 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | C&D True | 1056 | 12 | 176 | 24 | LG | LG | 18000 | 18000 | 2 | 42.6 | 0 | 1 | MTN | T3161 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_188M
284 | T3086 | IHS_CBT_189M | Chiwempala | 27.8422 | -12.5561 | Copperbelt | 2 | COPPERBELT | CHINGOLA | Yes | No | No | Suburban | 2G 3G 4G | P1 | BTS | HUB | On Air | Grid-Gen | Green Field | 54 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | IMG | IMG | 20 | perkins | 0 | Leroy Sommer | 0 | 400 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 75.6 | 0 | 1 | MTN | T3086 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | Done |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_189M
15 | T3240 | IHS_CBT_190M | Atheneon | 27.8446 | -14.3426 | Copperbelt | 2 | COPPERBELT | CHINGOLA | Yes | Yes | No | Urban | 2G 3G | P2 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | IMG | IMG | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | coslight | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 68.1 | 0 | 1 | MTN | T3240 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_190M
286 | T3331 | IHS_CBT_191M | Chiwempala Stadium | 27.8332 | -12.5602 | Copperbelt | 2 | COPPERBELT | CHINGOLA | No | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Yanmar | Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 46.8 | 0 | 1 | MTN | T3331 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_191M
94 | T3127 | IHS_CBT_193M | Chambatata | 27.9367 | -13.619 | Copperbelt | 2 | COPPERBELT | MPONGWE | No | No | No | Rural | 2G | P4 | BTS | BB | On Air | Grid-Gen | Green Field | 66 | Indoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Yanmar | Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 88 | 0 | 1 | MTN | T3127 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_193M
534 | T3244 | IHS_CBT_194M | Kakoso | 27.8559 | -12.3685 | Copperbelt | 1.8 | COPPERBELT | CHILILABOMBWE | No | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | Yanmar | 0 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 92.8 | 0 | 2 | MTNAirtel | T3244 | ZM6635 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_194M
188 | T3159 | IHS_CBT_195M | Chililabombwe | 27.8402 | -12.3816 | Copperbelt | 2.5 | COPPERBELT | CHILILABOMBWE | No | No | No | Urban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 42 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | coslight | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 90.5 | 0 | 2 | MTNINQ | T3159 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_CBT_195M
1437 | T3090 | IHS_CBT_196M | New Lands | 27.7225 | -12.5756 | Copperbelt | 2 | COPPERBELT | CHINGOLA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 66 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Mecc Alte | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Wolong | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 58.3 | 0 | 2 | MTNAirtel | T3090 | ZM3583 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_196M
187 | T3001 | IHS_CBT_197M | Chililabombwe | 27.845 | -12.3678 | Copperbelt | 2 | COPPERBELT | CHILILABOMBWE | Yes | Yes | No | Urban | 2G 3G 4G | P1 | HUB | BB | On Air | Grid-Gen | Green Field | 40 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Mecc Alte | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 118 | 0 | 3 | MTNParatus TelecomSmartnet | T3001 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_197M
589 | T3333 | IHS_CBT_198M | Kameza 2 | 27.8355 | -12.3747 | Copperbelt | 2.5 | COPPERBELT | CHILILABOMBWE | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Earth Technology | Earth technology | 20 | perkins | 0 | Leroy Sommer | 0 | 400 | Delta | DPS 2400B-48-5 | 250 | coslight | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 40.6 | 0 | 1 | MTN | T3333 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_198M
193 | T3332 | IHS_CBT_199M | Chililabomwe Central | 27.8386 | -12.3592 | Copperbelt | 1.8 | COPPERBELT | CHILILABOMBWE | No | No | No | Urban | 2G 3G | P3 | HUB | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | perkins | perkins | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | C&D True | 1056 | 12 | 176 | 24 | N/A | N/A | N/A | n/a | N/A | 55.9 | 0 | 2 | MTNAirtel | T3332 | ZM0516 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_199M
864 | T3275 | IHS_CBT_200M | Lubengele B. School | 27.8321 | -12.3616 | Copperbelt | 1.8 | COPPERBELT | CHILILABOMBWE | No | No | No | Suburban | 2G 3G | P2 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | Yanmar | 0 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 86.4 | 0 | 2 | MTNAirtel | T3275 | ZM6842 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_200M
24 | ZM0004 | IHS_CBT_201A | BALUBA | 28.4437 | -15.6704 | Copperbelt | 1.5 | COPPERBELT | Luanshya | No | No | No | Suburban | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 52 | Indoor | Neddy Chiwasa | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Earth Technology | Earth technology | 13 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 46.2 | 0 | 1 | Airtel | 0 | ZM0004 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_201A
783 | T3105 | IHS_CBT_202M | Konkola | 27.822 | -12.3703 | Copperbelt | 2 | COPPERBELT | CHILILABOMBWE | No | No | No | Suburban | 2G 3G 4G | P2 | BTS | BTS | On Air | Grid-Gen | Green Field | 48 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | C&D True | 1056 | 12 | 176 | 24 | LG | LG | 18000 | 18000 | 2 | 65.2 | 0 | 2 | MTNAirtel | T3105 | ZM0395 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_202M
189 | ZM0011 | IHS_CBT_203A | CHILILABOMBWE | 27.8432 | -12.3713 | Copperbelt | 2.5 | COPPERBELT | Chililabombwe | Yes | No | No | Urban | Silver | Silver |  | BB/HUB | On Air | Grid-Gen | Green Field | 60 | Indoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 4 | 117 | 0 | 1 | Airtel | 0 | ZM0011 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_203A
876 | T3107 | IHS_CBT_203M | Lufwanyama | 27.6259 | -12.8554 | Copperbelt | 1.5 | COPPERBELT | LUFWANYAMA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 13 | Yanmar | 3TNE88-G1A | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | C&D True | 1056 | 12 | 176 | 24 | N/A | N/A | N/A | n/a | N/A | 33.7 | 0 | 1 | MTN | T3107 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_203M
211 | ZM0012 | IHS_CBT_204A | CHINGOLA | 27.8611 | -12.5493 | Copperbelt | 5.5 | COPPERBELT | Chingola | No | No | Yes | Urban | Silver | Silver |  | BB/HUB | On Air | Grid-Gen | Green Field | 50 | Indoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | CK Works | CK Works | 45 | perkins | 0 | Leroy Sommer | 0 | 1000 | Emerson | 701 IG4 | 300 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 215 | 0 | 2 | AirtelINQ | 0 | ZM0012 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_204A
191 | T3367 | IHS_CBT_204M | Chililabombwe North | 27.8332 | -12.3507 | Copperbelt | 4.5 | COPPERBELT | CHILILABOMBWE | No | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | C&D True | 1056 | 12 | 176 | 24 | N/A | N/A | N/A | n/a | N/A | 76.6 | 0 | 2 | MTNAirtel | T3367 | ZM0289 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_204M
344 | ZM0018 | IHS_CBT_205A | EASTLEA | 28.2723 | -12.5559 | Copperbelt | 1.8 | COPPERBELT | Mufulira | No | No | No | Urban | Silver | Silver |  | BTS | On Air | Grid-Gen | Green Field | 50 | Indoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Emerson | 701 IG4 | 300 | coslight | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 42.2 | 0 | 1 | Airtel | 0 | ZM0018 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_205A
190 | T3158 | IHS_CBT_205M | Chililabombwe Mapelo Road | 27.8251 | -12.359 | Copperbelt | 2 | COPPERBELT | CHILILABOMBWE | No | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 42 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | C&D True | 1056 | 12 | 176 | 24 | LG | LG | 18000 | 18000 | 2 | 57.2 | 0 | 1 | MTN | T3158 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_205M
567 | ZM0030 | IHS_CBT_206A | KALULUSHI | 28.0874 | -12.8356 | Copperbelt | 1.8 | COPPERBELT | Kitwe | No | No | No | Urban | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 42 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | IMG | IMG | 15 | perkins | 0 | Leroy Sommer | 0 | 200 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 48 | 0 | 1 | Airtel | 0 | ZM0030 | yes |  | 0 | Mesh | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_206A
433 | T1041 | IHS_CBT_206M | Ipafu | 27.6905 | -12.5256 | Copperbelt | 2.5 | COPPERBELT | CHINGOLA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 42 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Earth Technology | Earth technology | 20 | perkins | GU 51798V | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 57.8 | 58 | 2 | MTNAirtel | T1041 | ZM6591 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_206M
625 | ZM0032 | IHS_CBT_207A | KANINI | 28.6287 | -12.9777 | Copperbelt | 2 | COPPERBELT | Ndola | Yes | No | Yes | Urban | Gold | Gold | HUB | HUB | On Air | Grid-Gen | Green Field | 45 | Indoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 64 | 0 | 1 | Airtel | 0 | ZM0032 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_207A
785 | T3365 | IHS_CBT_207M | Konocco | 27.7842 | -12.3046 | Copperbelt | 2 | COPPERBELT | CHILILABOMBWE | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 70 | Outdoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Yanmar | Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 41.2 | 0 | 1 | MTN | T3365 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | Done |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_207M
626 | ZM0033 | IHS_CBT_208A | KANKOYO | 28.2198 | -12.5314 | Copperbelt | 1.8 | COPPERBELT | Mufulira | No | No | No | Suburban | Silver | Silver |  | BTS | On Air | Grid-Gen | Green Field | 24 | Indoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | GNM | GNM | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 75.3 | 0 | 2 | MTNAirtel | T3268 | ZM0033 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_208A
718 | T3089 | IHS_CBT_208M | Kasumbalesa | 27.7949 | -12.2681 | Copperbelt | 5.5 | COPPERBELT | CHILILABOMBWE | Yes | No | No | Suburban | 2G 3G 4G | P1 | BTS | BTS | On Air | Grid-Gen | Green Field | 54 | Outdoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Vitalgen | Vitalgen | 40 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 900 | 48 | 100 | 9 | N/A | N/A | N/A | n/a | N/A | 220 | 210 | 7 | MTNAirtelLiquid TelecomParatus TelecomSmartnetJenny Internet Services | T3089 | ZM0037 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_208M
724 | ZM0039 | IHS_CBT_209A | Katanino | 28.5849 | -13.6477 | Copperbelt | 4.5 | COPPERBELT | MPongwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 30 | Indoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | ASCOT | ASCOT | 30 | Deutz | 0 | Mecc Alte | 0 | 2000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 59.968 | 0 | 1 | Airtel | 0 | ZM0039 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_209A
855 | ZM0050 | IHS_CBT_210A | LUANSHYA | 28.4201 | -13.1351 | Copperbelt | 2.5 | COPPERBELT | Luanshya | No | No | No | Urban | Silver | Silver | BB | BB | On Air | Grid-Gen | Green Field | 64 | Outdoor | Neddy Chiwasa | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | CK Works | CK Works | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 500 | 48 | 100 | 5 | N/A | N/A | N/A | 18000 | N/A | 82.142 | 0 | 1 | Airtel | 0 | ZM0050 | 0 |  | 0 | Mesh | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_210A
1221 | T3114 | IHS_CBT_210M | Mukumpu | 27.7504 | -13.674 | Copperbelt | 2 | COPPERBELT | MPONGWE | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 66 | Outdoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Yanmar | Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | C&D True | 1056 | 12 | 176 | 24 | N/A | N/A | N/A | n/a | N/A | 22 | 0 | 2 | MTNParatus Telecom | T3114 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_210M
1151 | ZM0061 | IHS_CBT_211A | MPATAMATU | 28.3212 | -13.0999 | Copperbelt | 2.5 | COPPERBELT | Luanshya | No | No | No | Suburban | Silver | Silver | BB | BTS | On Air | Grid-Gen | Green Field | 45 | Indoor | Neddy Chiwasa | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | IMG | IMG | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 47.917 | 0 | 1 | Airtel | 0 | ZM0061 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_211A
757 | T3103 | IHS_CBT_212M | Kayolelwa | 27.4895 | -12.4748 | Copperbelt | 2.5 | COPPERBELT | CHINGOLA | No | Yes | No | Rural | 2G 3G | P4 | BB | BB | On Air | Grid-Gen | Green Field | 66 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 62.4 | 0 | 2 | MTNAirtel | T3103 | ZM4009 | yes |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | Done |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_212M
1198 | ZM0063 | IHS_CBT_213A | MUFULIRA | 28.2493 | -12.5509 | Copperbelt | 4.5 | COPPERBELT | Mufulira | No | No | No | Urban | Silver | Silver |  | HUB | On Air | Grid-Gen | Green Field | 50 | Indoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 4 | 97.734 | 0 | 2 | AirtelINQ | 0 | ZM0063 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_213A
1707 | T3294 | IHS_CBT_213M | St. Marys Mission | 27.3717 | -12.8975 | Copperbelt | 1.5 | COPPERBELT | LUFWANYAMA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Pramac | Pramac | 10 | Yanmar | 3TNE88-G1A | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Amaron | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 45 | 0 | 1 | MTN | T3294 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_213M
1414 | ZM0066 | IHS_CBT_214A | NDOLA FRA SILOS | 28.6657 | -13.0223 | Copperbelt | 2.5 | COPPERBELT | Ndola | No | No | Yes | Urban | Gold | Gold | BTS | BB/HUB | On Air | Grid-Gen | Roof Top | RT | Indoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Lamasat | Lamasat | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Emerson | 701 IG4 | 300 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 69 | 0 | 1 | Airtel | 0 | ZM0066 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_214A
622 | T3100 | IHS_CBT_214M | Kangwena | 27.3142 | -12.3772 | Copperbelt | 2.5 | NORTH WESTERN | SOLWEZI | No | Yes | No | Rural | 2G | P4 | BB | BB | On Air | Grid-Gen | Green Field | 66 | Indoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 4TNE | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 58.4 | 0 | 2 | MTNAirtel | T3100 | ZM6597 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_214M
1538 | T3386 | IHS_CBT_215M | PHILIP FARM | 28.3518 | -13.697 | Copperbelt | 1.8 | COPPERBELT | MPONGWE | No | No | No | Rural | 2G | P4 | BTS | BTS | On Air | Solar-Gen | Green Field | 54 | Outdoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | perkins | perkins | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | EPW30-48A | 150 | Amaron | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 23 | 0 | 1 | MTN | T3386 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_215M
317 | T3388 | IHS_CBT_216M | COOL BANANAS | 28.5505 | -13.0704 | Copperbelt | 2 | COPPERBELT | NDOLA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 54 | Outdoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Generator City | Generator City | 13 | Yanmar | 3TNE88-G1A | ALPHAGEN | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 173.5 | 0 | 1 | MTN | T3388 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_216M
1018 | ZM0097 | IHS_CBT_217A | MAPOSA | 28.3692 | -12.9377 | Copperbelt | 4.5 | COPPERBELT | Luanshya | No | No | Yes | Rural | Silver | Silver | BB | BB | On Air | Grid-Gen | Green Field | 52 | Indoor | Neddy Chiwasa | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 30 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 68.552 | 0 | 1 | Airtel | 0 | ZM0097 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_217A
772 | T3393 | IHS_CBT_217M | KITWE MAIN SCHOOL | 28.2076 | -12.8152 | Copperbelt | 2 | COPPERBELT | KITWE | No | Yes | No | Urban | 2G 3G 4G | P1 | BTS | BTS | On Air | Grid-Gen | Green Field | 30 | Outdoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Generator City | Generator City | 16 | Yanmar | 3TNE88-G1A | ALPHAGEN | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Amaron | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 57 | 0 | 1 | MTN | T3393 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_217M
1519 | ZM0098 | IHS_CBT_218A | PAMODZI | 28.6196 | -12.9291 | Copperbelt | 2.5 | COPPERBELT | Ndola | No | No | No | Suburban | Gold | Gold | BTS | BTS | On Air | Grid-Gen | Green Field | 54 | Indoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 77 | 0 | 1 | Airtel | 0 | ZM0098 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_218A
1785 | T3395 | IHS_CBT_218M | WUSAKILE POLICE CAMP | 28.2306 | -12.8507 | Copperbelt | 2 | COPPERBELT | KITWE | No | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On Air | Grid-Gen | Green Field | 30 | Outdoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Generator City | Generator City | 16 | Yanmar | 3TNE88-G1A | ALPHAGEN | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | coslight | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 72.1 | 0 | 1 | MTN | T3395 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_218M
212 | ZM0100 | IHS_CBT_219A | CHINGOLA HILL | 27.8739 | -12.5222 | Copperbelt | 2 | COPPERBELT | Chingola | No | No | No | Suburban | Silver | Silver |  | BB/HUB | On Air | Grid-Gen | Green Field | 40 | Indoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | Yanmar | 0 | Mecc Alte | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 54 | 0 | 1 | Airtel | 0 | ZM0100 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_219A
1532 | T3396 | IHS_CBT_219M | PETAUKE CRESCENT | 28.6227 | -12.9564 | Copperbelt | 2.5 | COPPERBELT | NDOLA | Yes | Yes | No | Urban | 2G 3G 4G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 30 | Outdoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | CK Works | CK Works | 20 | Yanmar | 0 | ALPHAGEN | 0 | 600 | Power cube | ICC330-HA1-C10 | 750 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | n/a | N/A | 165 | 0 | 3 | MTNAirtelLiquid Telecom | T3396 | ZM0245 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_219M
443 | ZM0105 | IHS_CBT_220A | ITIMPI | 28.1746 | -12.7301 | Copperbelt | 2.5 | COPPERBELT | Kitwe | Yes | No | No | Suburban | Gold | Gold | BB | BB | On Air | Grid-Gen | Green Field | 54 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | MPI | MPI | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 42.1 | 0 | 2 | AirtelLiquid Telecom | 0 | ZM0105 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_220A
1554 | T3398 | IHS_CBT_220M | RAILWAY STATION | 28.6526 | -12.9636 | Copperbelt | 2.5 | COPPERBELT | NDOLA | No | Yes | No | Urban | 2G 3G | P2 | BTS | HUB | On Air | Grid-Gen | Green Field | 30 | Outdoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | CK Works | CK Works | 20 | Yanmar | 0 | ALPHAGEN | 0 | 600 | Power cube | ICC330-HA1-C10 | 750 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | n/a | N/A | 115 | 0 | 2 | MTNAirtel | T3398 | ZM0244 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_220M
148 | ZM0106 | IHS_CBT_221A | CHIBULUMA SOUTH | 28.1001 | -12.9011 | Copperbelt | 2.5 | COPPERBELT | Kitwe | No | No | No | Suburban | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 54 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | CDP | CDP | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 40.5 | 0 | 2 | MTNAirtel | T3369 | ZM0106 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_221A
1543 | T3400 | IHS_CBT_221M | POLO CLUB | 27.8776 | -12.5535 | Copperbelt | 2 | COPPERBELT | CHINGOLA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 30 | Outdoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Generator City | Generator City | 16 | Yanmar | 3TNV88 | ALPHAGEN | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | coslight | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 68.8 | 0 | 2 | MTNAirtel | T3400 | ZM0278 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_221M
104 | ZM0109 | IHS_CBT_222A | CHAMBOLI | 28.2206 | -12.8513 | Copperbelt | 4.5 | COPPERBELT | Kitwe | No | No | Yes | Suburban | Gold | Gold | HUB | BTS | On Air | Grid-Gen | Green Field | 54 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 30 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 97 | 0 | 2 | MTNAirtel | T3267 | ZM0109 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_222A
1752 | T3401 | IHS_CBT_222M | TWAPIA OVERSPILL | 28.5995 | -12.9927 | Copperbelt | 2 | COPPERBELT | NDOLA | No | Yes | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 30 | Outdoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Generator City | Generator City | 13 | Yanmar | 3TNV88 | ALPHAGEN | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | C&D True | 1056 | 12 | 176 | 24 | N/A | N/A | N/A | n/a | N/A | 52.7 | 0 | 1 | MTN | T3401 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_222M
877 | ZM0189 | IHS_CBT_223A | LUFWANYAMA | 27.6229 | -12.862 | Copperbelt | 2.5 | COPPERBELT | Lufwanyama | No | No | No | Rural | Silver | Silver | BB | HUB | On Air | Grid-Gen | Green Field | 80 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 44.298 | 0 | 1 | Airtel | 0 | ZM0189 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_223A
1633 | T3403 | IHS_CBT_223M | SHOW GROUNDS | 28.2164 | -12.8437 | Copperbelt | 2 | COPPERBELT | KITWE | No | No | No | Urban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 30 | Outdoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Generator City | Generator City | 16 | Yanmar | 3TNV88 | ALPHAGEN | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 69 | 0 | 1 | MTN | T3403 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_223M
1025 | ZM0197 | IHS_CBT_224A | MASAITI | 28.4159 | -13.3244 | Copperbelt | 4.5 | COPPERBELT | MPongwe | No | No | No | Rural | Silver | Silver | HUB | HUB | On Air | Grid-Gen | Green Field | 50 | Indoor | Neddy Chiwasa | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Earth Technology | Earth Technology | 20 | perkins | 0 | Leroy Sommer | 0 | 500 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 80 | 0 | 1 | Airtel | 0 | ZM0197 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_224A
1670 | T3404 | IHS_CBT_224M | SKYWAYS KAPIRI ROAD | 28.6589 | -13.0114 | Copperbelt | 2 | COPPERBELT | NDOLA | No | Yes | No | Suburban | 2G 3G | P3 | BTS | HUB | On Air | Grid-Gen | Green Field | 30 | Outdoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Generator City | Generator City | 13 | Yanmar | 3TNV88 | ALPHAGEN | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | C&D True | 1056 | 12 | 176 | 24 | N/A | N/A | N/A | n/a | N/A | 109 | 0 | 2 | MTNAirtel | T3404 | ZM0383 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_224M
1113 | ZM0210 | IHS_CBT_225A | MISENGA | 27.9561 | -12.5994 | Copperbelt | 2.5 | COPPERBELT | Kalulushi | No | No | No | Rural | Silver | Silver |  | BTS | On Air | Grid-Gen | Green Field | 56 | Indoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Earth Technology | Earth technology | 20 | perkins | 0 | Leroy Sommer | 0 | 400 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 32 | 0 | 1 | Airtel | 0 | ZM0210 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_225A
1293 | T3408 | IHS_CBT_225M | MUSHIPI | 28.2287 | -12.8652 | Copperbelt | 2 | COPPERBELT | KITWE | No | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 30 | Outdoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Generator City | Generator City | 16 | Yanmar | 3TNV88 | ALPHAGEN | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Wolong | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 75 | 0 | 1 | MTN | T3408 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_225M
1585 | ZM0211 | IHS_CBT_226A | SAKANIA | 28.5344 | -12.8601 | Copperbelt | 2 | COPPERBELT | Ndola | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 56 | Indoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 49 | 0 | 1 | Airtel | 0 | ZM0211 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_226A
163 | T3412 | IHS_CBT_226M | CHIFUBU WEST | 28.6075 | -12.9345 | Copperbelt | 2 | COPPERBELT | NDOLA | No | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 30 | Outdoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Generator City | Generator City | 13 | Yanmar | 3TNV88 | ALPHAGEN | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 69.6 | 0 | 1 | MTN | T3412 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_226M
360 | ZM0219 | IHS_CBT_227A | FIWALE | 28.75 | -13.3118 | Copperbelt | 1.8 | COPPERBELT | Masaiti | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 50 | Indoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | GNM | GNM | 15 | perkins | 0 | Leroy Sommer | 0 | 500 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 36 | 0 | 1 | Airtel | 0 | ZM0219 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_227A
856 | T3414 | IHS_CBT_227M | LUANSHYA EAST | 28.4292 | -13.1404 | Copperbelt | 2 | COPPERBELT | LUANSHYA | Yes | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 30 | Outdoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Generator City | Generator City | 16 | Yanmar | 3TNV88 | ALPHAGEN | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | C&D True | 1056 | 12 | 176 | 48 | N/A | N/A | N/A | n/a | N/A | 60.3 | 0 | 3 | MTNAirtelLiquid Telecom | T3414 | ZM0250 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_227M
1106 | ZM0230 | IHS_CBT_228A | MINDOLO | 28.1931 | -12.7981 | Copperbelt | 2.5 | COPPERBELT | Kitwe | No | No | Yes | Suburban | Gold | Gold | HUB | BTS | On Air | Grid-Gen | Green Field | 50 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Earth Technology | Earth technology | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 81.903 | 0 | 2 | AirtelINQ | 0 | ZM0230 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_228A
213 | T3415 | IHS_CBT_228M | CHINGOLA INDUSTRIAL | 27.5549 | -12.5387 | Copperbelt | 1.8 | COPPERBELT | CHINGOLA | No | No | No | Urban | 2G 3G 4G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 30 | Outdoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Generator City | Generator City | 15 | Yanmar | 3TNV88 | ALPHAGEN | 0 | 400 | Delta | DPS 2400B-48-5 | 250 | coslight | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 100 | 0 | 2 | MTNAirtel | T3415 | ZM0282 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_228M
205 | ZM0231 | IHS_CBT_229A | CHIMWEMWE | 28.2017 | -12.7726 | Copperbelt | 2.5 | COPPERBELT | Kitwe | Yes | No | Yes | Suburban | Gold | Gold | BB | BB | On Air | Grid-Gen | Green Field | 50 | Outdoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 20 | perkins | 0 | Mecc Alte | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 109.4 | 0 | 1 | Airtel | 0 | ZM0231 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_229A
670 | T3420 | IHS_CBT_229M | KAPISHA NORTH | 27.8983 | -12.5239 | Copperbelt | 1.8 | COPPERBELT | CHINGOLA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 30 | Outdoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Generator City | Generator City | 15 | Yanmar | 3TNV88 | ALPHAGEN | 0 | 400 | Delta | DPS 2400B-48-5 | 250 | C&D True | 1056 | 12 | 176 | 48 | N/A | N/A | N/A | n/a | N/A | 35 | 0 | 2 | MTNAirtel | T3420 | ZM0223 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_229M
1092 | ZM0239 | IHS_CBT_230A | MIKOMFWA | 28.4145 | -13.1619 | Copperbelt | 1.8 | COPPERBELT | Luanshya | No | No | No | Suburban | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 54 | Indoor | Neddy Chiwasa | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Earth Technology | Earth technology | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 68.055 | 0 | 1 | Airtel | 0 | ZM0239 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_230A
455 | T3425 | IHS_CBT_230M | JUMBE ROAD | 27.8637 | -12.5229 | Copperbelt | 2 | COPPERBELT | CHINGOLA | No | No | No | Urban | 2G 3G 4G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 30 | Outdoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Generator City | Generator City | 16 | Yanmar | 3TNV88 | ALPHAGEN | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 61 | 0 | 1 | MTN | T3425 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | Done | 2019-07-12 | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_230M
549 | T3475 | IHS_CBT_231M | Kalilo | 27.7718 | -12.4865 | Copperbelt | 2.5 | COPPERBELT | CHINGOLA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 55 | Outdoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | coslight | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 35.6 | 0 | 1 | MTN | T3475 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_231M
871 | ZM0267 | IHS_CBT_232A | LUBUTO | 28.6248 | -13.0121 | Copperbelt | 2.5 | COPPERBELT | Ndola | Yes | Yes | No | Suburban | Gold | Gold | HUB | BTS | On Air | Grid-Gen | Green Field | 50 | Indoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 20 | perkins | GV51790V | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 136 | 0 | 2 | MTNAirtel | T3273 | ZM0267 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_232A
167 | T3468 | IHS_CBT_232M | Chikola Valley | 27.8578 | -12.562 | Copperbelt | 2 | COPPERBELT | CHINGOLA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 55 | Outdoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Earth Technology | Earth technology | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-HA1-C10 | 750 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 68 | 0 | 2 | MTNAirtel | T3468 | ZM6960 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_232M
248 | ZM0268 | IHS_CBT_233A | CHIPULUKUSU | 28.6635 | -12.9371 | Copperbelt | 1.8 | COPPERBELT | Ndola | Yes | No | No | Suburban | Gold | Gold | HUB | BTS | On Air | Grid-Gen | Green Field | 50 | Indoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Earth Technology | Earth Technology | 15 | perkins | 0 | Leroy Sommer | 0 | 400 | Power cube | ICC330-HA1-C10 | 750 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 147 | 0 | 1 | Airtel | 0 | ZM0268 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_233A
1791 | T3457 | IHS_CBT_233M | Zambeef Mpongwe | 27.7516 | -13.575 | Copperbelt | 2 | COPPERBELT | MPONGWE | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 55 | Outdoor | Neddy Chiwasa | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Falcon | Falcon | 16 | perkins | 0 | Leroy Sommer | 0 | 400 | Delta | DPS 2400B-48-5 | 250 | C&D True | 1056 | 12 | 176 | 24 | N/A | N/A | N/A | n/a | N/A | 38 | 0 | 1 | MTN | T3457 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_233M
283 | ZM0269 | IHS_CBT_234A | CHIWALA | 28.7404 | -12.9997 | Copperbelt | 4.5 | COPPERBELT | Masaiti | No | No | No | Rural | Silver | Silver | HUB | HUB | On Air | Grid-Gen | Green Field | 48 | Indoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 26.5 | 0 | 1 | Airtel | 0 | ZM0269 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_234A
1810 | T3535 | IHS_CBT_234M | Zumran | 27.8791 | -12.6653 | Copperbelt | 2.5 | COPPERBELT | CHINGOLA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Solar-Gen | Green Field | 36 | Outdoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | IMG | IMG | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | EPW30-48A | 120 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | N/A | N/A | 30 | 0 | 1 | MTN | T3535 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_234M
528 | ZM0379 | IHS_CBT_235A | KAFULAFUTA | 28.6716 | -13.2496 | Copperbelt | 2.5 | COPPERBELT | Masaiti | No | No | No | Rural | Silver | Silver | HUB | BTS | On Air | Grid-Gen | Green Field | 50 | Indoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Lamasat | Lamasat | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 42 | 0 | 1 | Airtel | 0 | ZM0379 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_235A
749 | T3536 | IHS_CBT_235M | KAWAMA KCC (Chimwemwe rlf | 28.219 | -12.7574 | Copperbelt | 2.5 | COPPERBELT | KITWE | No | No | No | Urban | #N/A | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-HA1-C10 | 750 | Lithium | 600 | 48 | 100 | 6 | N/A | N/A | N/A | n/a | N/A | 104.9 | 0 | 2 | MTNAirtel | T3358 | ZM0469 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_235M
538 | ZM0650 | IHS_CBT_236A | KALALANGABO | 28.6766 | -13.4087 | Copperbelt | 4.5 | COPPERBELT | Masaiti | No | No | No | Rural | Silver | Silver | BB | BB | On Air | Grid-Gen | Green Field | 80 | Indoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | ASCOT | ASCOT | 30 | Deutz | 0 | Mecc Alte | 0 | 2000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 70.469 | 0 | 1 | Airtel | 0 | ZM0650 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_236A
1422 | T3552 | IHS_CBT_236M | Ndola ZSIC Rooftop | 28.6475 | -12.9727 | Copperbelt | 1.8 | COPPERBELT | 1 | No | No | No | Urban |  | P4 | BTS | BTS | On Air | Grid-Gen | Roof Top | RT | Outdoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 22 | 0 | 1 | MTN | T3552 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_236M
1460 | ZM0651 | IHS_CBT_237A | NKANA WEST | 28.2032 | -12.8312 | Copperbelt | 2.5 | COPPERBELT | Kitwe | No | No | Yes | Urban | Gold | Gold | HUB | HUB | On Air | Grid-Gen | Green Field | 50 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Earth Technology | Earth technology | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Emerson | 701 IG4 | 300 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 104.315 | 0 | 2 | MTNAirtel | T3317 | ZM0651 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_237A
1415 | T3563 | IHS_CBT_237M | Ndola- Hospital | 28.6342 | -12.9701 | Copperbelt | N/A | COPPERBELT | Ndola | No | No | No | Urban | P4 | P4 | BTS | BTS | On Air | Grid Only | Roof Top | RT | Outdoor | Elvis Mumba | SBC | SBC | MTN | Mwenya Banda | In House | GNM | n/a | n/a | N/A | N/A | N/A | N/A | N/A | N/A | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 104.315 | 0 | 1 | MTN | T3563 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_237M
889 | ZM0652 | IHS_CBT_238A | LULAMBA | 27.8493 | -12.574 | Copperbelt | 2 | COPPERBELT | Chingola | Yes | No | No | Suburban | Silver | Silver |  | BTS | On Air | Grid-Gen | Green Field | 50 | Indoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | Lister petter | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 44.5 | 0 | 1 | Airtel | 0 | ZM0652 | yes |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_238A
1390 | T1170 | IHS_CBT_238M | NAPSA Complex | 28.1251 | -12.8314 | Copperbelt | 1.8 | COPPERBELT | Kalulushi | No | No | No | Urban | P4 | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 50 | Outdoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | MPMC | MPMC | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 28 | 0 | 1 | MTN | T3564 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_238M
878 | ZM0678 | IHS_CBT_239A | LUFWANYAMA ROAD | 27.8039 | -12.8486 | Copperbelt | 2 | COPPERBELT | Kalulushi | No | No | No | Rural | Silver | Silver | BB | BB | On Air | Grid-Gen | Green Field | 80 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Diesel Electric | Diesel Electric | 16 | Lister petter | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 48.054 | 0 | 1 | Airtel | 0 | ZM0678 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_239A
1445 | T3577 | IHS_CBT_239M | Nfca mine | 28.0474 | -12.6959 | Copperbelt | 2.5 | COPPERBELT | Chambeshi | No | No | No | Rural | P4 | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 50 | Outdoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 25.5 | 0 | 1 | MTN | T3565 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_239M
604 | ZM0792 | IHS_CBT_240A | KAMUCHANGA | 28.237 | -12.5699 | Copperbelt | 2 | COPPERBELT | Mufulira | No | No | No | Suburban | Silver | Silver |  | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | LISTER PETTER | LISTER PETTER | 20 | Lister petter | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 71.465 | 0 | 1 | Airtel | 0 | ZM0792 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_240A
1142 | T3576 | IHS_CBT_240M | Mopani mindola mine | 28.2404 | -12.5211 | Copperbelt | 2 | COPPERBELT | KITWE | No | No | No | Suburban | P4 | P4 | BTS | BTS | On Air | Solar-Gen | Green Field | 50 | Outdoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | CDP | CDP | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 35.5 | 0 | 1 | MTN | T3567 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_240M
46 | ZM0793 | IHS_CBT_241A | BULANGILILO | 28.2339 | -12.77 | Copperbelt | 2.5 | COPPERBELT | Kitwe | Yes | No | No | Suburban | Gold | Gold | HUB | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | perkins | perkins | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 52.2 | 0 | 1 | Airtel | 0 | ZM0793 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_241A
531 | T3575 | IHS_CBT_241M | Kagem mine | 28.1275 | -13.0877 | Copperbelt | 2.5 | COPPERBELT | Kitwe | No | No | No | Rural | P4 | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 44 | Outdoor | Chrispin Lindundu | SBC | SBC | MTN | Mwenya Banda | GNM | GNM | perkins | perkins | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 37 | 0 | 1 | MTN | T3568 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_241M
1521 | ZM0794 | IHS_CBT_242A | PARKLANDS | 28.2084 | -12.8061 | Copperbelt | 2.5 | COPPERBELT | Kitwe | Yes | No | No | Urban | Gold | Gold | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 75.221 | 0 | 1 | Airtel | 0 | ZM0794 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_242A
379 | ZM0795 | IHS_CBT_243A | GEDDIS | 28.2201 | -12.8252 | Copperbelt | 1.8 | COPPERBELT | Kitwe | Yes | No | No | Urban | Gold | Gold | BTS | BTS | On Air | Grid-Gen | Green Field | 35 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 48.9 | 0 | 1 | Airtel | 0 | ZM0795 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_243A
98 | T3571 | IHS_CBT_243M | Chambeshi | 28.0715 | -12.6297 | Copperbelt | 2.5 | COPPERBELT | Chambeshi | No | No | No | Suburban | P4 | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 50 | Outdoor | Panji Njovu | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 40.1 | 0 | 1 | MTN | T3571 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_243M
1403 | ZM0796 | IHS_CBT_244A | NDEKE | 28.2436 | -12.8535 | Copperbelt | 1.8 | COPPERBELT | Kitwe | No | No | No | Suburban | Gold | Gold | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Earth Technology | Earth technology | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 132 | 0 | 2 | MTNAirtel | T3547 | ZM0796 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_244A
1480 | ZM0797 | IHS_CBT_245A | NORTHRISE | 28.6322 | -12.947 | Copperbelt | 2.5 | COPPERBELT | Ndola | Yes | Yes | Yes | Urban | Gold | Gold | BTS | BTS | On Air | Grid-Gen | Green Field | 35 | Indoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Lamasat | Lamasat | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 18000 | 18000 | 2 | 140 | 0 | 2 | MTNAirtel | T3237 | ZM0797 | yes |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | Done |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_245A
1421 | ZM0798 | IHS_CBT_246A | NDOLA TOWN | 28.6419 | -12.9702 | Copperbelt | 4.5 | COPPERBELT | Ndola | Yes | No | Yes | Urban | Gold | Gold | BTS | HUB | On Air | Grid-Gen | Green Field | 36 | Indoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | IMG Perkins | CK Power | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 180 | 0 | 1 | Airtel | 0 | ZM0798 | yes |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | Done |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_246A
1396 | ZM0799 | IHS_CBT_247A | NCHANGA | 27.8619 | -12.5346 | Copperbelt | 2 | COPPERBELT | Chingola | No | No | No | Urban | Silver | Silver |  | BTS | On Air | Grid-Gen | Green Field | 34 | Indoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | IMG | IMG | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 44.5 | 0 | 1 | Airtel | 0 | ZM0799 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_247A
981 | ZM0800 | IHS_CBT_248A | MALCOM WATSON | 28.2472 | -12.5423 | Copperbelt | 2 | COPPERBELT | Mufulira | No | No | No | Urban | Silver | Silver |  | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | LISTER PETTER | LISTER PETTER | 16 | Lister petter | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 50.4 | 0 | 1 | Airtel | 0 | ZM0800 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_248A
44 | ZM0801 | IHS_CBT_249A | BUCHI | 28.2057 | -12.7871 | Copperbelt | 2 | COPPERBELT | Kitwe | Yes | No | No | Suburban | Gold | Gold | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 18000 | 18000 | 2 | 63.359 | 0 | 2 | MTNAirtel | T3263 | ZM0801 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_249A
1674 | ZM0802 | IHS_CBT_250A | SOB | 28.2204 | -12.8603 | Copperbelt | 1.8 | COPPERBELT | Kitwe | No | No | No | Suburban | Gold | Gold | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 15 | Lister petter | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 48.3 | 0 | 1 | Airtel | 0 | ZM0802 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_250A
777 | ZM0803 | IHS_CBT_251A | Kitwe Railways | 28.2038 | -12.8204 | Copperbelt | 2.5 | COPPERBELT | Kitwe | No | Yes | No | Urban | Gold | Gold | BTS | BTS | On Air | Grid-Gen | Green Field | 35 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | MPI | MPI | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 71 | 0 | 2 | MTNAirtel | T3266 | ZM0803 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_251A
161 | ZM0804 | IHS_CBT_252A | CHIFUBU | 28.6115 | -12.9368 | Copperbelt | 4.5 | COPPERBELT | Ndola | Yes | No | No | Suburban | Gold | Gold | BB | BTS | On Air | Grid-Gen | Green Field | 35 | Indoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 30 | perkins | LPW4 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 180 | 0 | 3 | MTNAirtelLiquid Telecom | T3029 | ZM0804 | yes |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | Done | 2019-07-15 | No | No | Yes |  |  | yes - Emergency | 30 | 43661 | closed |  |  |  |  | IHS_CBT_252A
438 | ZM0805 | IHS_CBT_253A | ITAWA | 28.6546 | -12.9865 | Copperbelt | 2.5 | COPPERBELT | Ndola | Yes | No | No | Urban | Gold | Gold | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 20 | perkins | LPW4 | Listerpetter | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 73.8 | 0 | 2 | AirtelLiquid Telecom | 0 | ZM0805 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_253A
1169 | ZM0821 | IHS_CBT_254A | MPONGWE BOMA | 28.1821 | -13.5149 | Copperbelt | 2.5 | COPPERBELT | MPongwe | No | No | No | Rural | Silver | Silver | BTS | BB/HUB | On Air | Grid-Gen | Green Field | 70 | Indoor | Neddy Chiwasa | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 46 | 0 | 2 | AirtelTop Star | 0 | ZM0821 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_254A
285 | ZM0856 | IHS_CBT_255A | CHIWEMPALA | 27.8444 | -12.5521 | Copperbelt | 1.8 | COPPERBELT | Chingola | No | No | No | Suburban | Silver | Silver |  | BTS | On Air | Grid-Gen | Green Field | 50 | Indoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 55.284 | 0 | 1 | Airtel | 0 | ZM0856 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_255A
1751 | ZM0858 | IHS_CBT_257A | TWAPIA | 28.5879 | -12.9902 | Copperbelt | 2.5 | COPPERBELT | Ndola | Yes | No | No | Suburban | Gold | Gold | BTS | BB/HUB | On Air | Grid-Gen | Green Field | 40 | Outdoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | CK Works | CK Works | 20 | Lister petter | LPW4 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 500 | 48 | 100 | 5 | N/A | N/A | N/A | 0 | N/A | 212 | 0 | 2 | MTNAirtel | T3546 | ZM0858 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_257A
1302 | ZM0860 | IHS_CBT_258A | MUTENDA | 27.4137 | -12.4334 | Copperbelt | 4.5 | COPPERBELT | Chingola | No | No | No | Rural | Silver | Silver |  | BB | On Air | Grid-Gen | Green Field | 80 | Indoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 58.3 | 0 | 1 | Airtel | 0 | ZM0860 | yes |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | Done | 2019-07-12 | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_258A
582 | ZM0876 | IHS_CBT_259A | KAMAKANGA I & II | 28.0939 | -13.114 | Copperbelt | 2.5 | COPPERBELT | Lufwanyama | No | No | No | Rural | Silver | Silver |  | BTS | On Air | Grid-Gen | Green Field | 70 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | perkins | perkins | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Power safe | 1200 | 2 | 1200 | 24 | LG | LG | 18000 | 18000 | 2 | 35.2 | 0 | 1 | Airtel | 0 | ZM0876 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_259A
591 | ZM0877 | IHS_CBT_260A | KAMFINSA | 28.3313 | -12.8734 | Copperbelt | 2.5 | COPPERBELT | Kitwe | No | No | No | Suburban | Silver | Silver |  | BTS | On Air | Grid-Gen | Green Field | 60 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | perkins | perkins | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 50.436 | 0 | 2 | MTNAirtel | T3348 | ZM0877 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_260A
111 | ZM0883 | IHS_CBT_261A | CHATI | 27.8178 | -12.8198 | Copperbelt | 2 | COPPERBELT | Kalulushi | No | No | No | Rural | Silver | Silver |  | BTS | On Air | Solar-Gen | Green Field | 60 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | perkins | perkins | 16 | perkins | 0 | Zanardi | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 18000 | 18000 | 2 | 51.258 | 0 | 1 | Airtel | 0 | ZM0883 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_261A
1114 | ZM0889 | IHS_CBT_262A | MISESHI NATWANGE | 28.2209 | -12.8435 | Copperbelt | 2.5 | COPPERBELT | Kitwe | Yes | No | Yes | Suburban | Gold | Gold |  | BB/HUB | On Air | Grid-Gen | Green Field | 36 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | perkins | perkins | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 55.8 | 0 | 1 | Airtel | 0 | ZM0889 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_262A
1349 | ZM0890 | IHS_CBT_263A | NAKADOLI | 28.1919 | -12.7775 | Copperbelt | 2 | COPPERBELT | Kitwe | Yes | No | No | Suburban | Gold | Gold | HUB | BTS | On Air | Grid-Gen | Green Field | 35 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Lister petter | 0 | Leroy Sommer | 0 | 600 | Emerson | 701 IG4 | 300 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 18000 | 18000 | 2 | 68.2 | 0 | 1 | Airtel | 0 | ZM0890 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_263A
1419 | ZM0891 | IHS_CBT_264A | NDOLA OVERSPILL | 28.6306 | -12.933 | Copperbelt | 2 | COPPERBELT | Ndola | Yes | No | Yes | Urban | Gold | Gold | HUB | HUB | On Air | Grid-Gen | Green Field | 36 | Indoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 700 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 89 | 0 | 1 | Airtel | 0 | ZM0891 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_264A
1443 | ZM0894 | IHS_CBT_265A | NEW TOWN | 28.4059 | -13.1134 | Copperbelt | 2 | COPPERBELT | Luanshya | No | No | No | Urban | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 35 | Indoor | Neddy Chiwasa | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 56.658 | 0 | 1 | Airtel | 0 | ZM0894 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_265A
746 | ZM0896 | IHS_CBT_266A | KAWAMA Copperbelt | 28.1997 | -12.7516 | Copperbelt | 2 | COPPERBELT | Kitwe | Yes | No | No | Suburban | Gold | Gold | BTS | BTS | On Air | Grid-Gen | Green Field | 50 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 54.31 | 0 | 1 | Airtel | 0 | ZM0896 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_266A
569 | ZM0897 | IHS_CBT_267A | KALULUSHI EAST | 28.1008 | -12.8422 | Copperbelt | 2 | COPPERBELT | Kitwe | No | No | No | Suburban | Silver | Silver | HUB | BTS | On Air | Grid-Gen | Green Field | 40 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 60.5 | 0 | 2 | MTNAirtel | T3543 | ZM0897 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_267A
366 | ZM0898 | IHS_CBT_268A | FRANCIS MUKUKA | 28.2542 | -12.5713 | Copperbelt | 2.5 | COPPERBELT | Mufulira | No | No | No | Suburban | Silver | Silver |  | HUB | On Air | Grid-Gen | Green Field | 36 | Indoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 85 | 0 | 2 | MTNAirtel | T3270 | ZM0898 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_CBT_268A
1686 | ZM0899 | IHS_CBT_269A | SOSOLISO | 28.2496 | -12.7975 | Copperbelt | 1.8 | COPPERBELT | Kitwe | No | No | Yes | Urban | Gold | Gold | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Jiuan | Jiuan | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 47.5 | 0 | 1 | Airtel | 0 | ZM0899 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_269A
709 | ZM3108 | IHS_CBT_270A | KASOMPE | 27.8898 | -12.5848 | Copperbelt | 4.5 | COPPERBELT | Chingola | Yes | No | No | Suburban | Silver | Silver |  | BB/HUB | On Air | Grid-Gen | Green Field | 50 | Indoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 52.769 | 0 | 1 | Airtel | 0 | ZM3108 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_270A
1200 | ZM3215 | IHS_CBT_271A | MUFULIRA TURNOFF | 28.1241 | -12.7021 | Copperbelt | 2.5 | COPPERBELT | Kitwe | No | No | No | Suburban | Silver | Silver |  | BB | On Air | Grid-Gen | Green Field | 60 | Indoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | perkins | perkins | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 42.5 | 0 | 1 | Airtel | 0 | ZM3215 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_271A
192 | ZM3216 | IHS_CBT_272A | CHILILABOMBWE ROAD | 27.854 | -12.4419 | Copperbelt | 2 | COPPERBELT | Chingola | No | No | No | Rural | Silver | Silver |  | BTS | On Air | Grid-Gen | Green Field | 60 | Indoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Lister petter | 0 | Sincro | 0 | 400 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 35 | 0 | 2 | MTNAirtel | T3032 | ZM3216 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_272A
214 | ZM3240 | IHS_CBT_273A | CHINGOLA INDUSTRIAL Solwezi Road | 27.844 | -12.5413 | Copperbelt | 1.8 | COPPERBELT | Chingola | No | No | No | Urban | Silver | Silver |  | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Battery Tech | 0 | 190 | Shoto | 400 | 2 | 400 | 24 | N/A | N/A | N/A | 0 | N/A | 41.1 | 0 | 1 | Airtel | 0 | ZM3240 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_273A
1807 | ZM3261 | IHS_CBT_274A | ZNS | 28.219 | -12.9428 | Copperbelt | 2 | COPPERBELT | Kitwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 70 | Outdoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Lister petter | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 48.288 | 0 | 1 | Airtel | 0 | ZM3261 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_274A
486 | ZM3262 | IHS_CBT_275A | KABUNDI EAST | 27.8922 | -12.5261 | Copperbelt | 2.5 | COPPERBELT | Chingola | No | No | No | Suburban | Silver | Silver |  | BB | On Air | Grid-Gen | Green Field | 50 | Indoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | IMG | IMG | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 28.4 | 0 | 1 | Airtel | 0 | ZM3262 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_275A
532 | ZM3263 | IHS_CBT_276A | KAKOLO I & II | 28.3194 | -12.8057 | Copperbelt | 1.8 | COPPERBELT | Kitwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Solar-Gen | Green Field | 70 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Jiuan | Jiuan | 15 | Mitsubishi | SL40 | Zanardi | 0 | 600 | N/A | 0 | 0 | BSB | 1500 | 2 | 1500 | 24 | LG | LG | 18000 | 18000 | 2 | 18.5 | 0 | 1 | Airtel | 0 | ZM3263 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_CBT_276A
1564 | ZM3265 | IHS_CBT_277A | ROAN | 28.3767 | -13.1347 | Copperbelt | 2 | COPPERBELT | Luanshya | Yes | No | No | Suburban | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 50 | Outdoor | Neddy Chiwasa | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Narada | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 58 | 0 | 1 | Airtel | 0 | ZM3265 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_277A
1222 | ZM3266 | IHS_CBT_278A | MUKUMPU I & II | 27.7487 | -13.6727 | Copperbelt | 1.8 | COPPERBELT | MPongwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 70 | Outdoor | Neddy Chiwasa | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | perkins | perkins | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Emerson | 701 IG4 | 300 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 30 | 0 | 1 | Airtel | 0 | ZM3266 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_278A
95 | ZM3267 | IHS_CBT_279A | CHAMBATATA I & II | 27.9255 | -13.6016 | Copperbelt | 1.8 | COPPERBELT | MPongwe | No | No | No | Rural | Silver | Silver | HUB | BB | On Air | Grid-Gen | Green Field | 70 | Indoor | Neddy Chiwasa | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Jiuan | Jiuan | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 43.006 | 0 | 1 | Airtel | 0 | ZM3267 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_279A
369 | ZM3271 | IHS_CBT_280A | FRONTIER MINE | 28.4827 | -12.7541 | Copperbelt | 2.5 | COPPERBELT | Ndola | No | No | No | Rural | Silver | Silver | HUB | BTS | On Air | Grid-Gen | Green Field | 50 | Indoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Battery Tech | 0 | 190 | Shoto | 400 | 2 | 400 | 24 | LG | LG | 18000 | 18000 | 2 | 49.542 | 0 | 2 | AirtelParatus Telecom | 0 | ZM3271 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_280A
70 | ZM3275 | IHS_CBT_281A | CHABANYAMA | 27.8361 | -12.5658 | Copperbelt | 2.5 | COPPERBELT | Chingola | No | No | No | Suburban | Silver | Silver |  | HUB | On Air | Grid-Gen | Green Field | 50 | Indoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 85.8 | 0 | 2 | MTNAirtel | T3248 | ZM3275 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_281A
1029 | ZM3278 | IHS_CBT_283A | MASALA | 28.6156 | -13.017 | Copperbelt | 2.5 | COPPERBELT | Ndola | Yes | No | Yes | Suburban | Gold | Gold | BB | BTS | On Air | Grid-Gen | Green Field | 50 | Indoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | IMG | IMG | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 48.3 | 0 | 1 | Airtel | 0 | ZM3278 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_283A
66 | ZM3279 | IHS_CBT_284A | CBU | 28.2371 | -12.8061 | Copperbelt | 4.5 | COPPERBELT | Kitwe | Yes | No | Yes | Urban | Gold | Gold | HUB | BTS | On Air | Grid-Gen | Green Field | 50 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 30 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 146 | 0 | 2 | MTNAirtel | T3264 | ZM3279 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_284A
795 | ZM3290 | IHS_CBT_285A | KWACHA | 28.2235 | -12.7801 | Copperbelt | 2.5 | COPPERBELT | Kitwe | Yes | No | Yes | Suburban | Gold | Gold | HUB | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 125 | 0 | 3 | MTNAirtelLiquid Telecom | T3570 | ZM3290 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_285A
1567 | ZM3291 | IHS_CBT_286A | ROKANA | 28.211 | -12.8241 | Copperbelt | 2 | COPPERBELT | Kitwe | No | No | Yes | Urban | Gold | Gold | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 64.712 | 0 | 2 | AirtelINQ | 0 | ZM3291 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_286A
400 | ZM3292 | IHS_CBT_287A | HELLEN KAUNDA | 27.8245 | -12.3581 | Copperbelt | 2 | COPPERBELT | Chililabombwe | No | No | No | Suburban | Silver | Silver |  | BTS | On Air | Grid-Gen | Green Field | 50 | Indoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 300 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 39.5 | 0 | 1 | Airtel | 0 | ZM3292 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_287A
1412 | ZM3294 | IHS_CBT_288A | NDOLA BUS STATION | 28.6506 | -12.9754 | Copperbelt | 2.5 | COPPERBELT | Ndola | Yes | Yes | Yes | Urban | Gold | Gold | BTS | EBU Hub | On Air | Grid-Gen | Green Field | 36 | Indoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | CK Works | CK Works | 20 | perkins | 3TNV88 | ALPHAGEN | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 18000 | 18000 | 2 | 204 | 0 | 3 | MTNAirtelLiquid Telecom | T3397 | ZM3294 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_288A
52 | ZM3295 | IHS_CBT_289A | BUPE | 28.2328 | -12.864 | Copperbelt | 1.8 | COPPERBELT | Kitwe | No | No | No | Suburban | Gold | Gold | BTS | Hub | On Air | Grid-Gen | Green Field | 36 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 38.7 | 0 | 1 | Airtel | 0 | ZM3295 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_289A
1195 | ZM3296 | IHS_CBT_290A | MUCHINSHI | 28.4137 | -13.1491 | Copperbelt | 2 | COPPERBELT | Luanshya | No | No | No | Suburban | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Neddy Chiwasa | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 17 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 47.1 | 0 | 1 | Airtel | 0 | ZM3296 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_290A
1333 | ZM3336 | IHS_CBT_291A | MWATAYANVWA | 28.6447 | -12.955 | Copperbelt | 2.5 | COPPERBELT | Ndola | No | Yes | Yes | Urban | Gold | Gold | BTS | BTS | On Air | Grid-Gen | Green Field | 34 | Outdoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 20 | Lister petter | LPW4 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | 0 | N/A | 134 | 0 | 2 | MTNAirtel | T3272 | ZM3336 | yes |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | Done |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_291A
750 | ZM3337 | IHS_CBT_292A | KAWAMA MARKET | 28.6123 | -12.9171 | Copperbelt | 2.5 | COPPERBELT | Ndola | No | No | No | Suburban | Gold | Gold | HUB | HUB | On Air | Grid-Gen | Green Field | 36 | Indoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 20 | Lister petter | LPW4 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 32.7 | 0 | 1 | Airtel | 0 | ZM3337 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_292A
1284 | ZM3338 | IHS_CBT_293A | MUSAKASONKA | 28.6422 | -12.9936 | Copperbelt | 2.5 | COPPERBELT | Ndola | No | No | No | Suburban | Gold | Gold | BTS | BTS | On Air | Grid-Gen | Green Field | 35 | Indoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 74.465 | 0 | 1 | Airtel | 0 | ZM3338 | yes |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | Done |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_293A
1550 | ZM3350 | IHS_CBT_294A | PROTEA | 27.8803 | -12.5396 | Copperbelt | 2 | COPPERBELT | Chingola | No | No | No | Urban | Silver | Silver |  | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | Lister petter | 0 | Leroy Sommer | 0 | 400 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 41.6 | 0 | 1 | Airtel | 0 | ZM3350 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_294A
1749 | ZM3356 | IHS_CBT_295A | TWALUBUKA | 28.058 | -12.6335 | Copperbelt | 2 | COPPERBELT | Kalulushi | No | No | No | Suburban | Silver | Silver |  | HUB | On Air | Grid-Gen | Green Field | 50 | Outdoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Earth Technology | Earth technology | 15 | perkins | 0 | Leroy Sommer | 0 | 400 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 40.1 | 0 | 1 | Airtel | 0 | ZM3356 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_295A
607 | ZM3375 | IHS_CBT_296A | KAMUNGA | 28.2085 | -12.775 | Copperbelt | 2 | COPPERBELT | Kitwe | No | Yes | No | Suburban | Gold | Gold | BTS | BTS | On Air | Grid-Gen | Green Field | 30 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 300 | 48 | 150 | 2 | LG | LG | 18000 | 18000 | 2 | 75.6 | 0 | 2 | MTNAirtel | T3262 | ZM1502 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_296A
774 | ZM3376 | IHS_CBT_297A | KITWE POLICE | 28.2054 | -12.8165 | Copperbelt | 2 | COPPERBELT | Kitwe | No | No | No | Urban | Gold | Gold | BTS | BTS | On Air | Grid-Gen | Green Field | 30 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 51 | 0 | 1 | Airtel | 0 | ZM3376 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_297A
775 | ZM3378 | IHS_CBT_299A | KITWE POST OFFICE | 28.2109 | -12.8206 | Copperbelt | 2 | COPPERBELT | Kitwe | No | No | No | Urban | Gold | Gold | BTS | BTS | On Air | Grid-Gen | Roof Top | RT | Outdoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 17 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Emerson | 701 IG4 | 300 | Power safe | 1200 | 2 | 1200 | 24 | N/A | N/A | N/A | 0 | N/A | 45.6 | 0 | 1 | Airtel | 0 | ZM3378 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_299A
861 | ZM3380 | IHS_CBT_300A | LUBAMBE | 28.2214 | -12.7987 | Copperbelt | 4.5 | COPPERBELT | Kitwe | Yes | Yes | No | Urban | Gold | Gold | HUB | HUB | On Air | Grid-Gen | Green Field | 50 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Jiuan | Jiuan | 30 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 211 | 0 | 4 | MTNAirtelINQLiquid Telecom | T3327 | ZM3380 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | yes | 30 |  | Pending |  |  |  |  | IHS_CBT_300A
149 | ZM3381 | IHS_CBT_301A | CHIBULUMA TOWN | 28.1352 | -12.8512 | Copperbelt | 2 | COPPERBELT | Kitwe | Yes | No | No | Suburban | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 50 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 49.544 | 0 | 1 | Airtel | 0 | ZM3381 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_301A
1103 | ZM3382 | IHS_CBT_302A | MILYASHI | 28.3293 | -13.0741 | Copperbelt | 2 | COPPERBELT | Luanshya | No | No | No | Rural | Silver | Silver | BTS | HUB | On Air | Grid-Gen | Green Field | 70 | Indoor | Neddy Chiwasa | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 38.5499 | 0 | 1 | Airtel | 0 | ZM3382 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_302A
102 | ZM3383 | IHS_CBT_303A | CHAMBISHI SMELTER | 28.0986 | -12.6545 | Copperbelt | 1.8 | COPPERBELT | Kalulushi | No | No | No | Suburban | Silver | Silver |  | BTS | On Air | Grid-Gen | Green Field | 60 | Indoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | LAMASAT | LAMASAT | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 35.5 | 0 | 1 | Airtel | 0 | ZM3383 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_303A
1515 | ZM3393 | IHS_CBT_304A | ORCHARD | 28.2381 | -12.5463 | Copperbelt | 2.5 | COPPERBELT | Mufulira | No | No | No | Suburban | Silver | Silver |  | HUB | On Air | Grid-Gen | Green Field | 50 | Indoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | Energy star | Energy star | 18000 | 18000 | 2 | 108 | 0 | 2 | MTNAirtel | T3269 | ZM3393 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_304A
850 | ZM3396 | IHS_CBT_305A | LUANGWA KAFUE | 28.2493 | -12.882 | Copperbelt | 2 | COPPERBELT | Kitwe | Yes | No | No | Suburban | Gold | Gold | HUB | HUB | On Air | Grid-Gen | Green Field | 50 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Yanmar | Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 62.414 | 0 | 3 | MTNAirtelLiquid Telecom | T3349 | ZM3396 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_305A
1745 | ZM3397 | IHS_CBT_306A | TUG-ARGAN | 28.7693 | -13.0855 | Copperbelt | 2 | COPPERBELT | Masaiti | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Indoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Yanmar | Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 27 | 0 | 1 | Airtel | 0 | ZM3397 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_306A
1748 | ZM3398 | IHS_CBT_307A | TVTC | 28.4365 | -13.1276 | Copperbelt | 2 | COPPERBELT | Luanshya | No | No | No | Urban | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 50 | Outdoor | Neddy Chiwasa | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | Lister petter | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | 0 | N/A | 46.5 | 0 | 1 | Airtel | 0 | ZM3398 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_307A
1418 | ZM3470 | IHS_CBT_309A | NDOLA LIME | 28.6975 | -12.9973 | Copperbelt | 2.5 | COPPERBELT | Ndola | No | No | No | Suburban | Gold | Gold | BTS | BTS | On Air | Grid-Gen | Green Field | 35 | Indoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 15 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 50.2 | 0 | 2 | MTNAirtel | T3499 | ZM3470 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_309A
127 | ZM3505 | IHS_CBT_310A | CHEMBE CHATI | 27.9883 | -12.8389 | Copperbelt | 2 | COPPERBELT | Kalulushi | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 70 | Outdoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 17 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 39.793 | 0 | 1 | Airtel | 0 | ZM3505 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_310A
599 | ZM3507 | IHS_CBT_311A | KAMPOYO | 28.6453 | -13.7712 | Copperbelt | 1.8 | COPPERBELT | MPongwe | No | No | No | Rural | Silver | Silver | BB | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | GL Yanmar | GL Yanmar | 15 | Yanmar | 3TNE88-G1A | Mecc Alte | 0 | 700 | Emerson | 701 IG4 | 300 | Amaron | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 32.4 | 0 | 1 | Airtel | 0 | ZM3507 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_311A
359 | ZM3546 | IHS_CBT_312A | FISENGE | 28.4687 | -13.0699 | Copperbelt | 2 | COPPERBELT | Luanshya | No | No | No | Suburban | Silver | Silver | HUB | BB | On Air | Grid-Gen | Green Field | 60 | Indoor | Neddy Chiwasa | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Yanmar | Yanmar | 16 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 42 | 0 | 2 | MTNAirtel | T3381 | ZM3546 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_312A
766 | ZM3573 | IHS_CBT_313A | KICHIKWE | 27.2209 | -12.3495 | Copperbelt | 1.8 | COPPERBELT | Lufwanyama | No | No | No | Rural | Silver | Silver | BB | BTS | On Air | Solar-Gen | Green Field | 60 | Outdoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | IMG | IMG | 15 | Mitsubishi | SL40 | Zanardi | 0 | 600 | out back | flex max-80 | 0 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | 0 | N/A | 53.043 | 0 | 1 | Airtel | 0 | ZM3573 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_313A
510 | ZM3580 | IHS_CBT_314A | KAFUBU BLOCK | 28.5357 | -13.1271 | Copperbelt | 2.5 | COPPERBELT | Ndola | No | No | No | Rural | Silver | Silver | HUB | BB | On Air | Grid-Gen | Green Field | 60 | Outdoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | N/A | N/A | 0 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 34.5 | 0 | 1 | Airtel | 0 | ZM3580 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_314A
784 | ZM3705 | IHS_CBT_316A | Konkola North | 27.7535 | -12.3012 | Copperbelt | 1.5 | COPPERBELT | Chililabombwe | No | No | No | Suburban | Silver | Silver |  | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | Yanmar | 0 | Leroy Sommer | 0 | 400 | Emerson | 701 IG4 | 300 | coslight | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 72 | 0 | 2 | MTNAirtel | T3040 | ZM3705 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_316A
1376 | ZM3707 | IHS_CBT_317A | Namumba | 28.0008 | -12.6186 | Copperbelt | 2.5 | COPPERBELT | Kalulushi | No | No | No | Rural | Silver | Silver |  | BTS | On Air | Grid-Gen | Green Field | 50 | Outdoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Earth Technology | Earth technology | 20 | perkins | 0 | Leroy Sommer | 0 | 400 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 30.5 | 0 | 1 | Airtel | 0 | ZM3707 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_317A
1462 | ZM3756 | IHS_CBT_319A | Nkanga Hill (Mumena_1) | 28.2616 | -13.4068 | Copperbelt | 1.8 | COPPERBELT | MPongwe | No | No | No | Rural | Silver | Silver | HUB | HUB | On Air | Grid-Gen | Green Field | 36 | Outdoor | Neddy Chiwasa | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | GL Yanmar | GL Yanmar | 15 | Yanmar | 4TNE | Mecc Alte | 0 | 1000 | Power cube | ICC330-HA1-C10 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 45.804 | 0 | 1 | Airtel | 0 | ZM3756 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_319A
1649 | ZM3757 | IHS_CBT_320A | Silangwa (Ndola Rural_1) | 28.7951 | -13.4723 | Copperbelt | 1.8 | COPPERBELT | Masaiti | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | GNM | GNM | 15 | perkins | 0 | Leroy Sommer | 0 | 500 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 18 | 0 | 1 | Airtel | 0 | ZM3757 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_320A
367 | ZM3758 | IHS_CBT_321A | Fred Station (MAPOSA_2) | 28.42 | -12.9977 | Copperbelt | 2.5 | COPPERBELT | Luanshya | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 50 | Indoor | Neddy Chiwasa | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 46.441 | 0 | 1 | Airtel | 0 | ZM3758 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_321A
507 | ZM3759 | IHS_CBT_322A | KAFIRONDA | 28.1795 | -12.6264 | Copperbelt | 2 | COPPERBELT | Kitwe | No | No | No | Rural | Silver | Silver |  | BTS | On Air | Grid-Gen | Green Field | 60 | Indoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Vitalgen | Vitalgen | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 23 | 0 | 1 | MTN | 0 | 0 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_322A
794 | ZM3762 | IHS_CBT_324A | Kwa Zimba (Mufulira_Too) | 28.1886 | -12.5125 | Copperbelt | 2 | COPPERBELT | Mufulira | No | No | No | Rural | Silver | Silver |  | BTS | On Air | Grid-Gen | Green Field | 54 | Indoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Emerson | 701 IG4 | 300 | Power safe | 1200 | 2 | 1200 | 24 | LG | LG | 18000 | 18000 | 2 | 43.6 | 0 | 1 | Airtel | 0 | ZM3762 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_324A
556 | ZM3764 | IHS_CBT_325A | KALOKO KAFULAFUTA | 28.6933 | -13.1782 | Copperbelt | 1.8 | COPPERBELT | Masaiti | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 54 | Outdoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | GL Yanmar | GL Yanmar | 15 | Yanmar | 4TNE | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | coslight | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 32 | 0 | 1 | Airtel | 0 | ZM3764 | yes |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_325A
1215 | ZM3766 | IHS_CBT_326A | Mukolwe (Kafulafuta_Luan) | 28.5884 | -13.1863 | Copperbelt | 2.5 | COPPERBELT | Masaiti | No | No | No | Rural | Silver | Silver | BB | HUB | On Air | Grid-Gen | Green Field | 60 | Indoor | Neddy Chiwasa | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | GNM | GNM | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 70 | 0 | 1 | Airtel | 0 | ZM3766 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_326A
896 | ZM3878 | IHS_CBT_328A | Lumpuma | 27.9097 | -12.719 | Copperbelt | 1.5 | COPPERBELT | Kalulushi | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 48 | Outdoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 10 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 25 | 0 | 1 | Airtel | 0 | ZM3878 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_328A
1708 | ZM3881 | IHS_CBT_329A | St. Marys Mission (MUTENDA ST. MARYS_1) | 27.3717 | -12.8973 | Copperbelt | 1.8 | COPPERBELT | Lufwanyama | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Indoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | METCO | METCO | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 42.9514 | 0 | 1 | Airtel | 0 | ZM3881 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_329A
370 | ZM3884 | IHS_CBT_330A | Funda Junction (Mumena_5) | 27.4841 | -12.9238 | Copperbelt | 1.8 | COPPERBELT | Lufwanyama | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 80 | Outdoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | METCO | METCO | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 37.7 | 0 | 2 | MTNAirtel | T3310 | ZM3884 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_330A
1290 | ZM3963 | IHS_CBT_331A | Mushili Baracks | 28.6211 | -13.0648 | Copperbelt | 1.5 | COPPERBELT | Ndola | No | No | No | Suburban | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 50 | Outdoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | GL Isuzu | GL Isuzu | 10 | ISUZU | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 91 | 0 | 2 | MTNAirtel | T3569 | ZM3963 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_331A
1410 | ZM3965 | IHS_CBT_332A | Ndeke_Ndola | 28.6589 | -12.9943 | Copperbelt | 1.5 | COPPERBELT | Ndola | No | No | No | Suburban | Gold | Gold | BTS | BTS | On Air | Grid-Gen | Roof Top | RT | Outdoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | 0 | 0 | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 300 | Lithium | 500 | 48 | 100 | 5 | N/A | N/A | N/A | 0 | N/A | 48 | 0 | 1 | Airtel | 0 | ZM3965 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_332A
1107 | ZM3967 | IHS_CBT_333A | Mindolo North | 28.18 | -12.7839 | Copperbelt | 1.8 | COPPERBELT | Kitwe | Yes | No | No | Suburban | Gold | Gold | HUB | BTS | On Air | Grid-Gen | Green Field | 40 | Outdoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | perkins | perkins | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 62.078 | 0 | 1 | Airtel | 0 | ZM3967 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_333A
1115 | ZM3968 | IHS_CBT_334A | Miseshi Village | 28.2441 | -12.8369 | Copperbelt | 2 | COPPERBELT | Kitwe | Yes | Yes | No | Suburban | Gold | Gold | HUB | HUB | On Air | Grid-Gen | Green Field | 40 | Outdoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Generator City | Generator City | 16 | Yanmar | 3TNV88 | ALPHAGEN | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 500 | 48 | 100 | 5 | N/A | N/A | N/A | 0 | N/A | 94.5 | 0 | 3 | MTNAirtelLiquid Telecom | T3424 | ZM3968 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_334A
323 | ZM4007 | IHS_CBT_335A | Daag Hamershold | 28.5215 | -13.0081 | Copperbelt | 1.8 | COPPERBELT | Ndola | No | No | No | Suburban | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | LAMASAT | LAMASAT | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 40 | 0 | 2 | AirtelParatus Telecom | 0 | ZM4007 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_335A
353 | ZM6036 | IHS_CBT_336A | Fatima Girls | 28.6703 | -13.0919 | Copperbelt | 1.8 | COPPERBELT | Luanshya | No | No | No | Rural | Silver | Silver | BB | BB | On Air | Grid-Gen | Green Field | 50 | Outdoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | perkins | perkins | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 53.067 | 0 | 2 | MTNAirtel | T3290 | ZM6036 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_336A
1282 | ZM6085 | IHS_CBT_338A | Musa Kasonka_3_Rlf | 28.6358 | -12.9988 | Copperbelt | 2.5 | COPPERBELT | Ndola | Yes | No | No | Suburban | Gold | Gold | BTS | BTS | On Air | Grid-Gen | Green Field | 40 | Outdoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 500 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | 0 | N/A | 122 | 0 | 2 | MTNAirtel | T3542 | ZM6085 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_338A
738 | ZM6150 | IHS_CBT_339A | Katuni Eden Institute | 28.4615 | -13.36 | Copperbelt | 1.5 | COPPERBELT | MPongwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 50 | Outdoor | Neddy Chiwasa | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 10 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | 0 | N/A | 81 | 0 | 2 | MTNAirtel | T3363 | ZM6150 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_339A
209 | ZM6202 | IHS_CBT_340A | Chinfunshi Wildlife Orphange | 27.4817 | -12.366 | Copperbelt | 2.5 | COPPERBELT | Chingola | No | No | No | Rural | Silver | Silver |  | BTS | On Air | Solar-Gen | Green Field | 60 | Outdoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | N/A | 0 | 0 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | 0 | N/A | 40.22 | 0 | 1 | Airtel | 0 | ZM6202 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_340A
632 | ZM6675 | IHS_CBT_342A | Kantanta Street | 28.2266 | -12.819 | Copperbelt | 2.5 | COPPERBELT | Kitwe | No | No | No | Urban | Gold | Gold | BTS | BTS | On Air | Grid-Gen | Green Field | 50 | Outdoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 65 | 0 | 1 | Airtel | 0 | ZM6675 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_342A
208 | ZM6763 | IHS_CBT_343A | Chinese Colony | 28.4069 | -13.1266 | Copperbelt | 2.5 | COPPERBELT | Luanshya | No | No | No | Suburban | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Neddy Chiwasa | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | 0 | N/A | 62.38 | 0 | 2 | AirtelAir-link | 0 | ZM6763 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_343A
1475 | ZM6771 | IHS_CBT_344A | Nkwazi 3G | 28.6019 | -12.927 | Copperbelt | 2.5 | COPPERBELT | Ndola | No | No | No | Suburban | Gold | Gold | BTS | HUB | On Air | Grid-Gen | Green Field | 50 | Outdoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | CK Works | CK Works | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 60.6 | 0 | 1 | Airtel | 0 | ZM6771 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_344A
1406 | ZM6773 | IHS_CBT_345A | Ndeke Changachanga south 3G | 28.2474 | -12.8866 | Copperbelt | 2.5 | COPPERBELT | Kitwe | No | No | No | Suburban | Gold | Gold | BTS | BTS | On Air | Grid-Gen | Green Field | 50 | Outdoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 500 | 48 | 100 | 5 | N/A | N/A | N/A | 0 | N/A | 66.804 | 0 | 1 | Airtel | 0 | ZM6773 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_345A
1455 | ZM6950 | IHS_CBT_346A | Nilkant Mine | 28.7701 | -12.9781 | Copperbelt | 2.5 | COPPERBELT | Ndola | No | No | No | Suburban | Silver | Silver | BTS | BTS | On Air | Solar-Gen | Green Field | 50 | Outdoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HA1-C10 | 0 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | 0 | N/A | 42.7 | 41 | 1 | Airtel | 0 | ZM6950 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_346A
1417 | ZM0274 | IHS_CBT_347A | Ndola International Airport | 28.5156 | -12.9711 | Copperbelt | 2.5 | COPPERBELT | NDOLA | No | No | No | Urban | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 35 | Outdoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Vitalgen | Vitalgen | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 82 | 0 | 2 | MTNAirtel | T1173 | ZM0274 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_347A
1549 | ZM0394 | IHS_CBT_348A | Profund Flats | 28.651 | -12.9926 | Copperbelt | 2.5 | COPPERBELT | Ndola | No | No | No | Urban | Silver | Gold | BTS | BTS | On Air | Grid-Gen | Roof Top | RT | Outdoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 69 | 0 | 1 | Airtel | 0 | ZM0394 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_348A
511 | ZM0475 | IHS_CBT_349A | Kafubu Mall | 28.6403 | -12.9799 | Copperbelt | 2 | COPPERBELT | Ndola | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 45 | Outdoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | Gen Logic | Gen Logic | 16 | perkins | 4TNE | Mecc Alte | 0 | 600 | Power cube | ICC330-H1-C1 | 0 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 46 | 0 | 1 | Airtel | 0 | ZM0475 | yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | [11 empty] | n/a | n/a |  | n/a |  |  |  |  | IHS_CBT_349A
1561 | ZM1504 | IHS_CBT_351A | Riverside Congo Way | 28.2359 | -12.7995 | Copperbelt | 2 | COPPERBELT | Kitwe | No | No | No | Urban |  | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 78 |  | 1 | Airtel | 0 | ZM1504 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_CBT_351A
1522 | ZM1500 | IHS_CBT_352A | Parklands TBN | 28.2145 | -12.8055 | Copperbelt | 2.5 | Copperbelt | Kitwe | No | No | No | Urban |  | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 69 |  | 1 | Airtel | 0 | ZM1500 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_CBT_352A
320 | ZM1499 | IHS_CBT_353A | Court Barrifs | 28.1981 | -12.8062 | Copperbelt | 1.8 | COPPERBELT | Kitwe | No | No | No | Urban |  | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 72 |  | 1 | Airtel | 0 | ZM1499 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_CBT_353A
1196 | ZM1501 | IHS_CBT_354A | Mufuchani | 28.2599 | -12.7851 | Copperbelt | 2.5 | Copperbelt | Kitwe | No | No | No | Urban | Gold | Gold | BTS | BTS | On air | Gen Only | Green Field | 50 | Outdoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 81 |  | 1 | Airtel | 0 | ZM1501 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_CBT_354A
1408 | ZM1503 | IHS_CBT_355A | Ndeke Sub. A | 28.2309 | -12.8517 | Copperbelt | 2 | COPPERBELT | Kitwe | No | No | No | Urban | Gold | Gold | BTS | BTS | On air | Gen Only | Green Field | 50 | Outdoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 84 |  | 1 | Airtel | 0 | ZM1503 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_CBT_355A
1442 | ZM1497 | IHS_CBT_356A | New Ndeke Village | 28.2488 | -12.8455 | Copperbelt | 2 | COPPERBELT | Kitwe | No | No | No | Urban |  | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 75 |  | 1 | Airtel | 0 | ZM1497 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_CBT_356A
1736 | ZM1517 | IHS_CBT_358A | Thangata Sec. School | 28.2269 | -12.5505 | Copperbelt | 2.5 | Copperbelt | Mufulira | No | No | No | Urban | Silver | Silver | BTS | BTS | On air | Gen Only | Green Field | 50 | Outdoor | Neddy Chiwasa | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 75 |  | 1 | Airtel | 0 | ZM1517 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_CBT_358A
321 | ZM1526 | IHS_CBT_359A | Cross Crescent | 28.6221 | -12.9648 | Copperbelt | 4.5 | COPPERBELT | Ndola | No | No | No | Urban |  | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 77 |  | 1 | Airtel | 0 | ZM1526 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_CBT_359A
405 | ZM1524 | IHS_CBT_360A | Hilcrest Extension | 28.6208 | -12.9881 | Copperbelt | 5.5 | COPPERBELT | Ndola | No | No | No | Urban |  | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 200 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 81 |  | 1 | Airtel | ZM1524 | ZM1524 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_CBT_360A
1119 | ZM1529 | IHS_CBT_361A | Mitengo TDRC | 28.5985 | -12.9461 | Copperbelt | 2.5 | COPPERBELT | Ndola | No | No | No | Urban |  | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 102 |  | 1 | Airtel | ZM1529 | ZM1529 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_CBT_361A
1413 | ZM1522 | IHS_CBT_362A | Ndola Central Police | 28.6706 | -13.0046 | Copperbelt | 4.5 | COPPERBELT | Ndola | No | No | No | Urban |  | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 110 |  | 1 | Airtel | ZM1522 | ZM1522 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_CBT_362A
1097 | ZM1523 | IHS_CBT_363A | Milemu Sec. School | 28.6374 | -12.9405 | Copperbelt | 2.5 | COPPERBELT | Ndola | No | No | No | Urban |  | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 77 |  | 1 | Airtel | ZM1523 | ZM1523 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_CBT_363A
162 | ZM1527 | IHS_CBT_364A | Chifubu Sec. School | 28.6227 | -17.4754 | Copperbelt | 4.5 | COPPERBELT | Ndola | No | No | No | Urban |  | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Elvis Mumba | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 122 |  | 1 | Airtel | ZM1527 | ZM1527 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_CBT_364A
590 | ZM1470 | IHS_CBT_365A | Kameza East | 27.8544 | -12.3566 | Copperbelt | 2.5 | Copperbelt | Chililabombwe | No | No | No | Urban | Silver | Silver | BTS | BTS | On air | Gen Only | Green Field | 50 | Outdoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 123 |  | 1 | Airtel | 0 | ZM1470 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_CBT_365A
719 | ZM1494 | IHS_CBT_366A | Kasumbalesa Riverside | 27.7897 | -12.2805 | Copperbelt | 2.5 | Copperbelt | Kasumbalesa | No | No | No | Urban | Silver | Silver | BTS | BTS | On air | Gen Only | Green Field | 50 | Outdoor | Panji Njovu | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 165 |  | 1 | Airtel | 0 | ZM1494 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_CBT_366A
409 | ZM1509 | IHS_CBT_367A | Ibenge Girls | 28.4126 | -13.3586 | Copperbelt | 22 | COPPERBELT | Masati | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Neddy Chiwasa | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 90 |  | 1 | Airtel | ZM1509 | ZM1509 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_CBT_367A
402 | ZM1498 |  | Highland Sec School | 28.2308 | -12.8248 | Copperbelt | 2 | COPPERBELT | Kitwe | No | No | No | Urban |  | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Chrispin Lindundu | SBC | SBC | Airtel | Mwenya Banda | GNM | GNM | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 82 |  | 1 | Airtel | 0 | ZM1498 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_CBT_368A
495 | T0009 | IHS_CTR_001M | Kabwe | 28.4453 | -14.4265 | Central | 4.5 | Central | KABWE | No | Yes | No | Urban | 2G 3G | P3 | BB | BB | On Air | Grid-Gen | Green Field | 54 | Indoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Himoinsa | Himoinsa | 30 | Yanmar | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | NARADA | 1200 | 2 | 600 | 48 | Chigo/Energy star | Chigo/Energy star | 18000 | 18000 | 2 | 133 |  | 1 | MTN | T0009 | 0 | Yes |  | working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_001M
500 | T0134 | IHS_CTR_002M | Kabwe Town | 28.4522 | -14.4421 | Central | 2.5 | Central | KABWE | Yes | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On Air | Grid-Gen | Green Field | 42 | Indoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 184 |  | 3 | MTNAirtelLiquid Telecom | T0134 | ZM0382 | Yes |  | working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_002M
1033 | T0279 | IHS_CTR_003M | Masiye Motel (Luangwa West) | 28.4254 | -14.4249 | Central | 1.8 | Central | KABWE | No | No | No | Urban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | GNM | GNM | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 124 |  | 2 | MTNAirtel | T0279 | ZM6853 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_003M
56 | T0129 | IHS_CTR_004M | Bwacha | 28.4405 | -14.4064 | Central | 2.5 | Central | KABWE | No | No | No | Urban | 2G 3G | P2 | BTS | BTS | On Air | Grid-Gen | Green Field | 48 | Indoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | CK Works | CK Works | 20 | perkins | 0 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 18000 | 18000 | 2 | 80 |  | 1 | MTN | T0129 | 0 | Yes |  | working | Clear View | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | yes | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_CTR_004M
1541 | T0274 | IHS_CTR_005M | Pollen | 28.4659 | -14.4418 | Central | 1.8 | Central | KABWE | Yes | No | No | Urban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 15 | perkins | 0 | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 62 |  | 1 | MTN | T0274 | 0 | Yes |  | working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_005M
300 | T0040 | IHS_CTR_006M | Chowa | 28.4442 | -14.4598 | Central | 2.5 | Central | KABWE | No | No | No | Urban | 2G 3G | P2 | BTS | BTS | On Air | Grid-Gen | Green Field | 50 | Indoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | CK Works | CK Works | 20 | perkins | 4TNE88-G1A | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 69.2 |  | 1 | MTN | T0040 | 0 | Yes |  | Not working | Clear View | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_006M
690 | T0133 | IHS_CTR_007M | Kasanda | 28.4659 | -14.4596 | Central | 2.5 | Central | KABWE | No | No | No | Urban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 42 | Indoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 130 |  | 2 | MTNAirtel | T0133 | ZM0233 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | yes | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_CTR_007M
1212 | T0041 | IHS_CTR_008M | Mukobeko | 28.4082 | -14.4094 | Central | 2 | Central | KABWE | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 50 | Indoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88-G1A | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Sonnenschein | 1000 | 2 | 1000 | 24 | LG | LG | 18000 | 18000 | 2 | 55 |  | 1 | MTN | T0041 | 0 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_008M
174 | T0128 | IHS_CTR_011M | Chikusu Kabwe | 28.4574 | -14.3842 | Central | 2.5 | Central | KABWE | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 48 | Indoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | CK Works | CK Works | 20 | perkins | 0 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 18000 | 18000 | 2 | 125 |  | 2 | MTNAirtel | T0128 | ZM6856 | Yes |  | working | Clear View | Inala | 2022-08-05 | Yes | Yes | Nil | 1 |  |  | pending |  | yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_011M
973 | T0127 | IHS_CTR_012M | Makululu | 28.4015 | -14.4477 | Central | 2 | Central | KABWE | No | No | No | Urban | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 48 | Indoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88-G1A | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 400 | 48 | 100 | 4 | L/G/STAR ENERGY | L/G/STAR ENERGY | 18000 | 18000 | 2 | 35 |  | 1 | MTN | T0127 | 0 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Available | Not Collected |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_012M
502 | T0099 | IHS_CTR_013M | Kabwe ZNS | 28.3415 | -14.5301 | Central | 2 | Central | KABWE | No | Yes | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 66 | Outdoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88-G1A | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | 0 | N/A | 36 |  | 1 | MTN | T0099 | 0 | Yes |  | working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_013M
1242 | T0042 | IHS_CTR_014M | Mulungushi | 28.5538 | -14.2803 | Central | 2 | Central | KABWE | No | Yes | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 50 | Indoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88-G1A | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG/ENERGY STAR | LG/ENERGY STAR | 18000 | 18000 | 2 | 35 |  | 1 | MTN | T0042 | 0 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_014M
715 | T0131 | IHS_CTR_015M | Kasosoolo | 28.6499 | -14.4429 | Central | 2.5 | Central | KABWE | No | No | No | Suburban | 2G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 48 | Indoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | Amaron | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 21 |  | 1 | MTN | T0131 | 0 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | Yes | Yes | Nil | 0 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_015M
1218 | T0130 | IHS_CTR_016M | Mukosha | 28.6649 | -14.2936 | Central | 1.8 | Central | KABWE | No | No | No | Suburban | 2G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 48 | Indoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 15 | Yanmar | 4TNE88 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 25 |  | 1 | MTN | T0130 | 0 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_016M
1179 | T0112 | IHS_CTR_017M | Mpunde Mission | 28.2137 | -14.211 | Central | 2 | Central | KABWE | No | No | No | Rural | 2G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 66 | Outdoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 60 |  | 2 | MTNAirtel | T0112 | ZM3751 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_017M
1224 | T0018 | IHS_CTR_018M | Mukumwanji Mountain | 28.2186 | -14.6474 | Central | 2.5 | Central | CHIBOMBO | No | Yes | No | Rural | 2G 3G | P3 | BB | Hub | On Air | Grid-Gen | Green Field | 36 | Indoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | GNM | GNM | 30 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 60 |  | 1 | MTN | T0018 | 0 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 | [5 empty] | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_018M
392 | T3056 | IHS_CTR_019M | Green Leaf | 28.6117 | -14.1269 | Central | 1.8 | Central | KAPIRI | No | Yes | No | Rural | 2G 3G | P4 | HUB | BTS | On Air | Grid-Gen | Green Field | 54 | Indoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 15 | Yanmar | 4TNE88 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | GL/CHIGO | GL/CHIGO | 18000 | 18000 | 2 | 72 |  | 2 | MTNAirtel | T3056 | ZM3506 | Yes |  | working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_019M
168 | T0197 | IHS_CTR_020M | Chikonkomene | 28.3344 | -14.7668 | Central | 1.8 | Central | KABWE | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 70 | Indoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 15 | Yanmar | 4TNE88 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 48 |  | 1 | MTN | T0197 | 0 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_020M
1216 | T0113 | IHS_CTR_021M | Mukonchi | 28.8119 | -14.2636 | Central | 1.8 | Central | KABWE | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 66 | Outdoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | GNM | GNM | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | 0 | N/A | 78.5 |  | 2 | MTNAirtel | T0113 | ZM0692 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_021M
1244 | T0196 | IHS_CTR_022M | Mulungushi Dam | 28.7819 | -14.6956 | Central | 1.8 | Central | KABWE | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 15 | Yanmar | 4TNE88 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 60 |  | 1 | MTN | T0196 | 0 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_022M
259 | T0076 | IHS_CTR_023M | Chisamba/chibombo Turnoff | 28.1058 | -14.6928 | Central | 1.8 | Central | CHIBOMBO | Yes | Yes | No | Rural | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 70 | Indoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 15 | perkins | 0 | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 95 |  | 2 | MTNAirtel | T0076 | ZM6828 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_023M
139 | T0060 | IHS_CTR_024M | Chibombo Boma | 28.0723 | -14.6589 | Central | 2 | Central | CHIBOMBO | No | No | No | Rural | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 80 | Indoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Wolong | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 40 |  | 1 | MTN | T0060 | 0 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_024M
883 | T0123 | IHS_CTR_025M | Lukanga Swamp | 28.0061 | -14.3528 | Central | 2.5 | Central | KABWE | No | No | No | Rural | 2G | P4 | BTS | BTS | On Air | Solar-Gen | Green Field | 66 | Indoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-HI-CI | 333 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 59.9 |  | 2 | MTNAirtel | T0123 | ZM3743 | Yes |  | Not working | Palisade | Netco | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_025M
198 | T0195 | IHS_CTR_026M | Chimanimani | 28.1051 | -14.1134 | Central | 2.5 | Central | KABWE | No | No | No | Rural | 2G | P4 | BTS | BTS | On Air | Solar-Gen | Green Field | 70 | Indoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 750 | Power cube | ICC330-HI-CI | 333 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 18000 | 18000 | 2 | 65 |  | 2 | MTNAirtel | T0195 | ZM1096 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_026M
242 | T0090 | IHS_CTR_027M | Chipembi | 28.5717 | -14.9378 | Lusaka | 2 | Central | CHIBOMBO | No | No | No | Rural | 2G 3G | P4 | BTS | BB | On Air | Grid-Gen | Green Field | 70 | Outdoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88-G1A | Leroy Sommer | LSC 28S2 | 1000 | Power cube | DPR 2400B-48 | 250 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | N/A | N/A | 45 |  | 1 | MTN | T0090 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_027M
26 | T0002 | IHS_CTR_028M | Banani | 28.0568 | -16.5726 | Central | 1.8 | Central | CHIBOMBO | No | Yes | No | Rural | 2G 3G | P3 | HUB | Hub | On Air | Grid-Gen | Green Field | 70 | Indoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 15 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 57 |  | 1 | MTN | T0002 | 0 | Yes |  | working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_028M
666 | T3300 | IHS_CTR_029M | Kapiri Tazara | 28.6896 | -13.949 | Central | 1.5 | Central | KAPIRI | No | No | No | Rural | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 11 | perkins | 0 | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 54 |  | 2 | MTNINQ | T3300 | 0 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_029M
256 | T0030 | IHS_CTR_030M | Chisamba | 28.3785 | -14.981 | Lusaka | 2.5 | Central | CHIBOMBO | No | No | No | Rural | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 50 | Indoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 403A-15 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ECC500 | 750 | Lithium | 400 | 48 | 100 | 4 | GREE | GREE | 12000 | 12000 | 2 | 175 |  | 2 | MTNAirtel | T0030 | ZM3453 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | Yes |  |  | Pending | 20 |  | Pending |  |  |  |  | IHS_CTR_030M
663 | T3034 | IHS_CTR_031M | Kapiri glass factory | 28.6606 | -13.8924 | Central | 1.8 | Central | KAPIRI | No | Yes | No | Rural | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 50 | Indoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 15 | Yanmar | 4TNE88 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 200 | 48 | 100 | 2 | LG | LG | 18000 | 18000 | 2 | 48 |  | 1 | MTN | T3034 | 0 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_031M
802 | T0193 | IHS_CTR_032M | Landless Corner | 28.0588 | -14.8749 | Central | 1.8 | Central | CHIBOMBO | No | Yes | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 15 | Yanmar | 4TNE88 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 200 | 48 | 100 | 2 | LG | LG | 18000 | 18000 | 2 | 36 |  | 1 | MTN | T0193 | 0 | Yes |  | working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_032M
386 | T0032 | IHS_CTR_033M | Golden Valley | 28.0868 | -14.9468 | Lusaka | 2 | Central | CHIBOMBO | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 50 | Indoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88-G1A | Mecc Alte | ECO28-1LN/4 | 1000 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | EVO | EVO | 18000 | 18000 | 2 | 120 |  | 2 | MTNAirtel | T0032 | ZM6827 | NO |  | Working | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_033M
1627 | T0249 | IHS_CTR_034M | Shimukunami | 27.9016 | -14.7675 | Central | 1.8 | Central | CHIBOMBO | No | No | No | Rural | 2G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 70 | Outdoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 15 | Yanmar | 4TNE88-G1A | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | 0 | N/A | 85 |  | 2 | MTNAirtel | T0249 | ZM0994 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_034M
142 | T0094 | IHS_CTR_035M | Chibombo(Fringilla) | 28.1411 | -14.9986 | Lusaka | 2 | Central | CHIBOMBO | No | Yes | No | Rural | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 54 | Outdoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88-G1A | Mecc Alte | ECO28-1LN/4 | 1000 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 45 |  | 3 | MTNLiquid TelecomSmartnet | T0094 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_035M
581 | T0250 | IHS_CTR_036M | Kamaila | 28.2999 | -15.0822 | Lusaka | 2.5 | Central | CHIBOMBO | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Lamasat | Lamasat | 20 | perkins | 403A-15 | Leroy Sommer | LSAP 40H J 6S/4 | 1000 | IPT | DPR 2400B-48 | 250 | Coslight | 400 | 2 | 400 | 24 | N/A | N/A | N/A | N/A | N/A | 45 |  | 1 | MTN | T0250 | 0 | YES |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_036M
258 | T0210 | IHS_CTR_037M | Chisamba Protea | 28.2694 | -15.0747 | Lusaka | n/a | Central | CHIBOMBO | No | No | No | Rural | 2G | P4 | BTS | BB | On Air | Grid-Solar | Green Field | 18 | Outdoor | John Banda | SBC | SBC | MTN | Evans Ngonga | In House | In House | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | MPPT | MPPT | 3.5KW | Exciss | 460 | 12 | 230 | 8 | N/A | N/A | N/A |  | N/A | 25 |  | 1 | MTN | T0210 | 0 |  |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_037M
1411 | T0019 | IHS_CTR_038M | Ndesa | 28.2089 | -15.0627 | Lusaka | 4.5 | Central | CHIBOMBO | No | Yes | No | Rural | 2G 3G | P4 | BB | BB | On Air | Grid-Gen | Green Field | 80 | Indoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | CK Works | CK Works | 30 | perkins | 403A-15 | Leroy Sommer | LSC 28S2 | 1000 | Power cube | ECC500 | 400 | NARADA | 1200 | 2 | 600 | 48 | GREE | GREE | 18000 | 18000 | 2 | 85 |  | 2 | MTNAirtel | T0019 | ZM6826 | NO |  | Working | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 2 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_038M
1318 | T0126 | IHS_CTR_039M | Mwachisompola | 27.9551 | -14.9102 | Central | 2.5 | Central | CHIBOMBO | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 66 | Indoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | Lithium | 200 | 48 | 100 | 2 | LG | LG | 18000 | 18000 | 2 | 79 |  | 2 | MTNAirtel | T0126 | ZM3752 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_039M
1529 | T0021 | IHS_CTR_040M | Penya Onse Farm | 28.4724 | -15.1275 | Lusaka | 1.5 | Central | CHIBOMBO | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | MPMC | MPMC | 13 | perkins | 403A-15 | Leroy Sommer | LSA 40M5 C 6/4 | 1000 | IPT | DPR 2400B-48 | 250 | Power safe | 1200 | 2 | 1200 | 24 | N/A | N/A | N/A | N/A | N/A | 50 |  | 2 | MTNAirtel | T0021 | ZM3715 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_040M
1174 | T3111 | IHS_CTR_041M | Mpula Masanga | 28.9041 | -13.8791 | Central | 2.5 | Central | KAPIRI | No | Yes | No | Rural | 2G 3G | P3 | BB | BTS | On Air | Grid-Gen | Green Field | 54 | Indoor | Linos Thole | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 50 |  | 1 | MTN | T3111 | 0 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_041M
764 | T0061 | IHS_CTR_042M | Kembe | 27.777 | -14.903 | Central | 1.8 | Central | CHIBOMBO | No | No | No | Rural | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 80 | Indoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 15 | perkins | 0 | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 40 |  | 1 | MTN | T0061 | 0 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_042M
1593 | T0044 | IHS_CTR_043M | Savannah Park | 28.2635 | -15.2558 | Lusaka | 4.5 | Central | CHIBOMBO | No | Yes | No | Suburban | 2G 3G | P2 | BTS | BB | On Air | Grid-Gen | Green Field | 50 | Indoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | Yanmar | 4TNE88-G1A | Mecc Alte | ECO28-1LN/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 175 |  | 2 | MTNAirtel | T0044 | ZM3897 | YES |  | Working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | Yes |  |  | Pending | 20 |  | Pending |  |  |  |  | IHS_CTR_043M
351 | T3288 | IHS_CTR_044M | Farm Block West | 29.1567 | -13.8951 | Central | 1.8 | Central | MKUSHI | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Linos Thole | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Green Power | Green Power | 15 | perkins | 0 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 35 |  | 1 | MTN | T3288 | 0 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | Yes | Yes | Nil | 0 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_044M
1733 | T0121 | IHS_CTR_045M | Ten Miles | 28.2836 | -15.3069 | Lusaka | 5.5 | Lusaka | LUSAKA | Yes | No | No | Suburban | 2G 3G 4G | P1 | BTS | BTS | On Air | Grid-Gen | Green Field | 42 | Outdoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 45 | perkins | 404A-22 | Leroy Sommer | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | NARADA | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 190 |  | 4 | MTNAirtelLiquid TelecomAir-link | T0121 | ZM0864 | NO |  | Working | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 2 |  |  | pending |  | No | No | Yes |  |  | Pending | 30 |  | Pending |  |  |  |  | IHS_CTR_045M
287 | T0062 | IHS_CTR_046M | Chiyuni | 27.5947 | -14.7293 | Central | 1.8 | Central | CHIBOMBO | No | No | No | Rural | 2G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 80 | Indoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 15 | perkins | 0 | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | Lithium | 200 | 48 | 100 | 2 | LG | LG | 18000 | 18000 | 2 | 49 |  | 1 | MTN | T0062 | 0 | Yes |  | working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_046M
91 | T0144 | IHS_CTR_047M | Chamba Valley | 28.3309 | -15.3301 | Lusaka | 2.5 | Lusaka | LUSAKA | No | Yes | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | IPT | DPR 2400B-48 | 250 | BSB | 1500 | 2 | 1500 | 24 | LG | LG | 12000 | 12000 | 2 | 100 |  | 2 | MTNAirtel | T0144 | ZM3717 | N0 |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_047M
467 | T0299 | IHS_CTR_048M | Kabangwe | 28.2708 | -15.3302 | Lusaka | 1.5 | Lusaka | LUSAKA | No | No | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 10 | SUZUKI | 403A-15 | Leroy Sommer | LSA 40M5 C 6/4 | 1000 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 70 |  | 1 | MTN | T0299 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_048M
121 | T0262 | IHS_CTR_049M | Chazanga | 28.3054 | -15.3383 | Lusaka | 4.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | CK Works | CK Works | 30 | perkins | 403A-15 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 168 |  | 2 | MTNAirtel | T0262 | ZM6736 | YES |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | Pending | 30 |  | Pending |  |  |  |  | IHS_CTR_049M
460 | T0071 | IHS_CTR_050M | Kabanana | 28.3042 | -15.3522 | Lusaka | 4.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | HUB | HUB | On Air | Grid-Gen | Green Field | 54 | Indoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Vitalgen | Vitalgen | 30 | perkins | 1103A-33 | Leroy Sommer | LSAP 423F | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | GREE | GREE | 12000 | 12000 | 2 | 122 |  | 2 | MTNLiquid Telecom | T0071 | 0 | YES |  | Working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_050M
1798 | T0166 | IHS_CTR_051M | Zani Moune | 28.2797 | -15.3493 | Lusaka | 5.5 | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G | P1 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Indoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | CK Works | CK Works | 45 | perkins | 1103A-33 | Leroy Sommer | TAL 042C J 6/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 300 | 48 | 100 | 3 | CHIGO | CHIGO | 18000 | 18000 | 2 | 231 |  | 2 | MTNAirtel | T0166 | ZM0563 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_051M
1472 | T3075 | IHS_CTR_052M | Nkumbi | 29.0739 | -13.7283 | Central | 1.8 | Central | MKUSHI | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Indoor | Linos Thole | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 15 | perkins | 0 | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 50 |  | 1 | MTN | T3075 | 0 | Yes |  | working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_052M
463 | T0302 | IHS_CTR_053M | Kabanana West | 28.2711 | -15.3558 | Lusaka | 1.8 | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 404A-22 | Leroy Sommer | ECP-28-M/4 | 1000 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 92 |  | 1 | MTN | T0302 | 0 | YES |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_053M
233 | T0233 | IHS_CTR_054M | Chipata Overspill | 28.2883 | -15.3628 | Lusaka | 2.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 404A-22 | Leroy Sommer | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 189 |  | 3 | MTNAirtelLiquid Telecom | T0233 | ZM0118 | YES |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_054M
352 | T3003 | IHS_CTR_055M | Farm Centre | 29.1909 | -13.7831 | Central | 2.5 | Central | MKUSHI | No | No | No | Rural | 2G 3G | P4 | HUB | Hub | On Air | Grid-Gen | Green Field | 60 | Indoor | Linos Thole | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 50 |  | 1 | MTN | T3003 | 0 | Yes |  | working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_055M
362 | T3080 | IHS_CTR_056M | Forest Inn | 29.1521 | -13.7168 | Central | 2.5 | Central | MKUSHI | No | Yes | No | Rural | 2G 3G | P4 | BTS | Hub | On Air | Grid-Gen | Green Field | 54 | Outdoor | Linos Thole | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Lamasat | Lamasat | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 90 |  | 2 | MTNAirtel | T3080 | ZM3955 | Yes |  | working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_056M
1032 | T3231 | IHS_CTR_057M | Masebe farm | 29.2528 | -13.8017 | Central | 1.5 | Central | MKUSHI | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 50 | Outdoor | Linos Thole | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | New way power | New way power | 12.5 | perkins | 0 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 34 |  | 1 | MTN | T3231 | 0 | Yes |  | working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_057M
1031 | T3076 | IHS_CTR_058M | Masansa | 29.3881 | -13.9412 | Central | 1.8 | Central | MKUSHI | No | No | No | Rural | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 42 | Indoor | Linos Thole | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 15 | perkins | 0 | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | Lithium | 200 | 48 | 100 | 2 | LG | LG | 18000 | 18000 | 2 | 50 |  | 1 | MTN | T3076 | 0 | Yes |  | working | Palisade | Inala | 2022-08-05 | No | No | Available | Not Collected |  |  |  |  | yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_058M
1370 | T1054 | IHS_CTR_059M | Namitondwa | 27.5377 | -15.1259 | Lusaka | 2.5 | Central | MUMBWA | No | No | No | Rural | 2G | P4 | BTS | BB | On Air | Solar-Gen | Green Field | 42 | Outdoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Emerson | N/A | 150 | ROLLS | 1410 | 4 | 1500 | 12 | N/A | N/A | N/A | N/A | N/A | 68 |  | 1 | MTN | T1054 | 0 | N0 |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_059M
1228 | T3339 | IHS_CTR_060M | Mukushi Farm Block | 29.3975 | -13.7131 | Central | 2.5 | Central | MKUSHI | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Linos Thole | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 34 |  | 1 | MTN | T3339 | 0 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_060M
1373 | T0091 | IHS_CTR_061M | Nampundwe | 27.9123 | -15.492 | Lusaka | 1.5 | Lusaka | KAFUE | No | No | No | Rural | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 54 | Outdoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 13 | Yanmar | 4TNE88-G1A | Mecc Alte | ECO28-1LN/4 | 1000 | Power cube | ICC330-H1-C1 | N/A (out door unity) | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | N/A | N/A | 90 |  | 2 | MTNAirtel | T0091 | ZM6645 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | Pending | 20 |  | Pending |  |  |  |  | IHS_CTR_061M
1229 | T3013 | IHS_CTR_062M | Mukushi Hill | 29.3686 | -13.6491 | Central | 2.5 | Central | MKUSHI | No | No | No | Rural | 2G 3G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 54 | Indoor | Linos Thole | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Lamasat | Lamasat | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 90 |  | 4 | MTNAirtelLiquid TelecomParatus Telecom | T3013 | ZM1236 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_062M
1227 | T3228 | IHS_CTR_063M | Mukushi Boma | 29.3986 | -13.6165 | Central | 4.5 | Central | MKUSHI | No | Yes | No | Rural | 2G 3G 4G | P3 | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Linos Thole | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 30 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | Lithium | 500 | 48 | 100 | 5 | N/A | N/A | N/A | 0 | N/A | 170 |  | 3 | MTNAirtelLiquid Telecom | T3228 | ZM0392 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Available | Not Collected |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_063M
853 | T3297 | IHS_CTR_064M | Luanshimba ZNS | 29.5614 | -13.6895 | Central | 1.8 | Central | MKUSHI | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Linos Thole | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Lamasat | Lamasat | 15 | perkins | 0 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 34 |  | 1 | MTN | T3297 | 0 | Yes |  | working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_064M
130 | T3059 | IHS_CTR_065M | Chengelo | 29.5928 | -13.6132 | Central | 4.5 | Central | MKUSHI | No | No | No | Rural | 2G 3G | P4 | BB | BB | On Air | Grid-Gen | Green Field | 60 | Indoor | Linos Thole | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Vitalgen | Vitalgen | 30 | perkins | 0 | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | Lithium | 200 | 48 | 100 | 2 | LG | LG | 18000 | 18000 | 2 | 98 |  | 3 | MTNAirtelParatus Telecom | T3059 | ZM3746 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_065M
383 | T1015 | IHS_CTR_066M | Ginery Mumbwa | 27.1913 | -15.117 | Lusaka | 1.8 | Central | MUMBWA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Yanmar | Yanmar | 15 | Yanmar | 4TNE88-G1A | Leroy Sommer | LSC 28S2 | 600 | IPT | DPR 2400B-48 | 500 | Lithium | 600 | 48 | 100 | 6 | N/A | N/A | N/A | N/A | N/A | 58 |  | 1 | MTN | T1015 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_066M
1252 | T1008 | IHS_CTR_067M | Mumbwa | 27.0622 | -14.9826 | Lusaka | 2.5 | Central | MUMBWA | Yes | No | No | Rural | 2G 3G 4G | P1 | BTS | BTS | On Air | Grid-Gen | Green Field | 50 | Indoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 403A-15 | Mecc Alte | ECP 28-1L/4 | 1000 | IPT | DPR 2400B-48 | 250 | Wolong | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 68 |  | 1 | MTN | T1008 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_067M
87 | T3281 | IHS_CTR_068M | Chalata | 29.6863 | -13.5482 | Central | 2 | Central | MKUSHI | No | Yes | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Linos Thole | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 15 | Yanmar | 4TNE88 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | ROLLS | 1410 | 4 | 1410 | 12 | N/A | N/A | N/A | 0 | N/A | 30 |  | 1 | MTN | T3281 | 0 | NO |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_068M
1368 | T1053 | IHS_CTR_069M | Nambala | 27.0036 | -15.1445 | Lusaka | 4.5 | Central | MUMBWA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 48 | Indoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | HIMOINSA | HIMOINSA | 30 | Yanmar | 4TNV98-GGEH | HIMOINSA | S 160 LB | 1000 | IPT | DPR 2400B-48 | 250 | Lithium | 1200 | 48 | 100 | 12 | CHIGO | CHIGO | 18000 | 18000 | 2 | 80 |  | 2 | MTNAirtel | T1053 | ZM3606 | YES |  | No working | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 2 |  |  | Done | 2019-05-28 | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_069M
1401 | T3120 | IHS_CTR_070M | Ndabala | 29.8125 | -13.4767 | Central | 2.5 | Central | MKUSHI | No | Yes | No | Rural | 2G 3G | P4 | BB | BTS | On Air | Grid-Gen | Green Field | 70 | Indoor | Linos Thole | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Lamasat | Lamasat | 20 | perkins | 0 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 50 |  | 1 | MTN | T3120 | 0 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_070M
1352 | T1094 | IHS_CTR_071M | Nakanjoli | 26.7718 | -14.99 | Lusaka | 2.5 | Central | MUMBWA | No | No | No | Rural | 2G | P4 | BTS | BTS | On Air | Solar-Gen | Green Field | 36 | Outdoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | RID | RID | 20 | Mitsubishi | S4L261SDBC | Zanardi | AL 3/4 | 1000 | N/A | N/A | N/A | ROLLS | 1410 | 4 | 1500 | 12 | N/A | N/A | N/A | N/A | N/A | 78 |  | 1 | MTN | T1094 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | Pending | 16 |  | Pending |  |  |  |  | IHS_CTR_071M
1235 | T3115 | IHS_CTR_072M | Mulilima | 29.9488 | -13.341 | Central | 1.8 | Central | SERENJE | No | Yes | No | Rural | 2G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 66 | Outdoor | Linos Thole | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 15 | perkins | 0 | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 35 |  | 1 | MTN | T3115 | 0 | Yes |  | working | Palisade | Inala | 2022-08-05 | Yes | Yes | Nil | 0 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_072M
1606 | T3125 | IHS_CTR_073M | Serenje Hill | 30.1909 | -13.2483 | Central | 2.5 | Central | SERENJE | No | No | No | Rural | 2G | P4 | HUB | BB | On Air | Grid-Gen | Green Field | 54 | Indoor | Linos Thole | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Lamasat | Lamasat | 20 | perkins | 0 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Shoto | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 70 |  | 2 | MTNAirtel | T3125 | ZM3748 | NO |  | working | Palisade | Inala | 2022-08-05 | Yes | Yes | Available | Not Collected |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_073M
1605 | T3060 | IHS_CTR_074M | Serenje | 30.2413 | -13.252 | Central | 1.8 | Central | SERENJE | Yes | Yes | No | Rural | 2G 3G | P4 | BTS | BB | On Air | Grid-Gen | Green Field | 46 | Indoor | Linos Thole | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Falcon | Falcon | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 68 |  | 2 | MTNLiquid Telecom | T3060 | 0 | Yes |  | working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_074M
1527 | T3123 | IHS_CTR_075M | Pensulo | 30.4412 | -13.0346 | Central | 2 | Central | SERENJE | No | Yes | No | Rural | 2G 3G | P4 | BTS | BB | On Air | Grid-Gen | Green Field | 60 | Outdoor | Linos Thole | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Wolong | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 35 |  | 1 | MTN | T3123 | 0 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_075M
737 | T3141 | IHS_CTR_076M | Katunga BB | 30.6056 | -13.0771 | Central | 2 | Central | SERENJE | No | Yes | No | Rural | 2G | P4 | BB | BTS | On Air | Grid-Gen | Green Field | 66 | Indoor | Linos Thole | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 50 |  | 1 | MTN | T3141 | 0 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | Yes | Yes | Nil | 0 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_076M
1280 | T3215 | IHS_CTR_077M | Mupepetwe | 30.7669 | -13.1756 | Central | 1.8 | Central | SERENJE | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Indoor | Linos Thole | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Lamasat | Lamasat | 15 | perkins | 0 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 34 |  | 3 | MTNAirtelTop Star | T3215 | ZM3747 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No | Available | Not Collected |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_077M
1315 | T3130 | IHS_CTR_078M | Muzamaly | 30.7925 | -13.1208 | Central | 2.5 | Central | SERENJE | No | No | No | Rural | 2G | P4 | BB | BB | On Air | Grid-Gen | Green Field | 42 | Outdoor | Linos Thole | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 18000 | N/A | 80 |  | 1 | MTN | T3130 | 0 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_078M
790 | T3172 | IHS_CTR_079M | Kunda | 31.0852 | -13.2137 | Central | 2.5 | Central | SERENJE | No | No | No | Rural | 2G | P4 | BB | BTS | On Air | Solar-Gen | Green Field | 48 | Outdoor | Linos Thole | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | CK Works | CK Works | 20 | perkins | 0 | Zanardi | AL3/3 | 200 | Power cube | ICC330-HI-CI | 250 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | 0 | N/A | 50 |  | 1 | MTN | T3172 | 0 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_079M
1732 | T1073 | IHS_CTR_080M | TBZ Nkeyema | 25.5077 | -14.8975 | Southern | 1.8 | WESTERN | KAOMA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Indoor | Kelvin Simpasa | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | GU51794U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 94 |  | 2 | MTNAirtel | T1073 | ZM3862 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_080M
388 | T3391 | IHS_CTR_081M | GORDON CHANCE FARM | 29.459 | -13.6553 | Central | 1.8 | Central | MKUSHI | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 54 | Outdoor | Linos Thole | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 15 | perkins | 0 | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 34 |  | 1 | MTN | T3391 | 0 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_081M
157 | T3419 | IHS_CTR_082M | CHIEF NKOLE | 28.9102 | -13.7869 | Central | 1.5 | Central | MPOROKOSO | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 54 | Outdoor | Linos Thole | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen City | Gen City | 11 | Yanmar | 3TNE88 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 31 |  | 1 | MTN | T3419 | 0 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_082M
672 | T1117 | IHS_CTR_084M | KAPOKOLA BASIC | 27.1002 | -14.9453 | Lusaka | 1.5 | Central | MUMBWA | No | No | No | Rural | 2G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 54 | Outdoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Generator City | Generator City | 10 | Yanmar | 3TNV88-GGGE | ALPHAGEN | SLG164 | 600 | IPT | DPR 2400B-48 | 250 | Amaron | 400 | 2 | 400 | 24 | N/A | N/A | N/A | N/A | N/A | 40 |  | 1 | MTN | T1117 | 0 | N0 |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_084M
63 | T3390 | IHS_CTR_085M | CAMPBELL FARMS | 29.3184 | -13.814 | Central | 1.5 | Central | MKUSHI | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 54 | Outdoor | Linos Thole | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Gen City | Gen City | 11 | Yanmar | 3TNE88 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 12 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 34 |  | 1 | MTN | T3390 | 0 | Yes |  | working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_085M
153 | T3410 | IHS_CTR_087M | Chief Chibale | 30.1001 | -13.5814 | Central | 1.5 | Central | SERENJE | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 70 | Outdoor | Linos Thole | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | Falcon | Falcon | 13.5 | perkins | 0 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 34 |  | 1 | MTN | T3410 | 0 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_087M
301 | T0407 | IHS_CTR_088M | Chowa basic | 28.5629 | -14.4081 | Central | 1.8 | Central | KABWE | No | No | No | Rural | 2G | P4 | BTS | BTS | On Air | Solar-Gen | Green Field | 54 | Outdoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | GNM | GNM | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Emerson | Netsure 701 | 200 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | 0 | N/A | 30 |  | 2 | MTNAirtel | T0411 | ZM0122 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Available | Not Collected |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_088M
675 | T3453 | IHS_CTR_089M | Kapumba | 29.009 | -14.5607 | Central | 2.5 | Central | KAPIRI | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On Air | Solar-Gen | Green Field | 75 | Outdoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | CK Works | CK Works | 20 | perkins | 0 | Zanardi | AL3/3 | 200 | Power cube | ICC330-HI-CI | 80 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | 0 | N/A | 35 |  | 1 | MTN | T3453 | 0 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Available | Not Collected |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_089M
257 | T0411 | IHS_CTR_090M | Chisamba Mukuyu Farm | 28.3486 | -15.0735 | Lusaka | 2.5 | Central | KABWE | No | No | No | Rural | 2G | P4 | BTS | BTS | On Air | Solar-Gen | Green Field | 55 | Outdoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | GNM | GNM | 20 | perkins | 403A-15 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Emerson | Emmerson/IPT | 250/450 | NARADA | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 95 |  | 1 | MTN | T0407 | 0 | YES |  | Working | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 2 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_090M
826 | T0492 | IHS_CTR_091M | Lisiwasi | 30.6471 | -12.9658 | Central | 2.5 | Central | Mukushi | No | No | No | Rural | P4 | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 70 | Outdoor | Linos Thole | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 40 |  | 1 | MTN | T0492 | 0 | Yes |  | working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_091M
1542 | T0524 | IHS_CTR_093M | Pollen Airtel Share | 28.4718 | -14.431 | Central | 2.5 | Central | kabwe | No | No | No | Rural | P4 | P4 | BTS | BTS | On Air | Grid-Gen | Green Field | 36 | Outdoor | Robert Mwewa | SBC | SBC | MTN | Benson Phiri | GNM | Lithandi | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 49 |  | 1 | MTN | T0524 | 0 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_093M
2 | ZM0015 | IHS_CTR_201A | CHISAMBA | 28.1322 | -14.9959 | Lusaka | 2.5 | Central | Chibombo | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 56 | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | MPI -Perkins | MPI-Perkins | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 600 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 |  | LG | 18000 | 18000 | 2 | 70 |  | 1 | Airtel | 0 | ZM0015 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_201A
5 | ZM0026 | IHS_CTR_202A | Kabwe Main | 28.4463 | -14.4409 | Central | 5.5 | Central | Kabwe | No | No | Yes | Urban | Gold | Gold | BB | BSC | On Air | Grid-Gen | Green Field | 60 | Indoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | CK Works | CK Works | 45 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | Wolong | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 140 |  | 3 | AirtelINQKNC | 0 | ZM0026 | Yes |  | Not working | Clear View | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_202A
6 | ZM0031 | IHS_CTR_203A | KAMAILA | 28.2994 | -15.0825 | Lusaka | 4.5 | Central | Chibombo | No | No | No | Rural | Silver | Silver | BTS | BB/HUB | On Air | Grid-Gen | Green Field | 30 | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 300 | 48 | 100 | 3 | SAMSUNG/LG | SAMSUNG/LG | 18000 | 18000 | 4 | 110 |  | 1 | Airtel | 0 | ZM0031 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_203A
9 | ZM0035 | IHS_CTR_204A | Kapiri Old | 28.6808 | -14.0141 | Central | 4.5 | Central | Kapiri Mposhi | No | No | Yes | Rural | Silver | Silver | BB | BB | On Air | Grid-Gen | Green Field | 64 | Indoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 183 |  | 1 | Airtel | 0 | ZM0035 | Yes |  | working | Mesh | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_204A
10 | ZM0064 | IHS_CTR_205A | Mukumwanji | 28.2215 | -14.6489 | Central | 4.5 | Central | Kabwe | No | No | No | Rural | Silver | Silver | BB | BB | On Air | Grid-Gen | Green Field | 64 | Indoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 80.4 |  | 1 | Airtel | 0 | ZM0064 | Yes |  | Not working | Mesh | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_205A
12 | ZM0108 | IHS_CTR_207A | Mulungushi | 28.5609 | -14.2963 | Central | 2.5 | Central | Kapiri Mposhi | No | No | No | Rural | Silver | Silver | HUB | BTS | On Air | Grid-Gen | Green Field | 54 | Indoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 145 |  | 3 | MTNAirtelLiquid Telecom | T0406 | ZM0108 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_207A
13 | ZM0143 | IHS_CTR_208A | MUMBWA | 27.0633 | -14.9865 | Lusaka | 2.5 | Central | Mumbwa | No | No | No | Rural | Silver | Silver |  | BTS | On Air | Grid-Gen | Green Field | 80 | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 200 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 115 |  | 2 | AirtelKNC | 0 | ZM0143 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_208A
14 | ZM0146 | IHS_CTR_209A | NAMITONDWE | 27.5379 | -15.126 | Lusaka | N/A | Central | Mumbwa | No | No | No | Rural | Silver | Silver | BB | BB | On Air | Solar-Gen | Green Field | 60 | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Power cube | MPPT | 100 | N/a | N/a | N/a | N/a |  | LG | LG | 18000 | 18000 | 2 | 54 |  | 1 | Airtel | 0 | ZM0146 | 0 |  |  | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  | Consolidated on IHS_CTR_059M Namitondwe | IHS_CTR_209A
18 | ZM0147 | IHS_CTR_210A | NANGOMA | 27.3609 | -15.136 | Lusaka | 4.5 | Central | Mumbwa | No | No | No | Rural | Silver | Silver | BTS | BB/HUB | On Air | Grid-Gen | Green Field | 60 | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Lamasat | Lamasat | 30 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 130 |  | 2 | MTNAirtel | T1078 | ZM0147 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_210A
21 | ZM0204 | IHS_CTR_211A | SERENJE | 30.2356 | -13.2357 | Central | 2.5 | Central | Serenje | Yes | No | No | Rural | Silver | Silver | BB | BTS | On Air | Grid-Gen | Green Field | 50 | Indoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 74 |  | 1 | Airtel | 0 | ZM0204 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_211A
27 | ZM0238 | IHS_CTR_212A | Lunsemfwa | 29.1209 | -14.5012 | Central | 1.8 | Central | Kapiri Mposhi | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 80 | Indoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | Agisson | 600 | NA | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 65 |  | 2 | MTNAirtel | T0410 | ZM0238 | Yes |  | working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_212A
28 | ZM0292 | IHS_CTR_213A | LUNSEMFWA REPEATER | 28.9438 | -14.3888 | Central | 1.8 | Central | Kapiri Mposhi | No | No | No | Rural | Silver | Silver | HUB | BTS | On Air | Grid-Gen | Green Field | 70 | Indoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | TPA 48200A | 150 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 57 |  | 1 | Airtel | 0 | ZM0292 | Yes |  | Not working | Palisade | Netco | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_213A
29 | ZM0452 | IHS_CTR_214A | Mansansa | 29.3854 | -13.9426 | Central | 2.5 | Central | Mkushi | No | No | No | Rural | Silver | Silver | BB | BB | On Air | Grid-Gen | Green Field | 60 | Indoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 18000 | 18000 | 2 | 66 |  | 1 | Airtel | 0 | ZM0452 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_214A
30 | ZM0610 | IHS_CTR_215A | Ndabala | 29.7944 | -13.5037 | Central | 1.8 | Central | Mkushi | No | No | No | Rural | Silver | Silver | BB | BB | On Air | Grid-Gen-solar | Green Field | 70 | Indoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ECC 500 | 150 | Agisson | 490 | 48 | 490 | 24 | LG | LG | 18000 | 18000 | 2 | 45 |  | 1 | Airtel | 0 | ZM0610 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_215A
34 | ZM0653 | IHS_CTR_216A | MKUSHI EAST | 29.6424 | -13.6861 | Central | 2.5 | Central | Mkushi | No | No | No | Rural | Silver | Silver | HUB | BTS | On Air | Grid-Gen | Green Field | 60 | Indoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 63 |  | 2 | MTNAirtel | T3311 | ZM0653 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_216A
36 | ZM0676 | IHS_CTR_217A | Mkushi West | 29.1794 | -13.7946 | Central | 2.5 | Central | Mkushi | No | No | No | Rural | Silver | Silver | BB | BB | On Air | Grid-Gen | Green Field | 60 | Indoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 45 |  | 1 | Airtel | 0 | ZM0676 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_217A
40 | ZM0677 | IHS_CTR_218A | Mkushi Town | 29.3991 | -13.6137 | Central | 1.8 | Central | Mkushi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 170 |  | 2 | MTNAirtel | T3334 | ZM0677 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_218A
41 | ZM0679 | IHS_CTR_219A | CHIPEMBI GIRLS | 28.5694 | -14.9172 | Lusaka | 2.5 | Central | Chibombo | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 80 | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Garda | Garda | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 38 |  | 1 | Airtel | 0 | ZM0679 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_219A
42 | ZM0684 | IHS_CTR_220A | CHIBOMBO | 28.049 | -14.789 | Central | 1.8 | Central | Chibombo | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-HI-CI | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 57 |  | 1 | Airtel | 0 | ZM0684 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_220A
54 | ZM0697 | IHS_CTR_222A | MULUNGUSHI DAM | 28.8596 | -14.6955 | Central | 2 | Central | Kapiri Mposhi | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Solar-Gen | Green Field | 70 | Indoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | IMG | IMG | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-HI-CI | 400 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 54 |  | 1 | Airtel | 0 | ZM0697 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | Yes | Yes | Nil | 1 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_222A
57 | ZM0699 | IHS_CTR_223A | CHUNGA | 28.2455 | -15.3603 | Lusaka | 2.5 | Central | Chibombo | No | No | Yes | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 42 | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | IPT | ECC500 | 400 | Lithium | 1600 | 48 | 100 | 16 | FM25000 | FM25000 | 25000 | 25000 | 2 | 85 |  | 1 | Airtel | 0 | ZM0699 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_223A
65 | ZM0700 | IHS_CTR_224A | MATERO GIRLS | 28.2514 | -15.3761 | Lusaka | 2 | Central | Chibombo | No | No | Yes | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 30 | Outdoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | LG18000 | N/A | 86 |  | 1 | Airtel | 0 | ZM0700 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_224A
72 | ZM0709 | IHS_CTR_225A | HIGHRIDGE | 28.4636 | -14.4537 | Central | 2.5 | Central | Kabwe | No | No | Yes | Suburban | Gold | Gold | HUB | BTS | On air | Grid-Gen | Green Field | 48 | Indoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 98 |  | 1 | Airtel | 0 | ZM0709 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_225A
76 | ZM0710 | IHS_CTR_226A | BWACHA | 28.4452 | -14.4041 | Central | 2.5 | Central | Kabwe | No | No | No | Urban | Gold | Gold | HUB | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 80 |  | 1 | Airtel | 0 | ZM0710 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_226A
77 | ZM0736 | IHS_CTR_227A | Pensulo | 30.4318 | -13.0074 | Central | 2.5 | Central | Serenje | No | No | Yes | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 80 | Indoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Lamasat | Lamasat | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-HI-CI | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 76 |  | 1 | Airtel | 0 | ZM0736 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_227A
79 | ZM0751 | IHS_CTR_228A | LUKOMBA | 28.9024 | -13.8794 | Central | 4.5 | Central | Kapiri Mposhi | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 50 | Indoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 50 |  | 1 | Airtel | 0 | ZM0751 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_228A
80 | ZM0758 | IHS_CTR_229A | CHITAMBO | 30.6369 | -12.9166 | Central | 2 | Central | Serenje | No | No | No | Rural | Silver | Silver | BB | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 63 |  | 2 | MTNAirtel | T3454 | ZM0758 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_229A
83 | ZM0782 | IHS_CTR_230A | KABANANA WEST | 28.285 | -15.3456 | Lusaka | 2.5 | Central | Chibombo | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404D-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 88 |  | 1 | Airtel | 0 | ZM0782 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_230A
85 | ZM0837 | IHS_CTR_231A | NKUMBI | 29.0753 | -13.7275 | Central | 1.8 | Central | Mkushi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Lamasat | Lamasat | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-HI-CI | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 50 |  | 1 | Airtel | 0 | ZM0837 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_231A
88 | ZM0878 | IHS_CTR_233A | LANDLESS CORNER | 28.0285 | -14.8905 | Central | 1.8 | Central | Chibombo | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | 0 | N/A | 47 |  | 1 | Airtel | 0 | ZM0878 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_233A
89 | ZM0881 | IHS_CTR_234A | KAPIRI GLASS PRODUCT | 28.6494 | -13.8779 | Central | 1.8 | Central | Kapiri Mposhi | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 75 |  | 2 | MTNAirtel | T3338 | ZM0881 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_234A
92 | ZM0909 | IHS_CTR_235A | Muchimupati | 30.0939 | -13.2716 | Central | 2.5 | Central | Serenje | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 70 | Indoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 43 |  | 1 | Airtel | 0 | ZM0909 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_235A
93 | ZM0910 | IHS_CTR_236A | Mulilima | 29.9221 | -13.3573 | Central | 2 | Central | Serenje | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ECC 500 | 150 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 45 |  | 1 | Airtel | 0 | ZM0910 | Yes |  | Not working | Palisade | Netco | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_236A
131 | ZM0916 | IHS_CTR_237A | MAKULULU | 28.4308 | -14.4451 | Central | 4.5 | Central | Kabwe | No | Yes | Yes | Urban | Gold | Gold | HUB | HUB | On air | Grid-Gen | Green Field | 36 | Indoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | CK Works | CK Works | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 137 |  | 2 | MTNAirtel | T0216 | ZM0916 | Yes |  | working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_237A
138 | ZM3020 | IHS_CTR_238A | CHUNGA DAMS | 28.2532 | -15.3641 | Lusaka | 2.5 | Central | Chibombo | No | No | No | Urban | Platinum | Platinum | BB | BB | On air | Grid-Gen | Green Field | 36 | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Vitalgen | Vitalgen | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 155 |  | 2 | MTNAirtel | T0478 | ZM3020 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_238A
140 | ZM3167 | IHS_CTR_239A | KALENDE HILL | 26.9011 | -14.7365 | Lusaka | 2.5 | Central | Mumbwa | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 60 | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | CK Works | CK Works | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 68 |  | 2 | MTNAirtel | T3529 | ZM3167 | 0 |  |  | Palisade | Netco | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_239A
141 | ZM3168 | IHS_CTR_240A | CHITANDA | 27.732 | -14.8992 | Central | 1.8 | Central | Chibombo | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Grid-Gen | Green Field | 80 | Outdoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | GNM | GNM | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-HI-CI | 400 | Agisson | 1200 | 2 | 600 | 48 | 0 | 0 | N/A | 0 | 0 | 56 |  | 1 | Airtel | 0 | ZM3168 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_240A
169 | ZM3220 | IHS_CTR_241A | Kapiri Town | 28.6777 | -13.9687 | Central | 4.5 | Central | Kapiri Mposhi | Yes | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 194 |  | 3 | MTNAirtelLiquid Telecom | T3538 | ZM3220 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_241A
170 | ZM3222 | IHS_CTR_242A | MWALALA | 28.4467 | -14.4196 | Central | 1.8 | Central | Kabwe | No | No | Yes | Urban | Gold | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | GNM | GNM | 30 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-HI-CI | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 140 |  | 2 | MTNAirtel | T3541 | ZM3222 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_242A
173 | ZM3224 | IHS_CTR_243A | POLENI | 28.4649 | -14.4417 | Central | 4.5 | Central | Kabwe | Yes | No | Yes | Urban | Gold | Gold | HUB | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 30 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-HI-CI | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 122 |  | 3 | AirtelLiquid TelecomParatus Telecom | 0 | ZM3224 | Yes |  | working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_243A
203 | ZM3246 | IHS_CTR_244A | KABWE ZNS | 28.3505 | -14.5268 | Central | 1.8 | Central | Kabwe | No | No | No | Suburban | Silver | Silver | HUB | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | GNM | GNM | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-HI-CI | 400 | Lithium | 200 | 48 | 100 | 2 | LG | LG | 18000 | 18000 | 2 | 45 |  | 1 | Airtel | 0 | ZM3246 | Yes |  | Not working | Clear View | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_244A
271 | ZM3348 | IHS_CTR_245A | Kohima | 28.4892 | -14.3988 | Central | 2.5 | Central | Kabwe | Yes | Yes | No | Urban | Gold | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Vitalgen | Vitalgen | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 18000 | 18000 | 2 | 125 |  | 2 | MTNAirtel | T0012 | ZM3348 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_245A
272 | ZM3349 | IHS_CTR_246A | Mukobeko | 28.3947 | -14.388 | Central | 2.5 | Central | Kabwe | No | No | No | Suburban | Gold | Gold | HUB | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 95 |  | 2 | MTNAirtel | T0521 | ZM3349 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_246A
361 | ZM3384 | IHS_CTR_247A | RENEKAS | 28.4398 | -14.445 | Central | 2.5 | Central | Kabwe | No | Yes | No | Urban | Gold | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | GNM | GNM | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-HI-CI | 400 | Agisson | 1200 | 2 | 600 | 48 | LG/ENEGR STAR | LG/ENEGR STAR | 18000 | 18000 | 2 | 136 |  | 2 | MTNAirtel | T0358 | ZM3384 | Yes |  | Not working | Clear View | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_247A
401 | ZM3394 | IHS_CTR_248A | Chibombo Cov Imp | 28.076 | -14.6663 | Central | 1.8 | Central | Chibombo | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | GNM | GNM | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-HI-CI | 400 | Lithium | 200 | 48 | 100 | 2 | LG | LG | 18000 | 18000 | 2 | 52 |  | 1 | Airtel | 0 | ZM3394 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_248A
403 | ZM3422 | IHS_CTR_249A | High Ridge_3RLF ( Railways Market) | 28.4478 | -14.4581 | Central | 4.5 | Central | Kabwe | No | No | No | Urban | Gold | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 30 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-HI-CI | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 134 |  | 2 | MTNAirtel | T0479 | ZM3422 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_249A
425 | ZM3423 | IHS_CTR_250A | New Mkushi Mine | 29.149 | -13.9544 | Central | 2.5 | Central | Mkushi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Lamasat | Lamasat | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-HI-CI | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 18000 | N/A | 70 |  | 2 | MTNAirtel | T3232 | ZM3423 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_250A
434 | ZM3452 | IHS_CTR_251A | Protea New | 28.2089 | -15.1238 | Lusaka | 4.5 | Central | Chibombo | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 58 | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | CK Works | CK Works | 30 | perkins | 403A-15 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 135 |  | 2 | MTNAirtel | T0527 | ZM3452 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_CTR_251A
459 | ZM3521 | IHS_CTR_252A | KABANANA WEST-3-RLF | 28.2741 | -15.3534 | Lusaka | 2 | Central | Chibombo | No | No | Yes | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 404A-22 | Leroy Sommer | ECO-28-M/4 | 600 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 112 |  | 1 | Airtel | 0 | ZM3521 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_252A
496 | ZM3571 | IHS_CTR_253A | CHIKUPILI | 29.2421 | -14.0756 | Central | 2.5 | Central | Mkushi | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Solar-Gen | Green Field | 80 | Outdoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | CK Works | CK Works | 20 | perkins | 0 | 0 | 0 | 1000 | Power cube | ICC330-HI-CI | 200 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | 0 | N/A | 68 |  | 2 | MTNAirtel | T3517 | ZM3571 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | Yes | Yes | Nil | 2 |  |  | pending |  | No | Yes | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_CTR_253A
497 | ZM3620 | IHS_CTR_254A | OLD MKUSHI | 29.3546 | -14.3482 | Central | 2.5 | Central | Mkushi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 80 | Outdoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 150 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | 0 | N/A | 65 |  | 2 | MTNAirtel | T3502 | ZM3620 | Yes |  | Not working | Palisade | Netco | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_254A
498 | ZM3701 | IHS_CTR_255A | Mpima Prison | 28.4861 | -14.4361 | Central | 2.5 | Central | Chibombo | No | No | No | Rural | Gold | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 108 |  | 2 | MTNAirtel | T0111 | ZM3701 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | Yes |  |  | No | 20 |  | Pending |  |  |  |  | IHS_CTR_255A
499 | ZM3702 | IHS_CTR_256A | Kabwe West Kabwe Trades | 28.4124 | -14.4183 | Central | 1.8 | Central | Kabwe | No | No | No | Urban | Gold | Gold | HUB | BTS | On air | Grid-Gen | Green Field | 40 | Outdoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | GNM | GNM | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-HI-CI | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 65 |  | 1 | Airtel | 0 | ZM3702 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_256A
501 | ZM3712 | IHS_CTR_257A | Shikatende | 27.7226 | -15.4476 | Lusaka | 2.5 | Central | Mumbwa | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | CK Works | CK Works | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 89 |  | 2 | MTNAirtel | T1095 | ZM3712 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_257A
503 | ZM3737 | IHS_CTR_258A | MUKOBEKO AREA Kabwe Dar Farms | 28.3401 | -14.3506 | Central | 1.8 | Central | Kabwe | No | No | No | Suburban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 34 |  | 0 |  | 0 | 0 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_258A
558 | ZM3738 | IHS_CTR_259A | FIWILA MISSION | 29.6145 | -13.9547 | Central | 2.5 | Central | Mkushi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 0 | Lithium | 500 | 48 | 100 | 5 | N/A | N/A | N/A | 0 | N/A | 78 |  | 2 | MTNAirtel | T3504 | ZM3738 | Yes |  | Not working | Mesh | Netco | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_259A
579 | ZM3739 | IHS_CTR_260A | ST. PAULS MISSION | 28.6171 | -14.3326 | Central | 2.5 | Central | Kapiri Mposhi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 63 |  | 2 | MTNAirtel | T3455 | ZM3739 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_260A
662 | ZM3740 | IHS_CTR_261A | MWEMBESHI FARMS | 27.9093 | -15.2119 | Lusaka | 2.5 | Central | Chibombo | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 50 | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | R4850N2 | R4850N2 | 55 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 54 |  | 2 | MTNAirtel | T0456 | ZM3740 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_261A
664 | ZM3741 | IHS_CTR_262A | NGWERERE_3 | 28.2443 | -15.1715 | Lusaka | 2.5 | Central | Chibombo | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Vitalgen | Vitalgen | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 120 |  | 2 | MTNAirtel | T0412 | ZM3741 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_262A
665 | ZM3742 | IHS_CTR_263A | KASAVASA | 28.4051 | -14.5882 | Central | 2 | Central | Kabwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Metco | Metco | 17 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 56 |  | 3 | MTNAirtelParatus Telecom | T3387 | ZM3742 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_263A
667 | ZM3744 | IHS_CTR_264A | KUNDA | 31.0843 | -13.2324 | Central | 2.5 | Central | Serenje | No | No | No | Rural | Silver | Silver | BB | BTS | On air | Solar-Gen | Green Field | 66 | Outdoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Lamasat | Lamasat | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | TPA 48200A | 150 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 60 |  | 1 | Airtel | 0 | ZM3744 | Yes |  | Not working | Mesh | Netco | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_264A
693 | ZM3745 | IHS_CTR_265A | KALUNGA BB | 30.6054 | -13.077 | Central | 2 | Central | Serenje | No | No | No | Rural | Silver | Silver | BB | BTS | On air | Grid-Gen | Green Field | 54 | Outdoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Metco | Metco | 17 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 18000 | N/A | 65 |  | 1 | Airtel | 0 | ZM3745 | Yes |  | Not working | Mesh | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_265A
717 | ZM3753 | IHS_CTR_266A | Chibombo Chiyuni (Chitanda Clinic) | 27.5926 | -14.637 | Central | 1.8 | Central | Chibombo | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Metco | Metco | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | Agisson | 1200 | 2 | 600 | 48 | 0 | 0 | N/A | 0 | 0 | 54 |  | 1 | Airtel | 0 | ZM3753 | Yes |  | Not working | Mesh | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_266A
736 | ZM3754 | IHS_CTR_267A | Ginnery | 27.1895 | -15.1217 | Lusaka | 1.8 | Central | Mumbwa | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 52 | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | MPMC | Gen Logic | 15 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | R4850N2 | R4850N2 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 78 |  | 1 | Airtel | 0 | ZM3754 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_267A
782 | ZM3755 | IHS_CTR_268A | Kabwe Kapiri Hi | 28.5734 | -14.2239 | Central | 1.8 | Central | Kapiri Mposhi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | GNM | GNM | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-HI-CI | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 75 |  | 2 | MTNAirtel | T0409 | ZM3755 | Yes |  | Not working | Mesh | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_268A
791 | ZM3844 | IHS_CTR_269A | Nalusanga | 26.7114 | -14.9708 | Lusaka | 2.5 | Central | Mumbwa | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 60 | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | CK Works | CK Works | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | MPPT | MPPT | 187.5 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 79 |  | 2 | MTNAirtel | T3522 | ZM3844 | 0 |  |  | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_CTR_269A
803 | ZM3885 | IHS_CTR_270A | MUMBWA BHP_Exploration | 26.9389 | -15.0432 | Lusaka | 2.5 | Central | Mumbwa | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 54 | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Zanardi | AL 3/4 | 1000 | MPPT | MPPT | 187.5 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 76 |  | 2 | MTNAirtel | T3519 | ZM3885 | 0 |  |  | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_270A
852 | ZM3886 | IHS_CTR_271A | MACHIYA | 27.822 | -13.5854 | Copperbelt | 2 | Central | Kapiri Mposhi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Neddy Chiwasa | SBC | SBC | Airtel | Mwenya Banda | GNM | Lithandi | RID | RID | 16 | Mitsubishi | SL40 | Zanardi | 0 | 600 | Emerson | 701 IG4 | 300 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | 0 | N/A | 43.7383 | 0 | 2 | MTNAirtel | T3528 | ZM3886 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_271A
875 | ZM3888 | IHS_CTR_272A | Nakanjoli (MUMBWA 2_6) | 26.7669 | -15.1252 | Lusaka | 2.5 | Central | Mumbwa | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 54 | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 1103A-33 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 1200 | 48 | 100 | 12 | N/A | N/A | N/A | N/A | N/A | 85 |  | 2 | MTNAirtel | T3512 | ZM3888 | 0 |  |  | Palisade | Netco | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_272A
880 | ZM3891 | IHS_CTR_273A | MAKULULU-3 RLF David Ramusho | 28.4128 | -14.4533 | Central | 2.5 | Central | Kabwe | No | No | No | Urban | Gold | Gold | HUB | BTS | On air | Grid-Gen | Green Field | 40 | Outdoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 95 |  | 2 | MTNAirtel | T0522 | ZM3891 | Yes |  | Not working | Clear View | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_273A
881 | ZM3894 | IHS_CTR_274A | Zani Munone | 28.2741 | -15.3385 | Lusaka | 4.5 | Central | Chibombo | Yes | No | No | Urban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 188 |  | 3 | MTNAirtelLiquid Telecom | T0324 | ZM3894 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_274A
885 | ZM3953 | IHS_CTR_275A | Serenje_Town1 | 30.3814 | -13.1075 | Central | 2.5 | Central | Serenje | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 150 | Lithium | 600 | 48 | 100 | 6 | N/A | N/A | N/A | 0 | N/A | 78 |  | 2 | MTNAirtel | T3531 | ZM3953 | Yes |  | Not working | Palisade | Netco | 2022-08-05 | No | No | Available | Not Collected |  |  |  |  | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_275A
911 | ZM3954 | IHS_CTR_276A | Serenje_Town2 | 30.2348 | -13.2171 | Central | 2 | Central | Serenje | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 65 | Outdoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Metco | Metco | 17 | perkins | 0 | Leroy Sommer | 0 | 1000 | Emerson | Netsure 701 | 200 | ROLLS | 1410 | 4 | 1410 | 12 | N/A | N/A | N/A | 0 | N/A | 50 |  | 2 | MTNAirtel | T3451 | ZM3954 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_276A
912 | ZM4002 | IHS_CTR_277A | Chengelo Kasalamakanga (CHENGELO AREA_1) | 29.4795 | -13.5951 | Central | 2.5 | Central | Mkushi | No | No | Yes | Rural | Silver | Silver | BB | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-HI-CI | 80 | Lithium | 600 | 48 | 100 | 6 | N/A | N/A | N/A | 0 | N/A | 78 |  | 1 | Airtel | 0 | ZM4002 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_CTR_277A
914 | ZM4003 | IHS_CTR_278A | KABAMBA | 30.3165 | -13.2044 | Central | 2.5 | Central | Serenje | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 70 | Outdoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-HI-CI | 80 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | 0 | N/A | 50 |  | 1 | Airtel | 0 | ZM4003 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_278A
942 | ZM4004 | IHS_CTR_279A | MKUSHI ZNS | 29.5589 | -13.7035 | Central | 1.8 | Central | Mkushi | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 60 | Outdoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 150 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 53 |  | 1 | Airtel | 0 | ZM4004 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_279A
974 | ZM4005 | IHS_CTR_280A | Katuba (Airtel_ZM0245) | 29.2277 | -13.6897 | Central | 1.5 | Central | Mkushi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 11 | Yanmar | 3TNE88 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 150 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 64 |  | 3 | MTNAirtelParatus Telecom | T3283 | ZM4005 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_280A
975 | ZM4006 | IHS_CTR_281A | Chalata (ZAIN_ZM0246) | 29.6863 | -13.5486 | Central | 1.8 | Central | Mkushi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Lamasat | Lamasat | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-HI-CI | 150 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 40 |  | 1 | Airtel | 0 | ZM4006 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_281A
976 | ZM6004 | IHS_CTR_282A | Ipongo | 27.3194 | -14.6044 | Central | 1.8 | Central | Chibombo | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Lamasat | Lamasat | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ECC 500 | 150 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | 0 | N/A | 51 |  | 1 | Airtel | 0 | ZM6004 | Yes |  | Not working | Palisade | Netco | 2022-08-05 | Yes | Yes | Nil | 0 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_282A
985 | ZM6006 | IHS_CTR_283A | Kalola | 27.8333 | -15.0833 | Central | 2 | Central | Chibombo | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | IMG | IMG | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | TPA 48200A | 150 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | 0 | N/A | 68 |  | 2 | MTNAirtel | T0453 | ZM6006 | Yes |  | Not working | Mesh | Netco | 2022-08-05 | Yes | Yes | Nil | 1 |  |  | pending |  | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_283A
1006 | ZM6026 | IHS_CTR_284A | Chikonkomene Railway Station | 28.3677 | -14.7614 | Central | 1.8 | Central | Chibombo | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | TPA 48200A | 150 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 59 |  | 1 | Airtel | 0 | ZM6026 | Yes |  | Not working | Mesh | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_284A
1023 | ZM6027 | IHS_CTR_285A | Chikonkomene | 28.5525 | -14.7023 | Central | 2.5 | Central | Chibombo | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | TPA 48200A | 150 | Lithium | 500 | 48 | 100 | 5 | N/A | N/A | N/A | 0 | N/A | 75 |  | 2 | MTNAirtel | T0450 | ZM6027 | Yes |  | Not working | Palisade | Netco | 2022-08-05 | No | No | Available | Not Collected |  |  |  |  | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_285A
1120 | ZM6042 | IHS_CTR_286A | Muchabi Agic station | 27.2833 | -15.45 | Lusaka | 1.8 | Central | Mumbwa | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 70 | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | RID | RID | 15 | Mitsubishi | S4L261SDBC | Zanardi | AL 3/4 | 1000 | MPPT | MPPT | 187.5 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 84 |  | 2 | MTNAirtel | T3507 | ZM6042 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_286A
1121 | ZM6078 | IHS_CTR_287A | Mungule (Ngwerere Area) | 28.15 | -15.2167 | Lusaka | 1.8 | Central | Chibombo | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 85 |  | 2 | MTNAirtel | T0424 | ZM6078 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_287A
1122 | ZM6084 | IHS_CTR_288A | Matero Oddys_1_Rlf | 28.2647 | -15.373 | Lusaka | 2.5 | Central | Chibombo | No | No | Yes | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 30 | Outdoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Lamasat | lamasat | 20 | Yanmar | 404A-22 | Leroy Sommer | ECO-28-M/4 | 600 | Power cube | ECC500 | 400 | NARADA | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | LG18000 | N/A | 158 |  | 2 | MTNAirtel | T0499 | ZM6084 | 0 |  |  | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 2 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_288A
1123 | ZM6099 | IHS_CTR_289A | Chimupati RP | 30.2211 | -13.1575 | Central | 1.8 | Central | Serenje | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | TPA 48200A | 150 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | 0 | N/A | 45.5 |  | 2 | MTNAirtel | TX | ZM6099 | Yes |  | Not working | Mesh | Netco | 2022-08-05 | Yes | Yes | Nil | 2 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_289A
1165 | ZM6113 | IHS_CTR_290A | Nsansa Hill (replaces MUSHUKULA) | 30.4351 | -12.7338 | Central | 1.8 | Central | Serenje | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 70 | Outdoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Lamasat | Lamasat | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | TPA 48200A | 150 | Agisson | 490 | 2 | 490 | 24 | N/A | N/A | N/A | 0 | N/A | 50.2 |  | 2 | MTNAirtel | T3452 | ZM6113 | Yes |  | Not working | Clear View | Netco | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_290A
1194 | ZM6335 | IHS_CTR_291A | Lukanga Farm | 28.3074 | -14.4269 | Central | 2.5 | Central | Kabwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 60 |  | 2 | MTNAirtel | T0359 | ZM6335 | Yes |  | Not working | Mesh | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_291A
1213 | ZM6370 | IHS_CTR_292A | KAPOPO | 28.1902 | -15.2482 | Lusaka | 2.5 | Central | Chibombo | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Earth Technology | Earth technology | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 375 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 54.7 |  | 1 | Airtel | 0 | ZM6370 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_292A
1214 | ZM6387 | IHS_CTR_293A | Wile Chulu | 30.4 | -12.85 | Central | 1.5 | Central | Serenje | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 70 | Outdoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | TPA 48200A | 150 | Agisson | 980 | 2 | 490 | 48 | N/A | N/A | N/A | 0 | N/A | 35 |  | 1 | Airtel | T3510 | ZM6387 | Yes |  | Not working | Mesh | Netco | 2022-08-05 | Yes | Yes | Nil | 1 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_293A
1223 | ZM6451 | IHS_CTR_294A | Nambwa | 27.3352 | -14.9682 | Lusaka | 1.8 | Central | Mumbwa | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 50 | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 15 | Mitsubishi | S4L261SDBC | Zanardi | AL 3/4 | 1000 | Power cube | MPPT | 187.5 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 70 |  | 2 | MTNAirtel | T3506 | ZM6451 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_294A
1236 | ZM6469 | IHS_CTR_295A | TBZ 2 | 25.9738 | -14.9647 | Lusaka | 2.5 | Central | Mumbwa | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 50 | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | HPS2000-TL | 50 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 85 |  | 2 | MTNAirtel | T3514 | ZM6469 | 0 |  |  | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_295A
1243 | ZM6518 | IHS_CTR_296A | NANSENGA REP | 26.4368 | -14.9715 | Lusaka | 2.5 | Central | Mumbwa | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | HPS2000-TL | 50 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 84 |  | 3 | MTNAirtelMusekese | T3513 | ZM6518 | 0 |  |  | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_296A
1245 | ZM6803 | IHS_CTR_297A | Luangwa township 3G | 28.4327 | -14.4312 | Central | 2.5 | Central | Kabwe | Yes | No | Yes | Urban | Gold | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 60 |  | 2 | AirtelLiquid Telecom | 0 | ZM6803 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_297A
1320 | ZM0235 | IHS_CTR_298A | LUOMBA FARMING BLOCK | 29.8774 | -13.0964 | Central | 1.8 | Central | Chisamba | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 41 |  | 1 | Airtel | 0 | ZM0235 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | No | No | Nil | 0 |  |  |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_298A
1393 | ZM6664 | IHS_CTR_299A | MARANATHA IN KABWE | 28.474 | -14.4133 | Central | 1.8 | Central | Kabwe | No | No | No | Urban | Gold | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 55 | Outdoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Emerson | Netsure 701 | 200 | Sonnenschein | 1000 | 2 | 1000 | 24 | N/A | N/A | N/A | 0 | N/A | 85 |  | 1 | Airtel | 0 | ZM6664 | Yes |  | Not working | Palisade | Inala | 2022-08-05 | Yes | Yes | Nil | 0 |  |  | pending |  | yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_CTR_299A
1402 | ZM0468 | IHS_CTR_300A | St. Edmund School (Kabobe) (Katala) | 27.0556 | -15.0017 | Lusaka | 2.5 | Lusaka | Mumbwa | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404D-22 | Mecc Alte | ECO-28-M/4 | 1000 | Emerson | R483200 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 78 |  | 1 | Airtel | 0 | ZM0468 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_CTR_300A
1440 | ZM0483 | IHS_CTR_301A | St. Joseph-Chitaba | 28.3466 | -14.0619 | Central | 2.5 | Central | Kabwe | No | No | No | Rural |  | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 70 | Outdoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HI-CI | 400 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 50 |  | 1 | Airtel | 0 | ZM0483 | Yes |  | N/A | Palisade | Inala | 2022-08-05 | 0 |  | Nil | 0 | [17 empty] | IHS_CTR_301A
1470 | ZM0485 | IHS_CTR_302A | Imansa School | 28.4123 | -14.1562 | Central | 2.5 | Central | Kabwe | No | No | No | Rural |  | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | 0 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 50 |  | 1 | Airtel | 0 | ZM0485 | Yes |  | N/A | Palisade | Inala | 2022-08-05 | 0 |  | Nil | 0 | [17 empty] | IHS_CTR_302A
1473 | ZM1484 | IHS_CTR_303A | Lukanga Kabwe | 28.4587 | -14.4265 | Central | 1.8 | Central | Kabwe | No | No | No | Urban |  | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Robert Mwewa | SBC | SBC | Airtel | Mwenya Banda | GNM | Lithandi | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 82 |  | 1 | Airtel | 0 | ZM1484 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_CTR_303A
1485 | ZM1483 | IHS_CTR_304A | Luchi Lodge | 28.4436 | -14.4342 | Central | 2.5 | Central | Kabwe | No | No | No | Urban |  | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 85 |  | 1 | Airtel | ZM1492 | ZM1483 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_CTR_304A
1513 | ZM1486 | IHS_CTR_305A | Nkrumah Extension | 28.4771 | -14.4426 | Central | 2.5 | Central | Kabwe | No | No | No | Urban |  | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 78 |  | 1 | Airtel | ZM1491 | ZM1486 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_CTR_305A
1528 | ZM1485 | IHS_CTR_306A | Natuseko | 28.4637 | -14.4036 | Central | 2.5 | Central | Kabwe | No | No | No | Urban |  | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 80 |  | 1 | Airtel | ZM1495 | ZM1485 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_CTR_306A
1540 | ZM1482 | IHS_CTR_307A | Kabwe Bankers | 28.4578 | -14.4469 | Central | 2.5 | Central | Kabwe | No | No | No | Urban |  | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 73 |  | 1 | Airtel | ZM1471 | ZM1482 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_CTR_307A
1556 | ZM1481 | IHS_CTR_308A | Kabwe Aerodrome | 28.4519 | -14.471 | Central | 2.5 | Central | Kabwe | No | No | No | Urban |  | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 82 |  | 1 | Airtel | ZM1483 | ZM1481 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_CTR_308A
1604 | ZM1480 | IHS_CTR_309A | Makululu Moomba | 28.4211 | -14.449 | Central | 2.5 | Central | Kabwe | No | No | No | Urban |  | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 80 |  | 1 | Airtel | ZM1502 | ZM1480 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_CTR_309A
1607 | ZM1531 | IHS_CTR_310A | Serenje Zambia Compound | 30.2444 | -13.2674 | Central | 4.5 | Central | Serenje | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 78 |  | 1 | Airtel | ZM1530 | ZM1531 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_CTR_310A
1608 | ZM1391 | IHS_CTR_311A | Malwita Primary School | 30.2451 | -13.2676 | Central | 2.5 | Central | Serenje | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Linos Thole | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 64 |  | 1 | Airtel | ZM1531 | ZM1391 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_CTR_311A
1609 | ZM1519 | IHS_CTR_312A | Mumbwa Sec. School | 27.0585 | -14.9752 | Lusaka | 2.5 | Lusaka | Mumbwa | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 64 |  | 1 | Airtel | ZM1481 | ZM1519 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_CTR_312A
1705 | ZM1518 | IHS_CTR_313A | Makasa Pri. School | 23.1373 | -15.2572 | Lusaka | 2.5 | Lusaka | Mumbwa | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 62 |  | 1 | Airtel | ZM1482 | ZM1518 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_CTR_313A
1709 | ZM1490 | IHS_CTR_314A | Kapiri Ndeke | 28.6906 | -13.9695 | Central | 2.5 | Central | Kapiri_Mposhi | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | perkins | CK Works | 15 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 74 |  | 1 | Airtel | ZM1518 | ZM1490 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_CTR_314A
1779 | ZM1392 | IHS_CTR_315A | Kasukwe | 28.0804 | -14.7242 | central | 2.5 | central | Chibombo | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Robert Mwewa | SBC | SBC | Airtel | Benson Phiri | GNM | Lithandi | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 84 |  | 1 | Airtel | ZM1392 | ZM1392 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_CTR_315A
231 | T2048 | IHS_EST_001M | Chipata Industries | 32.6264 | -13.6295 | Eastern | 1.5 | EASTERN | CHIPATA | Yes | No | No | Urban | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | Huawei | Hauwei | 14 | Weichai | 0 | Xingnuo | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 1200 | 2 | 600 | 48 | NA | 0 | N/A | NA | 0 | 79 |  | 2 | MTNLiquid Telecom | T2048 | 0 | Yes |  | working | Palisade | inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_001M
226 | T2000 | IHS_EST_002M | Chipata | 32.6253 | -13.644 | Eastern | 4.5 | EASTERN | CHIPATA | Yes | Yes | No | Urban | 2G 3G 4G | P1 | BB | BB | On air | Grid-Gen | Green Field | 48 | Indoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | Vitalgen | Vitalgen | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 140 |  | 2 | MTNParatus Telecom | T2000 | 0 | Yes |  | working | Palisade | inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_002M
735 | T2035 | IHS_EST_003M | Katopola | 32.6371 | -13.6163 | Eastern | 1.8 | EASTERN | CHIPATA | No | No | No | Urban | 2G 3G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 48 | Indoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 15 | Yanmar | 0 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 107 |  | 1 | MTN | T2035 | 0 | Yes |  | working | Palisade | inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_003M
1698 | T2049 | IHS_EST_004M | ST Paul Anglican | 32.6481 | -13.6419 | Eastern | 1.5 | EASTERN | CHIPATA | Yes | No | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 32 | Outdoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | Huawei | Hauwei | 14 | Weichai | 0 | Xingnuo | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | NA | 0 | N/A | NA | 0 | 83 |  | 2 | MTNLiquid Telecom | T2049 | 0 | Yes |  | working | Clear View | inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_004M
1501 | T2026 | IHS_EST_005M | Nyakutwa Hill | 32.624 | -13.5743 | Eastern | 2.5 | EASTERN | CHIPATA | No | No | No | Suburban | 2G 3G | P4 | BTS | BB | On air | Grid-Gen | Green Field | 54 | Indoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | Earth Technology | Earth technology | 20 | perkins | 0 | Leroy Sommer | 0 | 375 | Delta | DPS 2400B-48-5 | 250 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 46 |  | 1 | MTN | T2026 | 0 | Yes |  | working | Palisade | inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_005M
387 | T2003 | IHS_EST_006M | Gonda | 32.5918 | -13.5551 | Eastern | 1.8 | EASTERN | CHIPATA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 46 | Indoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 15 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Power safe | 1200 | 2 | 1200 | 24 | LG | LG | 18000 | 18000 | 2 | 84 |  | 2 | MTNAirtel | T2003 | ZM3873 | Yes |  | not working | Palisade | inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_006M
1190 | T2059 | IHS_EST_007M | Mtengulen | 32.5027 | -13.7011 | Eastern | 1.8 | EASTERN | CHIPATA | No | No | No | Suburban | 2G 3G | P4 | BTS | Hub | On air | Grid-Gen | Green Field | 60 | Outdoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 0 | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 1200 | 2 | 600 | 48 | NA | 0 | N/A | NA | 0 | 91 |  | 2 | MTNAirtel | T2059 | ZM6873 | Yes |  | working | Palisade | inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_007M
225 | T2010 | IHS_EST_008M | Chipalamba BB | 32.4729 | -13.5725 | Eastern | 2.5 | EASTERN | CHIPATA | No | No | No | Suburban | 2G 3G | P4 | BB | BB | On air | Grid-Gen | Green Field | 54 | Indoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | Earth Technology | Earth technology | 20 | perkins | 0 | Leroy Sommer | 0 | 375 | Power cube | ICC330-H1-C1 | 400 | ROLLS | 1410 | 4 | 1410 | 12 | LG | LG | 18000 | 18000 | 2 | 82 |  | 2 | MTNAirtel | T2010 | ZM3825 | Yes |  | working | Palisade | inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_008M
1322 | T2005 | IHS_EST_009M | Mwami | 32.7798 | -13.7368 | Eastern | 1.8 | EASTERN | CHIPATA | No | No | No | Rural | 2G 3G | P4 | BTS | BB | On air | Grid-Gen | Green Field | 46 | Indoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 15 | Yanmar | 0 | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | Wolong | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 45 |  | 1 | MTN | T2005 | 0 | Yes |  | working | Palisade | inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_009M
945 | T2054 | IHS_EST_010M | Madzmawe | 32.4144 | -13.7089 | Eastern | 1.5 | EASTERN | CHIPATA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 70 | Outdoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | MPI | MPI | 13 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 1200 | 2 | 600 | 48 | NA | 0 | N/A | NA | 0 | 67 |  | 1 | MTN | T2054 | 0 | Yes |  | not working | Palisade | inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_010M
1441 | T2023 | IHS_EST_011M | New Mwami | 32.7632 | -13.8161 | Eastern | 2.5 | EASTERN | CHIPATA | No | No | No | Rural | 2G 3G | P4 | BTS | HUB | On air | Grid-Gen | Green Field | 54 | Outdoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 375 | Delta | DPS 2400B-48-5 | 250 | ROLLS | 1410 | 4 | 1410 | 12 | NA | 0 | N/A | NA | 0 | 84 |  | 2 | MTNAirtel | T2023 | ZM6201 | Yes |  | working | Palisade | inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_011M
164 | T2053 | IHS_EST_012M | Chikando | 32.4628 | -13.8442 | Eastern | 1.5 | EASTERN | CHIPATA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | MPI | MPI | 13 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Power safe | 1200 | 2 | 1200 | 24 | NA | 0 | N/A | NA | 0 | 42 |  | 1 | MTN | T2053 | 0 | Yes |  | working | Clear View | inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_012M
1706 | T2033 | IHS_EST_013M | St. Margret BB | 32.8203 | -13.4098 | Eastern | 1.8 | EASTERN | CHIPATA | No | No | No | Suburban | 2G 3G | P4 | HIUB | BTS | On air | Grid-Gen | Green Field | 48 | Outdoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | Elcos | Elcos | 15 | perkins | 0 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | ROLLS | 1410 | 4 | 1410 | 12 | NA | 0 | N/A | NA | 0 | 44 |  | 1 | MTN | T2033 | 0 | Yes |  | working | Palisade | inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_013M
1375 | T2038 | IHS_EST_014M | Namsumba BB | 32.3358 | -13.4407 | Eastern | 2.5 | EASTERN | CHIPATA | No | No | No | Rural | 2G 3G | P4 | BB | BTS | On air | Solar-Gen | Green Field | 54 | Indoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | GNM | GNM | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | MPPT | Shelf 19" Cordex 3.6KW | 250 | Power safe | 1200 | 2 | 1200 | 24 | LG | LG | 12000 | 12000 | 2 | 110 |  | 2 | MTNAirtel | T2038 | ZM6602 | Yes |  | working | Palisade | inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_014M
151 | T2036 | IHS_EST_015M | Chichele BB | 32.2841 | -13.922 | Eastern | 2.5 | EASTERN | KATETE | No | No | No | Rural | 2G 3G | P4 | BB | BTS | On air | Grid-Gen | Green Field | 70 | Indoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 60 |  | 1 | MTN | T2036 | 0 | Yes |  | working | Palisade | inala | 2022-08-05 | No | Yes |  |  |  |  | Done |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_015M
109 | T2029 | IHS_EST_016M | Chankandwe(Vubwi) | 32.9541 | -13.9448 | Eastern | 2.5 | EASTERN | CHADIZA | No | No | No | Rural | 2G | P4 | BTS | BTS | On air | Solar-Gen | Green Field | 54 | Outdoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Emerson | Shelf 19" Cordex 3.6KW | 250 | Wolong | 1200 | 2 | 600 | 48 | NA | 0 | N/A |  | 0 | 96 |  | 2 | MTNAirtel | T2029 | ZM6872 | Yes |  | not working | Palisade | inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | Yes |  |  | no | 20 |  | Pending |  |  |  |  | IHS_EST_016M
73 | T2007 | IHS_EST_017M | Chadiza | 32.4359 | -14.0628 | Eastern | 1.8 | EASTERN | CHADIZA | Yes | No | No | Rural | 2G 3G | P4 | BTS | Hub | On air | Grid-Gen | Green Field | 46 | Indoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 0 | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 46 |  | 1 | MTN | T2007 | 0 | Yes |  | working | Palisade | inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_017M
1772 | T2006 | IHS_EST_018M | Vubwi | 32.8817 | -14.0284 | Eastern | 2.5 | EASTERN | CHAMA | No | No | No | Rural | 2G 3G | P4 | BTS | BB | On air | Grid-Gen | Green Field | 70 | Indoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | Ghaddar | Ghaddar | 20 | perkins | 0 | Leroy Sommer | 0 | 750 | Emerson | Shelf 19" Cordex 3.6KW | 250 | ROLLS | 1410 | 4 | 1410 | 12 | LG | LG | 18000 | 18000 | 2 | 80 |  | 2 | MTNAirtel | T2006 | ZM6154 | Yes |  | not working | Palisade | inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_018M
1427 | T2024 | IHS_EST_019M | New Bwarrow BB | 32.8986 | -13.2239 | Eastern | NA | EASTERN | CHIPATA | No | No | No | Rural | 2G 3G | P3 | BB | BB | On air | Solar-Gen | Green Field | 54 | Indoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | NA | 0 | NA | NA | 0 | 0 | 0 | 750 | Power cube | Shelf 19" Cordex 3.6KW | 250 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 12000 | 12000 | 2 | 52 |  | 1 | MTN | T2024 | 0 | Yes |  | working | Palisade | inala | 2022-08-05 | Yes | Yes |  |  |  |  | Done |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  | Consolidated on IHS_EST_22A | IHS_EST_019M
1773 | T2040 | IHS_EST_020M | Walubwe Hill | 32.1324 | -13.9524 | Eastern | 1.8 | EASTERN | KATETE | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Outdoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 15 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Power safe | 1200 | 2 | 1200 | 24 | NA | 0 | N/A | NA | 0 | 76 |  | 2 | MTNAirtel | T2040 | ZM0729 | Yes |  | working | Palisade | inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_020M
989 | T2009 | IHS_EST_021M | Mambwe | 32.0953 | -13.2939 | Eastern | 1.8 | EASTERN | MAMBWE | Yes | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 66 | Indoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | Elcos | Elcos | 15 | perkins | 0 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Shoto | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 47 |  | 1 | MTN | T2009 | 0 | Yes |  | not working | Palisade | inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_021M
1146 | T2014 | IHS_EST_022M | Mpata Hill | 32.0088 | -13.3244 | Eastern | 1.8 | EASTERN | MAMBWE | No | No | No | Rural | 2G | P4 | BB | BB | On air | Grid-Gen | Green Field | 54 | Indoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 0 | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 73 |  | 1 | MTN | T2014 | 0 | Yes |  | working | Palisade | inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_022M
730 | T2062 | IHS_EST_023M | Katete Junction | 32.059 | -14.0301 | Eastern | 2.5 | EASTERN | KATETE | No | No | No | Rural | 2G 3G | P2 | BTS | Hub | On air | Grid-Gen | Green Field | 60 | Outdoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | ROLLS | 1410 | 4 | 1410 | 12 | NA | 0 | N/A | NA | 0 | 98 |  | 2 | MTNAirtel | T2062 | ZM3709 | Yes |  | working | Palisade | inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_023M
726 | T2002 | IHS_EST_024M | Katete | 32.0962 | -14.0809 | Eastern | 4.5 | EASTERN | KATETE | No | No | No | Rural | 2G 3G | P2 | BB | BB | On air | Grid-Gen | Green Field | 44 | Indoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | CK Works | CK Works | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 108 |  | 1 | MTN | T2002 | 0 | Yes |  | working | Palisade | inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_024M
107 | T2008 | IHS_EST_025M | Chanida Border | 32.347 | -14.2961 | Eastern | 1.8 | EASTERN | PETAUKE | Yes | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 80 | Outdoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | Power safe | 1200 | 2 | 1200 | 24 | NA | 0 | N/A | NA | 0 | 95 |  | 3 | MTNAirtelParatus Telecom | T2008 | ZM6498 | Yes |  | not working | Palisade | inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_025M
1703 | T2061 | IHS_EST_026M | St. Frances | 32.0162 | -14.0663 | Eastern | 1.5 | EASTERN | KATETE | No | No | No | Rural | 2G 3G | P4 | BTS | Hub | On air | Grid-Gen | Green Field | 36 | Outdoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 10 | perkins | 0 | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 1200 | 2 | 600 | 48 | NA | 0 | N/A | NA | 0 | 110 |  | 2 | MTNAirtel | T2061 | ZM4001 | Yes |  | working | Palisade | inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_026M
1084 | T2013 | IHS_EST_027M | Mfuwe int. Airport | 31.9336 | -13.2539 | Eastern | 1.8 | EASTERN | MAMBWE | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 20 | Indoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 0 | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | Power safe | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 56 |  | 1 | MTN | T2013 | 0 | Yes |  | not working | Palisade | inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_027M
1083 | T2012 | IHS_EST_028M | Mfuwe Cropping | 31.8098 | -13.1061 | Eastern | 1.8 | EASTERN | MAMBWE | No | No | No | Rural | 2G 3G | P3 | BB | BTS | On air | Grid-Gen | Green Field | 54 | Indoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | Wolong | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 107 |  | 3 | MTNAirtelParatus Telecom | T2012 | ZM6024 | Yes |  | working | Palisade | inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_028M
1758 | T2044 | IHS_EST_029M | Ukwimi | 31.6504 | -13.8897 | Eastern | 2 | EASTERN | PETAUKE | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 80 | Outdoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 1200 | 2 | 600 | 48 | NA | 0 | N/A | NA | 0 | 106 |  | 1 | MTN | T2044 | 0 | Yes |  | working | Palisade | inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | Pending | 20 |  | Pending |  |  |  |  | IHS_EST_029M
1663 | T2011 | IHS_EST_030M | Sinda | 31.7662 | -14.22 | Eastern | 2.5 | EASTERN | PETAUKE | No | No | No | Rural | 2G 3G | P3 | BB | BB | On air | Grid-Gen | Green Field | 70 | Indoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | Earth Technology | Earth technology | 20 | perkins | 0 | Leroy Sommer | 0 | 375 | Delta | DPS 2400B-48-5 | 250 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 98 |  | 1 | MTN | T2011 | 0 | Yes |  | working | Palisade | inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_030M
1502 | T2027 | IHS_EST_031M | Nyanje | 31.7981 | -14.3803 | Eastern | 1.8 | EASTERN | PETAUKE | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Outdoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 15 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Wolong | 600 | 2 | 600 | 24 | NA | 0 | N/A | NA | 0 | 35 |  | 1 | MTN | T2027 | 0 | Yes |  | not working | Palisade | inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_031M
893 | T2052 | IHS_EST_032M | Lumezi | 33.0448 | -12.5284 | Eastern | 1.5 | EASTERN | LUNDAZI | No | No | No | Rural | 2G 3G | P4 | BTS | Hub | On air | Grid-Gen | Green Field | 70 | Outdoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 11 | perkins | 0 | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | ROLLS | 1410 | 4 | 1410 | 12 | NA | 0 | N/A | NA | 0 | 75 |  | 1 | MTN | T2052 | 0 | Yes |  | not working | Palisade | inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_032M
1075 | T2022 | IHS_EST_033M | Mbwindi BB | 31.5631 | -14.3084 | Eastern | 1.8 | EASTERN | PETAUKE | No | No | No | Rural | 2G 3G | P3 | BB | BB | On air | Grid-Gen | Green Field | 70 | Indoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 66 |  | 1 | MTN | T2022 | 0 | Yes |  | working | Palisade | inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_033M
1494 | T2063 | IHS_EST_034M | Nthitimila | 33.1322 | -12.4249 | Eastern | 1.5 | EASTERN | LUNDAZI | No | No | No | Rural | 2G | P4 | BB | Hub | On air | Grid-Gen | Green Field | 60 | Outdoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | MPI | MPI | 13 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | ROLLS | 1410 | 4 | 1410 | 12 | NA | 0 | N/A | NA | 0 | 38 |  | 1 | MTN | T2063 | 0 | Yes |  |  | Palisade | inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_034M
1530 | T2001 | IHS_EST_035M | Petauke | 31.3283 | -14.2496 | Eastern | 4.5 | EASTERN | PETAUKE | Yes | No | No | Rural | 2G 3G | P1 | BTS | BB | On air | Grid-Gen | Green Field | 66 | Indoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | CK Works | CK Works | 30 | perkins | 0 | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 110 |  | 1 | MTN | T2001 | 0 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_035M
907 | T2004 | IHS_EST_036M | Lundazi | 33.1744 | -12.2933 | Eastern | 1.8 | EASTERN | LUNDAZI | Yes | No | No | Rural | 2G 3G | P2 | BTS | BB | On air | Grid-Gen | Green Field | 66 | Indoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 0 | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | Wolong | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 98 |  | 1 | MTN | T2004 | 0 | yes |  | working | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_036M
1534 | T2045 | IHS_EST_037M | Petauke Junction | 31.3355 | -14.2955 | Eastern | 1.5 | EASTERN | PETAUKE | No | No | No | Rural | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | MPI | MPI | 13 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | ROLLS | 1410 | 4 | 1410 | 12 | NA | 0 | N/A |  | 0 | 112 |  | 1 | MTN | T2045 | 0 | yes |  | not working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_037M
254 | T2037 | IHS_EST_039M | Chisakasa BB | 31.0981 | -14.44 | Eastern | 1.8 | EASTERN | PETAUKE | No | No | No | Rural | 2G | P4 | BB | BTS | On air | Grid-Gen | Green Field | 54 | Indoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 51 |  | 1 | MTN | T2037 | 0 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_039M
1508 | T2030 | IHS_EST_040M | Nyimba town | 30.8314 | -14.5575 | Eastern | 2.5 | EASTERN | NYIMBA | Yes | No | No | Rural | 2G 3G | P3 | BB | BTS | On air | Grid-Gen | Green Field | 70 | Indoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | Vital Gen | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 89 |  | 2 | MTNSmartnet | T2030 | 0 | yes |  | working | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_040M
505 | T2016 | IHS_EST_041M | Kacholola | 30.6724 | -14.7579 | Lusaka | N/A | EASTERN | NYIMBA | No | No | No | Rural | 2G 3G | P4 | BB | BB | On air | Solar-Gen | Green Field | 70 | Indoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/a | Power cube | ICC330-HA1-C10 | 600 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 45 |  | 1 | MTN | T2016 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  | consolidated on IHS_EST_219A Kacholola | IHS_EST_041M
1621 | T2032 | IHS_EST_042M | Shi Bwalya | 30.5354 | -14.838 | Lusaka | N/A | Lusaka | LUANGWA | No | No | No | Rural | 2G | P4 | BB | BB | On air | Solar-Gen | Green Field | 54 | Indoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/a | Cordex | Cordex | 200 | Wolong | 600 | 2 | 600 | 24 | GREE | GREE | 12000 | 12000 | 2 | 45 |  | 1 | MTN | T2032 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  | Consolidated on IHS_EST_220A Shi bwalya | IHS_EST_042M
851 | T2039 | IHS_EST_043M | Luangwa Saulo | 30.2937 | -14.9374 | Lusaka | 2.5 | Lusaka | LUANGWA | No | No | No | Rural | 2G | P4 | BTS | BTS | On air | Solar-Gen | Green Field | 54 | Outdoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | CK Works | CK Works | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Emerson | Cordex | 200 | ROLLS | 1410 | 4 | 1500 | 12 | N/A | N/A | N/A | N/A | N/A | 37 |  | 1 | MTN | T2039 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | yes - Emergency | 20 | 43655 | closed |  |  |  |  | IHS_EST_043M
741 | T2069 | IHS_EST_044M | kaulembe | 32.7321 | -13.479 | Eastern | 1.5 | EASTERN | CHIPATA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 55 | Outdoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | MPI | MPI | 10 | perkins | 0 | Leroy Sommer | LSA 40M5 J M/4 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | NA | 0 | N/A |  | 0 | 80 |  | 2 | MTNAirtel | T2069 | ZM0165 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_044M
1536 | T2082 | IHS_EST_045M | Petauke Rlf | 31.3261 | -14.242 | Eastern | 1.8 | EASTERN | CHIPATA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 55 | Outdoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | MPI | MPI | 15 | perkins | 0 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | NA | 0 | N/A |  | 0 | 63 |  | 1 | MTN | T2082 | 0 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_045M
728 | T2094 | IHS_EST_046M | Katete CBD | 32.0429 | -14.0653 | Eastern | 2.5 | EASTERN | Katete | Yes | No | No | Suburban | P4 | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | AL3/4 | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 800 | 2 | 800 | 24 | NA | 0 | N/A |  | 0 | 135 |  | 2 | MTNAirtel | T2091 | ZM0480 | No |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_046M
744 | T2093 | IHS_EST_047M | Kavulamukoko | 31.9201 | -14.1154 | Eastern | 1.8 | EASTERN | Kavulamukoko | No | No | No | Rural | P4 | P4 | BTS | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | CK Works | CK Works | 15 | perkins |  |  |  | 1000 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | NA | 0 | N/A | NA | 0 | 86 |  | 2 | MTNAirtel | T2093 | ZM6601 | yes |  | working | Palisade | inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_047M
227 | ZM0013 | IHS_EST_201A | CHIPATA | 32.6257 | -13.6443 | Eastern | 4.5 | EASTERN | Chipata | Yes | No | No | Urban | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 50 | Indoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | BSB | 1500 | 2 | 1500 | 24 | LG | LG | 18000 | 18000 | 2 | 210 |  | 1 | Airtel | 0 | ZM0013 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_201A
152 | ZM0116 | IHS_EST_202A | CHICHELE VILLAGE | 32.2859 | -13.9395 | Eastern | 4.5 | EASTERN | Chipata | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 60 | Indoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 82 |  | 1 | Airtel | 0 | ZM0116 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_202A
727 | ZM0120 | IHS_EST_203A | KATETE | 32.0963 | -14.0813 | Eastern | 4.5 | EASTERN | Katete | No | No | No | Rural | Silver | Silver | BB | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | CK Works | CK Works | 30 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 164 |  | 2 | AirtelMphangwe | 0 | ZM0120 | yes |  | not working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_203A
1076 | ZM0125 | IHS_EST_204A | MCHINJI/MWAMI | 32.7934 | -13.7442 | Eastern | 2.5 | EASTERN | Chipata | Yes | No | No | Rural | Silver | Silver | HUB | BTS | On air | Grid-Gen | Green Field | 80 | Indoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Earth Technology | Earth technology | 20 | perkins | 0 | Leroy Sommer | 0 | 375 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 57 |  | 1 | Airtel | 0 | ZM0125 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_204A
1082 | ZM0126 | IHS_EST_205A | MFUWE AIRPORT | 31.9337 | -13.254 | Eastern | 1.8 | EASTERN | Mambwe | Yes | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Roof Top | RT | Indoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | IMG | IMG | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Amaron | 600 | 2 | 400 | 24 | LG | LG | 18000 | 18000 | 2 | 71 |  | 1 | Airtel | 0 | ZM0126 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_205A
1531 | ZM0133 | IHS_EST_206A | PETAUKE | 31.3289 | -14.2507 | Eastern | 4.5 | EASTERN | Nyimba | Yes | No | No | Rural | Silver | Silver | BB | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 142 |  | 1 | Airtel | 0 | ZM0133 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_206A
1664 | ZM0138 | IHS_EST_207A | SINDA | 31.7665 | -14.2164 | Eastern | 2 | EASTERN | Katete | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 61 |  | 1 | Airtel | 0 | ZM0138 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_207A
90 | ZM0173 | IHS_EST_208A | CHAMA | 33.151 | -11.2145 | Eastern | 2.5 | EASTERN | Chama | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 138 |  | 2 | MTNAirtel | T2041 | ZM0173 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_208A
74 | ZM0175 | IHS_EST_209A | CHADIZA | 32.5632 | -13.9471 | Eastern | 2.5 | EASTERN | Chipata | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 54 |  | 1 | Airtel | 0 | ZM0175 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_209A
908 | ZM0187 | IHS_EST_210A | LUNDAZI | 33.1775 | -12.2939 | Eastern | 2.5 | EASTERN | Lundazi | Yes | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 50 | Indoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 135 |  | 2 | AirtelLiquid Telecom | 0 | ZM0187 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_210A
990 | ZM0193 | IHS_EST_211A | MAMBWE | 32.1081 | -13.3019 | Eastern | 2.5 | EASTERN | Mambwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | IMG | IMG | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 42 |  | 1 | Airtel | 0 | ZM0193 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_211A
1208 | ZM0260 | IHS_EST_212A | MUGUBUDU | 32.8203 | -13.4095 | Eastern | 0 | EASTERN | Chipata | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | NA | NA | 0 | NA | 0 | NA | 0 | 0 | NA | NA | NA | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 44 |  | 1 | Airtel | 0 | ZM0260 | yes |  | not working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_212A
1324 | ZM0264 | IHS_EST_213A | MWAMI MISSION | 32.7446 | -13.7879 | Eastern | 4.5 | EASTERN | Chipata | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | CK Works | CK Works | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 98 |  | 2 | MTNAirtel | T2088 | ZM0264 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_213A
1495 | ZM0323 | IHS_EST_214A | NTHITIMILA | 33.2175 | -12.5453 | Eastern | 4.5 | EASTERN | Lundazi | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 60 | Indoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | CK Works | CK Works | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Emerson | ICC330-H1-C1 | 400 | BSB | 1500 | 2 | 1500 | 24 | LG | LG | 12000 | 12000 | 2 | 63 |  | 2 | MTNAirtel | T2079 | ZM0323 | yes |  |  | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_214A
894 | ZM0327 | IHS_EST_215A | LUMEZI | 33.0849 | -12.5366 | Eastern | 2.5 | EASTERN | Lundazi | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 60 | Indoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | GNM | GNM | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 68 |  | 2 | MTNAirtel | T2083 | ZM0327 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_215A
1166 | ZM0332 | IHS_EST_216A | MPONDA | 32.9335 | -12.7743 | Eastern | 2.5 | EASTERN | Lundazi | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 60 | Indoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | CK Works | CK Works | 20 | 0 | 0 | 0 | 0 | 600 | Emerson | EPC48200/2900-HC1 | 250 | Lithium | 600 | 48 | 100 | 6 | LG | LG | 18000 | 18000 | 2 | 102 |  | 2 | MTNAirtel | T2058 | ZM0332 | yes |  | working | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_EST_216A
115 | ZM0444 | IHS_EST_217A | LUANGWA CATHOLIC Unyanya) | 30.3054 | -14.9314 | Lusaka | 2.5 | EASTERN | Petauke | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 66 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | HPS2000-TL | 100 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 38 |  | 1 | Airtel | 0 | ZM0444 | 0 |  |  | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_217A
1158 | ZM0602 | IHS_EST_218A | MPHATA HILL | 32.0087 | -13.3242 | Eastern | 2.5 | EASTERN | Mambwe | No | No | No | Rural | Silver | Silver | BB | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 52 |  | 1 | Airtel | 0 | ZM0602 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_218A
118 | ZM0606 | IHS_EST_219A | KACHOLOLA | 30.6724 | -14.7581 | Lusaka | 4.5 | EASTERN | Petauke | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 66 | Indoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Vitalgen | Vitalgen | 45 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 18000 | 18000 | 2 | 87 |  | 1 | Airtel | 0 | ZM0606 | 0 |  |  | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | yes | 30 |  | Pending |  |  |  |  | IHS_EST_219A
119 | ZM0607 | IHS_EST_220A | SIWALYA | 30.5353 | -14.8376 | Lusaka | 4.5 | EASTERN | Petauke | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 64 | Indoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Vitalgen | Vitalgen | 45 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 76.9 |  | 1 | Airtel | 0 | ZM0607 | 0 |  |  | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_EST_220A
1500 | ZM0693 | IHS_EST_221A | NYAKUTWA | 32.6241 | -13.5743 | Eastern | 2 | EASTERN | Chipata | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 50 | Indoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 16 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 43 |  | 1 | Airtel | 0 | ZM0693 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_221A
1426 | ZM0694 | IHS_EST_222A | NEW BWALO | 32.8982 | -13.2239 | Eastern | 4.5 | EASTERN | Lundazi | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 50 | Indoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 0 | Leroy Sommer | 0 | N/A | Emerson | 701 IG4 | 250 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 74 |  | 1 | Airtel | 0 | ZM0694 | yes |  | working | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_222A
156 | ZM0833 | IHS_EST_224A | CHIEF MWASE | 33.3364 | -12.4102 | Eastern | 2.5 | EASTERN | Lundazi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | IMG | IMG | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 71 |  | 2 | MTNAirtel | T2072 | ZM0833 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_224A
154 | ZM0834 | IHS_EST_225A | CHIEF MAGODI | 33.1382 | -11.98 | Eastern | 2.5 | EASTERN | Lundazi | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 60 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | AL3/4 | 600 | MPPT | 0 | 0 | Lithium | 500 | 48 | 100 | 5 | NA | 0 | N/A |  | 0 | 112 |  | 2 | MTNAirtel | T2047 | ZM0834 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_225A
946 | ZM0835 | IHS_EST_226A | MAGODI REPEATER | 33.1626 | -12.0988 | Eastern | 2 | EASTERN | Lundazi | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 70 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 16 | perkins | 0 | Mecc Alte | 0 | 1000 | Emerson | ICC330-H1-C1 | 250 | Agisson | 600 | 2 | 600 | 24 | LG | 0 | N/A |  | 0 | 106 |  | 2 | MTNAirtel | T2076 | ZM0835 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_226A
236 | ZM0836 | IHS_EST_227A | CHIPATA SHOPRITE | 32.6511 | -13.6501 | Eastern | 4.5 | EASTERN | Chipata | Yes | No | No | Urban | Silver | Silver | HUB | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 146 |  | 2 | MTNAirtel | T2046 | ZM0836 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | yes |  |  | yes - Emergency | 30 |  | Pending |  |  |  |  | IHS_EST_227A
1180 | ZM0925 | IHS_EST_228A | MSORO | 31.902 | -13.612 | Eastern | 2.5 | EASTERN | Mambwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 70 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | IMG | IMG | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | NA | 0 | N/A |  | 0 | 106 |  | 2 | MTNAirtel | T2042 | ZM0925 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_228A
1331 | ZM0930 | IHS_EST_229A | MWASE MPHANGWE | 32.9594 | -13.0325 | Eastern | 2 | EASTERN | Lundazi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 16 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC300-H1 | 200 | Lithium | 500 | 48 | 100 | 5 | NA | 0 | N/A |  | 0 | 91 |  | 2 | MTNAirtel | T2021 | ZM0930 | yes |  | working | Palisade | Netco | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_229A
1181 | ZM3269 | IHS_EST_230A | MSORO REPEATER | 31.892 | -13.9275 | Eastern | 2.5 | EASTERN | Katete | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Solar-Gen | Green Field | 50 | Indoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 600 | Lithium | 600 | 48 | 100 | 6 | LG | LG | 18000 | 18000 | 2 | 91 |  | 2 | MTNAirtel | T2085 | ZM3269 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | yes |  |  | yes | 16 |  | Pending |  |  |  |  | IHS_EST_230A
1167 | ZM3309 | IHS_EST_231A | MPONDA REPEATER | 32.9817 | -12.607 | Eastern | 2.5 | EASTERN | Lundazi | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 70 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | MPPT | 0 | 250 | ROLLS | 1410 | 4 | 1410 | 12 | NA | 0 | N/A |  | 0 | 74 |  | 2 | MTNAirtel | T2074 | ZM3309 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_231A
234 | ZM3341 | IHS_EST_232A | CHIPATA RELIEF 1 Katopola | 32.6369 | -13.6163 | Eastern | 2.5 | EASTERN | Chipata | No | No | No | Urban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 84 |  | 2 | AirtelINQ | 0 | ZM3341 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_232A
235 | ZM3342 | IHS_EST_233A | CHIPATA RELIEF 2 (Kapata) | 32.6469 | -13.6287 | Eastern | 5.5 | EASTERN | Chipata | No | No | No | Urban | Silver | Silver | HUB | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | CK Works | CK Works | 45 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 360 |  | 2 | MTNAirtel | T2051 | ZM3342 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_233A
994 | ZM3364 | IHS_EST_234A | MANDA HILL | 33.2258 | -11.5902 | Eastern | 2.5 | EASTERN | Chama | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 80 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | 0 | 0 | 1000 | MPPT | 0 | 0 | Lithium | 500 | 48 | 100 | 5 | NA | 0 | N/A |  | 0 | 69 |  | 2 | MTNAirtel | TX | ZM3364 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_234A
934 | ZM3365 | IHS_EST_235A | Lyonekela | 33.2174 | -11.2734 | Eastern | 2.5 | EASTERN | Chama | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 80 | Indoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 52 |  | 2 | MTNAirtel | T2080 | ZM3365 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_235A
1306 | ZM3386 | IHS_EST_236A | MUTILANSEMBE | 32.6465 | -13.6232 | Eastern | 2.5 | EASTERN | Chipata | No | No | No | Urban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | IMG | IMG | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 43 |  | 1 | Airtel | 0 | ZM3386 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_236A
1081 | ZM3429 | IHS_EST_237A | MFUWE | 32.8566 | -13.1517 | Eastern | 2 | EASTERN | Mambwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 70 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Mecc Alte | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | NA | 0 | N/A |  | 0 | 64 |  | 1 | Airtel | 0 | ZM3429 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_237A
944 | ZM3515 | IHS_EST_238A | MADZIMAWE | 32.4107 | -13.7137 | Eastern | 2.5 | EASTERN | Chipata | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | IMG | IMG | 20 | perkins | 0 | Mecc Alte | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Amaron | 600 | 2 | 600 | 24 | NA | 0 | N/A |  | 0 | 68 |  | 1 | Airtel | 0 | ZM3515 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_EST_238A
1535 | ZM3547 | IHS_EST_239A | PETAUKE RELIEF | 31.3402 | -14.2987 | Eastern | 1.8 | EASTERN | Petauke | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 15 | Yanmar | 0 | Mecc Alte | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 70 |  | 1 | Airtel | 0 | ZM3547 | yes |  | not working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_239A
1313 | ZM3575 | IHS_EST_240A | Muyombe Repeater 1 A | 33.2984 | -10.8722 | Eastern | 1.5 | EASTERN | Chama | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 60 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 14 | Mitsubishi | S4LZ | Zanardi | AL3/4 | 600 | MPPT | 0 | 0 | Agisson | 600 | 2 | 600 | 24 | NA | 0 | N/A |  | 0 | 66 |  | 2 | MTNAirtel | TX | ZM3575 | yes |  | working | Mesh | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_240A
1314 | ZM3576 | IHS_EST_241A | Muyombe Repeater 2 B | 33.3079 | -10.9944 | Eastern | 1.5 | EASTERN | Chama | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 60 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 11 | Yanmar | 0 | Mecc Alte | 0 | 600 | Power cube | ICC300-H1 | 200 | Lithium | 500 | 48 | 100 | 5 | NA | 0 | N/A |  | 0 | 87 |  | 2 | MTNAirtel | TX | ZM3576 | yes |  | working | Mesh | Netco | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_241A
1193 | ZM3710 | IHS_EST_243A | Muchereka | 33.1055 | -12.2702 | Eastern | 1.5 | EASTERN | Lundazi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 70 | Indoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | RID | RID | 14 | Mitsubishi | S4LZ | Zanardi | AL3/4 | 600 | MPPT | 0 | 0 | BSB | 1500 | 2 | 1500 | 24 | LG | LG | 18000 | 18000 | 2 | 84 |  | 2 | MTNAirtel | T2084 | ZM3710 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_243A
1504 | ZM3821 | IHS_EST_244A | NYANJE MISSION HOSPITAL | 31.7981 | -14.3803 | Eastern | 1.8 | EASTERN | Sinda | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 70 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 15 | Yanmar | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 200 | Power safe | 600 | 2 | 600 | 24 | NA | 0 | N/A |  | 0 | 41 |  | 1 | Airtel | 0 | ZM3821 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_244A
1503 | ZM3822 | IHS_EST_245A | Nyanje | 31.851 | -14.3253 | Eastern | 2.5 | EASTERN | Sinda | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 40 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC300-H1 | 400 | Agisson | 600 | 2 | 600 | 24 | NA | 0 | N/A |  | 0 | 36 |  | 1 | Airtel | 0 | ZM3822 | yes |  | working | Palisade | Netco | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_245A
561 | ZM3823 | IHS_EST_246A | Kalongwezi | 32.6381 | -13.6489 | Eastern | 2.5 | EASTERN | Chipata | No | No | No | Urban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Earth Technology | Earth technology | 20 | perkins | 0 | Leroy Sommer | 0 | 375 | Power cube | ICC300-H1 | 400 | ROLLS | 1410 | 4 | 1410 | 12 | NA | 0 | N/A |  | 0 | 100 |  | 2 | MTNAirtel | T2081 | ZM3823 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_246A
108 | ZM3824 | IHS_EST_247A | CHANIDA BORDER | 32.3328 | -14.2272 | Eastern | 1.8 | EASTERN | Chadiza | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Indoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 41 |  | 1 | Airtel | 0 | ZM3824 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_247A
895 | ZM3874 | IHS_EST_248A | Lumezi Hospital | 31.3835 | -13.9073 | Eastern | 2 | EASTERN | Lundazi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 16 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | NARADA | 1200 | 2 | 600 | 48 | NA | 0 | N/A |  | 0 | 46 |  | 1 | Airtel | 0 | ZM3874 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_248A
1423 | ZM3875 | IHS_EST_249A | Ndondo (Lyonekela_7) | 32.9144 | -12.4476 | Eastern | 2.5 | EASTERN | Lundazi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Emerson | EPC48200/2900-HC1 | 250 | BSB | 1500 | 2 | 1500 | 24 | NA | 0 | N/A |  | 0 | 52 |  | 2 | MTNAirtel | T2080 | ZM3875 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_249A
1328 | ZM3877 | IHS_EST_250A | MWANJAWANTU | 31.4267 | -14.6148 | Eastern | 1.8 | EASTERN | Petauke | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 70 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 15 | Yanmar | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | ROLLS | 1410 | 4 | 1410 | 12 | NA | 0 | N/A |  | 0 | 57 |  | 2 | MTNAirtel | T2043 | ZM3877 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_250A
595 | ZM3956 | IHS_EST_251A | Kamono (Nyimba Town_Town1) | 30.7568 | -14.619 | Eastern | 2.5 | EASTERN | Nyimba | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 54 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 200 | 48 | 100 | 2 | NA | 0 | N/A |  | 0 | 78 |  | 2 | MTNAirtel | T2075 | ZM3956 | yes |  | working | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_251A
1719 | ZM3957 | IHS_EST_252A | Sungani Village (Nyimba Town_Town2) | 30.7869 | -14.5135 | Eastern | 1.8 | EASTERN | Nyimba | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Power safe | 1200 | 2 | 1200 | 24 | NA | 0 | N/A |  | 0 | 38 |  | 1 | Airtel | 0 | ZM3957 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_252A
1505 | ZM3958 | IHS_EST_253A | Nyanphande (Petauke town1) | 31.2031 | -14.2049 | Eastern | 1.8 | EASTERN | Petauke | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 45 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | CK Works | CK Works | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | NARADA | 1200 | 2 | 600 | 48 | NA | 0 | N/A |  | 0 | 96 |  | 2 | MTNAirtel | T2068 | ZM3958 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_253A
237 | ZM3959 | IHS_EST_254A | Chipata town1 (Mchenga) | 32.6623 | -13.6658 | Eastern | 4.5 | EASTERN | Chipata | Yes | No | No | Urban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 40 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | CK Works | CK Works | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | NARADA | 1200 | 2 | 600 | 48 | NA | 0 | N/A |  | 0 | 126 |  | 3 | MTNAirtelLiquid Telecom | T2060 | ZM3959 | yes |  | working | Clear View | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | Done |  | No | No | Yes |  |  | Pending | 30 |  | Pending |  |  |  |  | IHS_EST_254A
841 | ZM3961 | IHS_EST_255A | Luampamba (Lundazi town2) | 33.1327 | -12.4244 | Eastern | 2.5 | EASTERN | Lundazi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | IMG | IMG | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | ROLLS | 1410 | 4 | 1410 | 12 | NA | 0 | N/A |  | 0 | 44 |  | 1 | Airtel | 0 | ZM3961 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_255A
1424 | ZM4010 | IHS_EST_257A | Ndondo Hill (Mumbi) | 31.2578 | -14.424 | Eastern | 2.5 | EASTERN | Petauke | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 36 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Earth Technology | Earth technology | 20 | perkins | 0 | 0 | AL3/4 | 400 | MPPT | 0 | 0 | Lithium | 500 | 48 | 100 | 5 | NA | 0 | N/A |  | 0 | 70 |  | 2 | MTNAirtel | T2078 | ZM4010 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_257A
1323 | ZM6022 | IHS_EST_258A | mwami boarder | 32.7943 | -13.7477 | Eastern | 2.5 | EASTERN | Chipata | Yes | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | NA | 0 | N/A |  | 0 | 140 |  | 3 | MTNAirtelParatus Telecom | T2089 | ZM6022 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_EST_258A
1109 | ZM6023 | IHS_EST_259A | Minga | 31.1464 | -14.3539 | Eastern | 2 | EASTERN | Petauke | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 16 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | ROLLS | 1410 | 4 | 1410 | 12 | NA | 0 | N/A |  | 0 | 64 |  | 2 | MTNAirtel | T2057 | ZM6023 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_259A
241 | ZM6025 | IHS_EST_260A | Chipembe | 31.0112 | -14.5307 | Eastern | 2 | EASTERN | Petauke | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 16 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Power safe | 1200 | 2 | 1200 | 24 | NA | 0 | N/A |  | 0 | 66 |  | 2 | MTNAirtel | T2073 | ZM6025 | yes |  | not working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_260A
240 | ZM6080 | IHS_EST_261A | Chipata_1_Rlf | 32.6209 | -13.6211 | Eastern | 2.5 | EASTERN | Chipata | No | No | No | Urban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 40 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | IMG | IMG | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Power safe | 600 | 2 | 600 | 24 | NA | 0 | N/A |  | 0 | 63 |  | 1 | Airtel | 0 | ZM6080 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_261A
1159 | ZM6098 | IHS_EST_262A | Mphata Hill Repeater | 32.3582 | -13.449 | Eastern | 2.5 | EASTERN | Mambwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Emerson | PC48200/2900-HC1 | 250 | BSB | 1500 | 2 | 1500 | 24 | NA | 0 | N/A |  | 0 | 47 |  | 1 | Airtel | 0 | ZM6098 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_262A
1759 | ZM6107 | IHS_EST_263A | Ukwimi A & B | 31.6125 | -13.9543 | Eastern | 1.8 | EASTERN | Sinda | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | ROLLS | 1410 | 4 | 1410 | 12 | NA | 0 | N/A |  | 0 | 43 |  | 1 | Airtel | 0 | ZM6107 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_263A
1760 | ZM6174 | IHS_EST_264A | UKWIMI_2 | 31.706 | -13.9967 | Eastern | 2.5 | EASTERN | Sinda | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 70 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | 0 | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | NARADA | 1200 | 2 | 600 | 48 | NA | 0 | N/A |  | 0 | 76 |  | 2 | MTNAirtel | T2071 | ZM6174 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_EST_264A
228 | ZM6183 | IHS_EST_265A | Chipata 2 Rlf (mafarendum) | 32.596 | -13.6335 | Eastern | 4.5 | EASTERN | Chipata | Yes | No | No | Urban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | CK Works | CK Works | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | ROLLS | 1410 | 4 | 1410 | 12 | NA | 0 | N/A |  | 0 | 102 |  | 3 | MTNAirtelLiquid Telecom | T2087 | ZM6183 | yes |  | working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | yes |  |  | Pending | 30 |  | Pending |  |  |  |  | IHS_EST_265A
1332 | ZM6343 | IHS_EST_266A | Mwata | 33.2424 | -11.7282 | Eastern | 2.5 | EASTERN | Lundazi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | 0 | AL3/4 | 1000 | MPPT | 0 | 0 | NARADA | 1200 | 2 | 600 | 48 | NA | 0 | N/A |  | 0 | 97 |  | 2 | MTNAirtel | T2070 | ZM6343 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_266A
110 | ZM6344 | IHS_EST_267A | Chasefu | 33.092 | -11.9223 | Eastern | 2.5 | EASTERN | Lundazi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Vitalgen | Vitalgen | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC300-H1 | 200 | NARADA | 600 | 2 | 600 | 24 | NA | 0 | N/A |  | 0 | 68 |  | 2 | MTNAirtel | T2086 | ZM6344 | yes |  |  | Palisade | Netco | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_267A
1465 | ZM6345 | IHS_EST_268A | Nkhanga | 33.0414 | -12.156 | Eastern | 2.5 | EASTERN | Lundazi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | GNM | GNM | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Emerson | EPC48200/2900-HC1 | 250 | NARADA | 1200 | 2 | 600 | 48 | NA | 0 | N/A |  | 0 | 65 |  | 2 | MTNAirtel | T2077 | ZM6345 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_268A
1394 | ZM6396 | IHS_EST_269A | Naviruli | 32.3081 | -14.1105 | Eastern | 2.5 | EASTERN | Chadiza | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Vital gen | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC300-H1 | 200 | Lithium | 600 | 48 | 100 | 6 | NA | 0 | N/A |  | 0 | 45 |  | 2 | MTNAirtel | T2092 | ZM6396 | yes |  |  | Palisade | Netco | 2022-08-05 | No | No |  |  |  |  | 0 |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_269A
909 | ZM6805 | IHS_EST_270A | Lundazi 3G | 33.1644 | -12.2917 | Eastern | 2.5 | EASTERN | Lundazi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 70 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC300-H1 | 250 | NARADA | 1200 | 2 | 600 | 48 | NA | 0 | N/A |  | 0 | 81 |  | 1 | Airtel | 0 | ZM6805 | yes |  |  | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_270A
239 | ZM0479 | IHS_EST_271A | Chipata ZCCF Command | 32.637 | -13.6328 | Eastern | 4.5 | EASTERN | Chipata | No | No | No | Urban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 600 | 48 | 100 | 6 | N/A | 0 | N/A | N/A | 0 | 103 |  | 1 | Airtel | 0 | ZM0479 | No |  | working | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_EST_271A
910 | ZM0559 | IHS_EST_272A | Lundazi Old Airstrip | 33.1837 | -12.2872 | Eastern | 2.5 | EASTERN | Lundazi | No | No | No | Suburban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Emerson | EPC48200/2900-HC1 | 250 | NARADA | 1200 | 2 | 600 | 48 | N/A | 0 | N/A | N/A | 0 | 75 |  | 1 | Airtel | 0 | ZM0559 | No |  | working | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_EST_272A
1809 | ZM0577 | IHS_EST_273A | Zumaili (old chadiza road) | 32.6168 | -13.7721 | Eastern | 2.5 | EASTERN | Chipata | No | No | No | Suburban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 500 | 48 | 100 | 5 | NA | 0 | N/A | NA | 0 | 79 |  | 1 | Airtel | 0 | ZM0577 | No |  | working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_273A
232 | ZM1472 | IHS_EST_274A | Chipata Magazine | 32.6428 | -13.6589 | Eastern | 2.5 | Eastern | Chipata | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 90 |  | 1 | Airtel | ZM1472 | ZM1472 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_EST_274A
659 | ZM1475 | IHS_EST_275A | Kapata Market | 32.6662 | -13.6335 | Eastern | 2.5 | Eastern | Chipata | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 96 |  | 1 | Airtel | ZM1475 | ZM1475 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_EST_275A
230 | ZM1473 | IHS_EST_276A | Chipata East Rise | 32.6615 | -13.6448 | Eastern | 2.5 | Eastern | Chipata | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 93 |  | 1 | Airtel | ZM1473 | ZM1473 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_EST_276A
1395 | ZM1474 | IHS_EST_277A | Navutika | 32.638 | -13.6051 | Chipata | 2.5 | Eastern | Eastern | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 80 |  | 1 | Airtel | ZM1490 | ZM1474 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_EST_277A
238 | ZM1471 | IHS_EST_278A | Chipata Trades | 32.6731 | -13.6686 | Eastern | 2.5 | Eastern | Chipata | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 78 |  | 1 | Airtel | ZM1474 | ZM1471 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_EST_278A
729 | ZM1495 | IHS_EST_279A | Katete Ibex | 32.0432 | -14.0492 | Eastern | 2.5 | Eastern | Katete | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 75 |  | 1 | Airtel | ZM1485 | ZM1495 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_EST_279A
1533 | ZM1530 | IHS_EST_280A | Petauke Industrial | 31.3325 | -14.264 | Eastern | 2.5 | Eastern | Petauke | No | No | No | Urban |  | silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Fetus Kalunga | SBC | SBC | Airtel | Fetus Kalunga | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 78 |  | 1 | Airtel | ZM1480 | ZM1530 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_EST_280A
1845 | ZM1352 | IHS_EST_281A | Tafelansoni Basic School | 32.435 | -14.2118 | Eastern | 5.5 | Eastern | Chadiza | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Solar-Gen | Green Field | 70 | Outdoor | Fetus Kalunga | N/A | N/A | Airtel | Fetus Kalunga | CCS | CCS | perkins |  | 30 |  |  |  |  | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_EST_281A
1831 | ZM1363 | IHS_EST_282A | Chinunda RHC | 32.6536 | -13.3343 | Eastern | 4.5 | Eastern | Chipangali | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Solar-Gen | Green Field | 60 | Outdoor | Fetus Kalunga | N/A | N/A | Airtel | Fetus Kalunga | CCS | CCS | perkins | [6 empty] | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_EST_282A
1844 | ZM1348 | IHS_EST_283A | Bwanunkha Basic School | 32.5777 | -13.9294 | Eastern | 4.5 | Eastern | Chadiza | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Solar-Gen | Green Field | 60 | Outdoor | Fetus Kalunga | N/A | N/A | Airtel | Fetus Kalunga | CCS | CCS | perkins |  | 30 |  |  |  |  | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_EST_283A
1841 | ZM1337 | IHS_EST_284A | Kasenengwa Basic School | 32.3013 | -13.6254 | Eastern | 4.5 | Eastern | Kasenengwa | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Solar-Gen | Green Field | 80 | Outdoor | Fetus Kalunga | N/A | N/A | Airtel | Fetus Kalunga | CCS | CCS | perkins |  | 30 |  |  |  |  | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_EST_284A
1827 | ZM1344 | IHS_EST_286A | Gundani Basic School | 32.378 | -13.6378 | Eastern | 4.5 | Eastern | Kasenengwa | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Solar-Gen | Green Field | 60 | Outdoor | Fetus Kalunga | N/A | N/A | Airtel | Fetus Kalunga | CCS | CCS | perkins | [6 empty] | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_EST_286A
1814 | ZM1353 | IHS_EST_288A | Choongo Turnoff | 32.3956 | -13.6351 | Eastern | 2.5 | Eastern | Kasenengwa | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Fetus Kalunga | CCS | CCS | Airtel | Fetus Kalunga | CCS | CCS | perkins | [6 empty] | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [8 empty] | Palisade |  | 2022-09-01 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_288A
1830 | ZM1357 | IHS_EST_289A | Kadama Basic School | 32.1891 | -13.7146 | Eastern | 4.5 | Eastern | Kasenengwa | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Solar-Gen | Green Field | 60 | Outdoor | Fetus Kalunga | N/A | N/A | Airtel | Fetus Kalunga | CCS | CCS | perkins | [6 empty] | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_EST_289A
1817 | ZM1364 | IHS_EST_290A | Muzeyi Mission RHC | 32.4467 | -13.5051 | Eastern | 2.5 | Eastern | Chipangali | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Fetus Kalunga | CCS | CCS | Airtel | Fetus Kalunga | CCS | CCS | perkins | [6 empty] | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [8 empty] | Palisade |  | 2022-09-04 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_290A
1825 | ZM1299 | IHS_EST_291A | Mtandaza Basic School | 31.9706 | -14.3426 | Eastern | 4.5 | Eastern | Sinda | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Solar-Gen | Green Field | 60 | Outdoor | Fetus Kalunga | N/A | N/A | Airtel | Fetus Kalunga | CCS | CCS | perkins | [6 empty] | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_EST_291A
1842 | ZM1340 | IHS_EST_292A | David Seinfield school | 31.8539 | -14.1015 | Eastern | 5.5 | Eastern | Katete | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 80 | Outdoor | Fetus Kalunga | N/A | N/A | Airtel | Fetus Kalunga | CCS | CCS | perkins |  | 30 |  |  |  |  | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_EST_292A
1813 | ZM1349 | IHS_EST_293A | Dole Primary School | 32.0661 | -14.1502 | Eastern | 2.5 | Eastern | Katete | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Fetus Kalunga | CCS | CCS | Airtel | Fetus Kalunga | CCS | CCS | perkins | [6 empty] | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [8 empty] | Palisade |  | 2022-08-31 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_293A
1829 | ZM1356 | IHS_EST_294A | Kagoro Basic School | 32.0744 | -14.2418 | Eastern | 4.5 | Eastern | Katete | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Fetus Kalunga | N/A | N/A | Airtel | Fetus Kalunga | CCS | CCS | perkins | [6 empty] | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_EST_294A
1815 | ZM1358 | IHS_EST_295A | Msazanla Primary school | 31.4523 | -14.0732 | Eastern | 1.8 | Eastern | Petauke | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 70 | Outdoor | Fetus Kalunga | CCS | CCS | Airtel | Fetus Kalunga | CCS | CCS | perkins | [6 empty] | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [8 empty] | Palisade |  | 2022-09-02 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_295A
1833 | ZM1283 | IHS_EST_296A | Mawanda Basic School | 31.4666 | -14.0161 | Eastern | 4.5 | Eastern | Lusangazi | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 80 | Outdoor | Fetus Kalunga | N/A | N/A | Airtel | Fetus Kalunga | CCS | CCS | perkins | [6 empty] | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_EST_296A
1843 | ZM1347 | IHS_EST_297A | Mumbi Primary School | 31.3087 | -14.4793 | Eastern | 5.5 | Eastern | Petauke | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 80 | Outdoor | Fetus Kalunga | N/A | N/A | Airtel | Fetus Kalunga | CCS | CCS | perkins |  | 30 |  |  |  |  | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_EST_297A
1816 | ZM1278 | IHS_EST_298A | Kaulu School | 31.4705 | -14.5157 | Eastern | 2.5 | Eastern | Petauke | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Fetus Kalunga | CCS | CCS | Airtel | Fetus Kalunga | CCS | CCS | perkins | [6 empty] | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [8 empty] | Palisade |  | 2022-09-03 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_298A
1832 | ZM1284 | IHS_EST_299A | Chikalawa Basic School | 31.6321 | -14.4921 | Eastern | 4.5 | Eastern | Sinda | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Solar-Gen | Green Field | 60 | Outdoor | Fetus Kalunga | N/A | N/A | Airtel | Fetus Kalunga | CCS | CCS | perkins | [6 empty] | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_EST_299A
1819 | ZM1288 | IHS_EST_300A | Chipungu RHC | 31.2917 | -14.0935 | Eastern | 2.5 | Eastern | Lusangazi | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Solar-Gen | Green Field | 60 | Outdoor | Fetus Kalunga | CCS | CCS | Airtel | Fetus Kalunga | CCS | CCS | perkins | [6 empty] | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [8 empty] | Palisade |  | 2022-09-06 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_300A
1820 | ZM1294 | IHS_EST_301A | Kakwiya RHC | 31.193 | -14.1331 | Eastern | 4.5 | Eastern | Lusangazi | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Fetus Kalunga | CCS | CCS | Airtel | Fetus Kalunga | CCS | CCS | perkins | [6 empty] | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [8 empty] | Palisade |  | 2022-09-07 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_301A
1821 | ZM1411 | IHS_EST_302A | Mngoza Basic School | 31.4696 | -14.2537 | Eastern | 2.5 | Eastern | Petauke | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Solar-Gen | Green Field | 60 | Outdoor | Fetus Kalunga | CCS | CCS | Airtel | Fetus Kalunga | CCS | CCS | perkins | [6 empty] | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [8 empty] | Palisade |  | 2022-09-08 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_302A
1818 | ZM1280 | IHS_EST_303A | Monde Day Sec Sch | 31.3621 | -14.0406 | Eastern | 2.5 | Eastern | Lusangazi | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Solar-Gen | Green Field | 60 | Outdoor | Fetus Kalunga | CCS | CCS | Airtel | Fetus Kalunga | CCS | CCS | perkins | [6 empty] | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [8 empty] | Palisade |  | 2022-09-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_303A
1812 | ZM1345 | IHS_EST_304A | Nyamutuma Turn off | 31.5887 | -14.184 | Eastern | 2.5 | Eastern | Sinda | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Fetus Kalunga | CCS | CCS | Airtel | Fetus Kalunga | CCS | CCS | perkins | [6 empty] | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [8 empty] | Palisade |  | 2022-08-30 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_EST_304A
1828 | ZM1351 | IHS_EST_305A | Chilasa RHC | 31.9487 | -14.2666 | Eastern | 4.5 | Eastern | Sinda | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Solar-Gen | Green Field | 60 | Outdoor | Fetus Kalunga | N/A | N/A | Airtel | Fetus Kalunga | CCS | CCS | perkins | [6 empty] | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_EST_305A
1846 | ZM1366 | IHS_EST_306A | Chataika Primary School | 31.682 | -14.3461 | Eastern | 4.5 | Eastern | Sinda | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Solar-Gen | Green Field | 80 | Outdoor | Fetus Kalunga | N/A | N/A | Airtel | Fetus Kalunga | CCS | CCS | perkins |  | 30 |  |  |  |  | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_EST_306A
1191 | T0017 | IHS_LSK_001M | MTSO | 28.2873 | -15.4101 | Lusaka | 5.5 | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G 4G | P2 | HUB | BB | On air | Grid-Gen | Green Field | 80 | Indoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | CK Works | CK Works | 45 | perkins | 1103A-33 | Leroy Sommer | LSAP 423F | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | CHIGO | CHIGO | 18000 | 18000 | 4 | 212 |  | 3 | MTNINQSmartnet | T0017 | 0 | YES |  | Working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_001M
1589 | T0161 | IHS_LSK_002M | Salvation Army House | 28.2808 | -15.4126 | Lusaka | N/A | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid Only | Roof Top | RT | Indoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | In House | In House | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | IPT | DPR 2400B-48 | 250 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 12000 | 12000 | 2 | 56 |  | 1 | MTN | T0161 | 0 | no |  | no | n/a | Inala | 2022-08-05 | No | No |  |  |  |  | Done | 2019-08-02 | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_002M
1787 | T0170 | IHS_LSK_003M | Yotam Muleya | 28.2833 | -15.4031 | Lusaka | 5.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | CK Works | CK Works | 45 | perkins | 1103A-33 | Leroy Sommer | LSAP 423F | 1000 | Power cube | ECC500 | 400 | NARADA | 1200 | 2 | 600 | 48 | CHIGO | CHIGO | 18000 | 18000 | 4 | 175 |  | 4 | MTNAirtelINQLiquid Telecom | T0170 | ZM3400 | N0 |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_003M
1544 | T0342 | IHS_LSK_004M | Post Office | 28.2822 | -15.4164 | Lusaka | 2.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P3 | BTS | BTS | On air | Grid-Gen | Roof Top | RT | Outdoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | In House | In House | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | N/A | 0 | 0 | C&D True | 704 | 12 | 176 | 16 | N/A | N/A | N/A |  | N/A | 79 |  | 1 | MTN | T0342 | 0 |  |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_004M
1456 | T0311 | IHS_LSK_005M | NIPA | 28.2928 | -15.4171 | Lusaka | 2.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | LSAP 40H | 1000 | IPT | DPR 2400B-48 | 250 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 152 |  | 2 | MTNAirtel | T0311 | ZM6647 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_005M
1539 | T0181 | IHS_LSK_007M | Plaza3 Chachacha | 28.2814 | -15.4187 | Lusaka | 4.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid-Gen | Roof Top | RT | Indoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 404A-22 | Leroy Sommer | LSAP 423F | 1000 | IPT | DPR 2400B-48 | 200 | NARADA | 600 | 2 | 600 | 24 | CHIGO | CHIGO | 18000 | 18000 | 2 | 200 |  | 1 | MTN | T0181 | 0 | N0 |  | Working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_007M
801 | T0269 | IHS_LSK_008M | Lagos Road | 28.2988 | -15.4086 | Lusaka | 2.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Wolong | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 131 |  | 3 | MTNAirtelLiquid Telecom | T0269 | ZM6830 | YES |  | Working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_008M
61 | T0004 | IHS_LSK_009M | Cairo Road | 28.2821 | -15.4205 | Lusaka | N/A | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | BTS | Hub | On air | Grid Only | Roof Top | RT | Indoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | In House | In House | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | IPT |  |  | Lithium | 200 | 48 | 100 | 2 | GREE | GREE | 18000 | 18000 | 2 | 59.1 |  | 2 | MTNLiquid Telecom | T0004 | 0 |  |  |  | n/a | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_009M
106 | T0301 | IHS_LSK_010M | Chandwe Musonda | 28.2784 | -15.4018 | Lusaka | 2 | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 16 | perkins | 403D-15 | Mecc Alte | ECP 28-1L/4 | 1000 | IPT | ECC500 | 400 | C&D True | 704 | 12 | 176 | 16 | N/A | N/A | N/A | N/A | N/A | 98 |  | 2 | MTNAirtel | T0301 | ZM0417 | N0 |  | No working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | Yes |  |  | Pending | 20 |  | Pending |  |  |  |  | IHS_LSK_010M
1546 | T0022 | IHS_LSK_011M | Premium House | 28.2883 | -15.4231 | Lusaka | N/A | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid Only | Roof Top | RT | Indoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | In House | In House | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | IPT |  | 250 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 58 |  | 2 | MTNLiquid Telecom | T0022 | 0 |  |  |  | n/a | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_011M
444 | T0034 | IHS_LSK_012M | Jacaranda | 28.2993 | -15.4157 | Lusaka | 4.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P3 | BTS | Hub | On air | Grid-Gen | Green Field | 40 | Indoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 1103A-33 | Mecc Alte | ECP 28-1L/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | CHIGO | CHIGO | 18000 | 18000 | 2 | 190 |  | 2 | MTNLiquid Telecom | T0034 | 0 | YES |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_012M
1774 | T0177 | IHS_LSK_013M | WASHAMA RD | 28.2734 | -15.4085 | Lusaka | 1.5 | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | New way | New way | 13 | perkins | 403A-15 | Leroy Sommer | LSA 4OM5 | 1000 | IPT | DPR 2400B-48 | 250 | Lithium | 600 | 48 | 100 | 6 | LG | LG | 18000 | 18000 | 2 | 90 |  | 2 | MTNAirtel | T0177 | ZM6847 | YES |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | Pending | 20 |  | Pending |  |  |  |  | IHS_LSK_013M
788 | T0211 | IHS_LSK_014M | Kulima Tower | 28.2804 | -15.4226 | Lusaka | N/A | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G 4G | P3 | BTS | BTS | On air | Grid only | Roof Top | RT | Outdoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | In House | In House | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Power cube | R4850N2 | 0 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A |  | N/A | 48 |  | 1 | MTN | T0211 | 0 |  |  |  | N/A | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_014M
836 | T0212 | IHS_LSK_015M | LKP Lusaka House | 28.2797 | -15.4258 | Lusaka | N/A | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G | P2 | BTS | BTS | On air | Grid Only | Roof Top | RT | Outdoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | In House | In House | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | IPT | Huawei |  | Lithium | 700 | 48 | 100 | 7 | N/A | N/A | N/A |  | N/A | 78 |  | 1 | MTN | T0212 | 0 |  |  |  | n/a | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_015M
920 | T0160 | IHS_LSK_016M | Lusaka city council | 28.301 | -15.421 | Lusaka | 1.8 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P3 | BTS | BB | On air | Grid-Gen | Roof Top | RT | Indoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 15 | Yanmar | 4TNE88-G1A | Mecc Alte | ECO28-1LN/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | CHIGO | CHIGO | 18000 | 18000 | 2 | 75 |  | 2 | MTNLiquid Telecom | T0160 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | Pending | 20 |  | Pending |  |  |  |  | IHS_LSK_016M
609 | T0294 | IHS_LSK_017M | Kamwala Shops | 28.2887 | -15.4308 | Lusaka | 4.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P1 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 403A-15 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 174 |  | 3 | MTNAirtelLiquid Telecom | T0294 | ZM0347 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_017M
404 | T0069 | IHS_LSK_018M | HIGHRISE FLATS LSK | 28.3067 | -15.4177 | Lusaka | N/A | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G 4G | P2 | BTS | Hub | On air | Grid Only | Roof Top | RT | Outdoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | In House | In House | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | IPT | DPR 2400B-48 | 250 | NA | NA | N/A | N/A |  | N/A | N/A | N/A |  | N/A | 70 |  | 1 | MTN | T0069 | 0 |  |  |  | n/a | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_018M
1689 | T0025 | IHS_LSK_019M | Soweto | 28.2718 | -15.4241 | Lusaka | 4.5 | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G | P3 | BTS | BB | On air | Grid-Gen | Green Field | 50 | Indoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | CK Works | CK Works | 30 | perkins | 1103C-33 | Leroy Sommer | S 160 LB | 1000 | Power cube | ICC330-H1-C1 | 400 | Wolong | 1200 | 2 | 600 | 48 | CHIGO | CHIGO | 18000 | 18000 | 2 | 180 |  | 1 | MTN | T0025 | 0 | YES |  | Working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_019M
365 | T0171 | IHS_LSK_020M | FRA | 28.2667 | -15.4139 | Lusaka | 2.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Indoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Earth Technology | Earth technology | 20 | perkins | 403A-15 | Leroy Sommer | LSA 4OM5 | 375 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | CHIGO | CHIGO | 18000 | 18000 | 2 | 65 |  | 2 | MTNParatus Telecom | T0171 | 0 | YES |  | Working | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | Done | 2019-05-30 | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_020M
995 | T0244 | IHS_LSK_021M | Manda Road | 28.2666 | -15.4147 | Lusaka | 2.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | IMG | IMG | 20 | perkins | 404A-22 | Mecc Alte | TAL 040F J 6S/4 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 800 | 2 | 800 | 24 | N/A | N/A | N/A | N/A | N/A | 135 |  | 3 | MTNAirtelLiquid Telecom | T0244 | ZM0084 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_021M
868 | T0268 | IHS_LSK_022M | Lubu Road | 28.3109 | -15.4088 | Lusaka | 2.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Mecc Alte | ECP 28-1L/4 | 1000 | IPT | DPR 2400B-48 | 250 | Lithium | 600 | 48 | 100 | 6 | N/A | N/A | N/A | N/A | N/A | 107 |  | 3 | MTNAirtelLiquid Telecom | T0268 | ZM6832 | YES |  | Working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_022M
1692 | T0305 | IHS_LSK_023M | Soweto West | 28.2661 | -15.4215 | Lusaka | 1.8 | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 403D-15 | Mecc Alte | ECP 28-1L/4 | 1000 | IPT | DPR 2400B-48 | 250 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | N/A | N/A | 55 |  | 1 | MTN | T0305 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_023M
943 | T0204 | IHS_LSK_024M | Madras | 28.2965 | -15.4326 | Lusaka | 4.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | CK Works | CK Works | 20 | perkins | ENLP30S-3 | Leroy Sommer | TAL 040 DJ 6S/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 200 | 48 | 100 | 2 | CHIGO | CHIGO | 18000 | 18000 | 2 | 97 |  | 1 | MTN | T0204 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_024M
135 | T0229 | IHS_LSK_025M | Chibolya | 28.2724 | -15.4313 | Lusaka | 1.5 | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Falcon | Falcon | 13 | perkins | 403A-15 | Leroy Sommer | LSA 40M5 C 6/4 | 600 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 30 |  | 1 | MTN | T0229 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_025M
60 | T0003 | IHS_LSK_026M | Cabinet | 28.31 | -15.4242 | Lusaka | 2 | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G 4G | P3 | HUB | Hub | On air | Grid-Gen | Green Field | 30 | Indoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Yarnmar | Yanmar | 16 | Yanmar | 4TNE88-G1A | Leroy Sommer | LSC 28S2 | 600 | IPT | DPR 2400B-48 | 250 | Agisson | 600 | 2 | 600 | 24 | GREE | GREE | 12000 | 12000 | 2 | 52 |  | 1 | MTN | T0003 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_026M
992 | T0014 | IHS_LSK_027M | Manda Hill | 28.3038 | -15.3885 | Lusaka | 4.5 | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BB | On air | Grid-Gen | Green Field | 50 | Indoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 1103A-33 | Leroy Sommer | TAL 042C J 6/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 300 | 48 | 100 | 3 | CHIGO | CHIGO | 18000 | 18000 | 2 | 122 |  | 2 | MTNAirtel | T0014 | ZM0372 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | yes | 30 | 43655 | closed |  |  |  |  | IHS_LSK_027M
1523 | T0033 | IHS_LSK_028M | Parmalat | 28.2615 | -15.3987 | Lusaka | 2.5 | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G 4G | P2 | HUB | HUB | On air | Grid-Gen | Green Field | 36 | Indoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | CHIGO | CHIGO | 18000 | 18000 | 2 | 98 |  | 1 | MTN | T0033 | 0 | YES |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_028M
78 | T0183 | IHS_LSK_029M | Chaisa | 28.2844 | -15.38 | Lusaka | 2.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P1 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | GNM | GNM | 20 | IMG | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 600 | IPT | DPR 2400B-48 | 250 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 100 |  | 1 | MTN | T0183 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 2 |  |  | pending |  | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_029M
1767 | T0295 | IHS_LSK_030M | UTH | 28.3106 | -15.4309 | Lusaka | 2.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P1 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | LSAP 40H | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 179 |  | 3 | MTNAirtelLiquid Telecom | T0295 | ZM6892 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_030M
1117 | T0140 | IHS_LSK_031M | Misisi | 28.2816 | -15.4408 | Lusaka | 1.5 | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G | P1 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Green Power | Green Power | 11 | perkins | 403D-15T | Leroy Sommer | LSA 040M5 C 6/4 | 600 | IPT | DPR 2400B-48 | 250 | Wolong | 600 | 2 | 600 | 24 | GREE | GREE | 12000 | 12000 | 2 | 40 |  | 1 | MTN | T0140 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_031M
451 | T0152 | IHS_LSK_032M | John Laing | 28.267 | -15.4373 | Lusaka | 2 | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | Yanmar | 4TNE88-G1A | Mecc Alte | ECO 28-1LN/4 | 1000 | Power cube | ECC500 | 600 | Lithium | 200 | 48 | 100 | 2 | LG | LG | 12000 | 12000 | 2 | 110 |  | 2 | MTNAirtel | T0152 | ZM0561 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_032M
490 | T0035 | IHS_LSK_034M | Kabwata | 28.3039 | -15.44 | Lusaka | 4.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Vitalgen | Vitalgen | 30 | perkins | 1103A-33 | Leroy Sommer | LSAP 423F | 1000 | Power cube | ICC330-H1-C1 | 400 | Wolong | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 110 |  | 3 | MTNAirtelLiquid Telecom | T0035 | ZM0374 | NO |  | Working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_034M
1034 | T0038 | IHS_LSK_035M | Mass Media | 28.3215 | -15.4069 | Lusaka | N/A | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | HUB | HUB | On air | Grid-Gen | Green Field | 80 | Indoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Power cube | ICC330-H1-C1 | 400 | C&D True | 1056 | 12 | 176 | 24 | GREE | GREE | 12000 | 12000 | 2 | 208 |  | 5 | MTNAirtelLiquid TelecomCgrateAir-link | T0038 | ZM6888 | YES |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_035M
398 | T0241 | IHS_LSK_036M | Heavy Industrial | 28.2535 | -15.401 | Lusaka | 2.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | GNM | GNM | 20 | perkins | 403A-15 | Leroy Sommer | LSA 42.3VS2 J 6/4 | 1000 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 98 |  | 1 | MTN | T0241 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | yes | Yes |  | 1 |  |  | Done | 2019-05-29 | Yes | No | Yes |  |  | Pending | 20 |  | Pending |  |  |  |  | IHS_LSK_036M
1796 | T0306 | IHS_LSK_037M | Zambian Italian Hospital (Radian) | 28.3213 | -15.4217 | Lusaka | 2.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Earth Technology | Earth technology | 20 | perkins | 403A-15 | Leroy Sommer | LSAP 40H | 375 | Power cube | ICC330-H1-C1 | 400 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 120 |  | 2 | MTNLiquid Telecom | T0306 | 0 | NO |  | YES | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | Done |  | No | No | Yes |  |  | Pending | 20 |  | Pending |  |  |  |  | IHS_LSK_037M
1654 | T0086 | IHS_LSK_038M | Simon Mwansa Kapwepwe | 28.2964 | -15.3739 | Lusaka | 2.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Earth Technology | Earth technology | 20 | perkins | 403A-15 | Leroy Sommer | LSA 40M5 C 6/4 | 375 | IPT | DPR 2400B-48 | 250 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 190 |  | 2 | MTNAirtel | T0086 | ZM0142 | NO |  | Working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | Yes |  |  | Pending | 20 |  | Pending |  |  |  |  | IHS_LSK_038M
1039 | T0176 | IHS_LSK_039M | Matero Boys Basic School | 28.2592 | -15.3848 | Lusaka | 2.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | GNM | GNM | 20 | perkins | 403A-22 | Leroy Sommer | TAL 040 DJ 6S/4 | 1000 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 12000 | 12000 | 2 | 100 |  | 1 | MTN | T0176 | 0 | YES |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_039M
1713 | T0026 | IHS_LSK_040M | Stadium | 28.2701 | -15.3736 | Lusaka | 5.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P1 | HUB | HUB | On air | Grid-Gen | Green Field | 50 | Indoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 45 | perkins | 403A-15 | Leroy Sommer | TAL 040 DJ 6S/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 4 | 225 |  | 3 | MTNAirtelParatus Telecom | T0026 | ZM1252 | YES |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_040M
577 | T0100 | IHS_LSK_041M | Kalundu | 28.3193 | -15.3826 | Lusaka | 4.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | CK Works | CK Works | 30 | perkins | 403A-15 | Leroy Sommer | LSAP 423F | 1000 | Power cube | ECC500 | 400 | Wolong | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 150 |  | 3 | MTNAirtelLiquid Telecom | T0100 | ZM0156 | N0 |  | No working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_041M
332 | T0282 | IHS_LSK_043M | Dell Motors | 28.2677 | -15.4514 | Lusaka | 2.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P1 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | NARADA | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 162 |  | 3 | MTNAirtelLiquid Telecom | T0282 | ZM0515 | NO |  | YES | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 2 |  |  | Done | 2019-05-28 | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_043M
610 | T0083 | IHS_LSK_044M | Kamwala South | 28.2956 | -15.4553 | Lusaka | 2.5 | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404D-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 200 | 48 | 100 | 2 | CHIGO | CHIGO | 18000 | 18000 | 2 | 208 |  | 2 | MTNAirtel | T0083 | ZM0096 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | Yes |  |  | Pending | 30 |  | Pending |  |  |  |  | IHS_LSK_044M
1801 | T0307 | IHS_LSK_045M | Zecco 2 RIF | 28.2464 | -15.388 | Lusaka | 2.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 500 | 48 | 100 | 5 | N/A | N/A | N/A | N/A | N/A | 120 |  | 3 | MTNAirtelLiquid Telecom | T0307 | ZM0095 | NO |  | Working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_045M
1211 | T0080 | IHS_LSK_046M | Mukandawire | 28.3225 | -15.4414 | Lusaka | 2 | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Indoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88-G1A | Mecc Alte | ECO28-SN/4 | 1000 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 179 |  | 2 | MTNINQ | T0080 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_046M
637 | T0101 | IHS_LSK_047M | Kanyama 2 | 28.2494 | -15.4408 | Lusaka | 1.8 | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Indoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | GNM | GNM | 15 | perkins | 403A-15 | Leroy Sommer | LSA 42.3VS2 J 6/4 | 600 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | CHIGO | CHIGO | 18000 | 18000 | 2 | 53 |  | 1 | MTN | T0101 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_047M
1042 | T0300 | IHS_LSK_048M | Matero Girls Sec School | 28.2512 | -15.3771 | Lusaka | 1.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 13 | perkins | 403A-22 | Mecc Alte | ECO28-SN/4 | 1000 | IPT | DPR 2400B-48 | 250 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 92 |  | 2 | MTNLiquid Telecom | T0300 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_048M
1570 | T0085 | IHS_LSK_049M | Roma Girls | 28.3131 | -15.3681 | Lusaka | 4.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 1103A-33 | Leroy Sommer | LSAP 423F | 1000 | Power cube | ECC500 | 400 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 18000 | 18000 | 2 | 145 |  | 4 | MTNAirtelLiquid TelecomParatus Telecom | T0085 | ZM0159 | NO |  | No working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_049M
578 | T0237 | IHS_LSK_050M | Kalundu | 28.3295 | -15.3847 | Lusaka | 2.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | IMG | IMG | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | ECC500 | 400 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 95 |  | 4 | MTNAirtelINQLiquid Telecom | T0237 | ZM0790 | NO |  | No working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_050M
1671 | T0149 | IHS_LSK_051M | Small Airport | 28.3367 | -15.4149 | Lusaka | 2 | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G 4G | P2 | BTS | Hub | On air | Grid-Gen | Green Field | 42 | Indoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88-G1A | Leroy Sommer | LSC 28S2 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 90 |  | 2 | MTNINQ | T0149 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | Pending | 20 |  | Pending |  |  |  |  | IHS_LSK_051M
808 | T0153 | IHS_LSK_052M | Libala | 28.318 | -15.4499 | Lusaka | 1.8 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 15 | Yanmar | 4TNE88-G1A | Mecc Alte | ECO28-1LN/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | NARADA | 1200 | 2 | 600 | 48 | SAMSUNG | SAMSUNG | 12000 | 12000 | 2 | 87 |  | 2 | MTNLiquid Telecom | T0153 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | Pending | 20 |  | Pending |  |  |  |  | IHS_LSK_052M
959 | T0117 | IHS_LSK_053M | Makeni East | 28.2703 | -15.4592 | Lusaka | 4.5 | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G 4G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 404A-15 | Leroy Sommer | ECP-28-M/4 | 1000 | Power cube | ECC500 | 600 | Lithium | 200 | 48 | 100 | 2 | LG | LG | 18000 | 18000 | 2 | 113 |  | 3 | MTNAirtelINQ | T0117 | ZM0113 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_053M
117 | T0291 | IHS_LSK_054M | Chawama East | 28.2766 | -15.4621 | Lusaka | 1.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 11 | perkins | 403D-15 | Mecc Alte | ECP 28-1L/4 | 1000 | IPT | DPR 2400B-48 | 250 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 62 |  | 2 | MTNLiquid Telecom | T0291 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_054M
641 | T0143 | IHS_LSK_055M | Kanyama West | 28.2349 | -15.426 | Lusaka | 1.5 | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G 4G | P1 | BTS | BB | On air | Grid-Gen | Green Field | 36 | Indoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | MPMC | MPMC | 13 | perkins | 403A-15 | Leroy Sommer | LSA 40M5 C 6/4 | 1000 | IPT | DPR 2400B-48 | 250 | Amaron | 400 | 2 | 400 | 24 | CHIGO | CHIGO | 18000 | 18000 | 2 | 69 |  | 1 | MTN | T0143 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_055M
551 | T0137 | IHS_LSK_057M | Kalingalinga | 28.3421 | -15.4019 | Lusaka | 2 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 48 | Indoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88-G1A | Mecc Alte | ECO28-1LN/4 | 600 | IPT | DPR 2400B-48 | 250 | Agisson | 600 | 2 | 600 | 24 | CHIGO | CHIGO | 18000 | 18000 | 2 | 116 |  | 1 | MTN | T0137 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_057M
380 | T0206 | IHS_LSK_058M | George | 28.2342 | -15.388 | Lusaka | 2.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G | P1 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | CK Works | CK Works | 20 | perkins | 403A-15 | Leroy Sommer | LSA 40M5 C 6/4 | 1000 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 75 |  | 2 | MTNAirtel | T0206 | ZM3524 | NO |  | Working | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | Done | 2019-05-29 | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_058M
814 | T0067 | IHS_LSK_059M | Lilanda | 28.2433 | -15.3728 | Lusaka | 4.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | HUB | HUB | On air | Grid-Gen | Green Field | 66 | Indoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | HIMOINSA | HIMOINSA | 30 | Yanmar | 4TNV98-GGEH | HIMOINSA | S 160 LB | 1000 | Power cube | ECC500 | 400 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 120 |  | 1 | MTN | T0067 | 0 | YES |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_059M
1781 | T0027 | IHS_LSK_060M | Woodlands | 28.3429 | -15.4301 | Lusaka | 65 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P3 | HUB | Hub | On air | Grid-Gen | Green Field | 50 | Indoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 65 | perkins | 403D-15T | Leroy Sommer | LSAP42.3K | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 25000 | 25000 | 2 | 250 |  | 5 | MTNAirtelLiquid( Former Hai)Liquid TelecomSmartnet | T0027 | ZM0373 | YES |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_060M
482 | T0313 | IHS_LSK_061M | Kabulonga Girls | 28.3461 | -15.4207 | Lusaka | 1.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 11 | perkins | 403D-15 | Mecc Alte | ECP 28-1L/4 | 1000 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 103 |  | 3 | MTNINQLiquid Telecom | T0313 | 0 | N0 |  | No working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_061M
183 | T0178 | IHS_LSK_062M | Chilenje South | 28.3321 | -15.4515 | Lusaka | 2.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | MPMC | MPMC | 20 | perkins | 403A-15 | Leroy Sommer | LSA 40M5 C 6/4 | 1000 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 12000 | 12000 | 2 | 97 |  | 1 | MTN | T0178 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 2 |  |  | pending |  | Yes | No | Yes |  |  | Pending | 20 |  | Pending |  |  |  |  | IHS_LSK_062M
606 | T0059 | IHS_LSK_063M | Kamulanga | 28.2925 | -15.4711 | Lusaka | 4.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G | P2 | BTS | BB | On air | Grid-Gen | Green Field | 50 | Indoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Vitalgen | Vitalgen | 40 | perkins | 404 | Leroy Sommer | LSAP 423F | 1000 | Power cube | ICC330-H1-C1 | 400 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 12000 | 12000 | 2 | 134 |  | 3 | MTNAirtelLiquid Telecom | T0059 | ZM0514 | YES |  | Working | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 2 |  |  | Done | 2019-06-30 | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_063M
1262 | T0136 | IHS_LSK_064M | Munali Sec School | 28.3437 | -15.3842 | Lusaka | 4.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | CK Works | CK Works | 30 | perkins | 404A-22 | Leroy Sommer | SAP 40H J 6S/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | CHIGO | CHIGO | 18000 | 18000 | 2 | 120 |  | 2 | MTNLiquid Telecom | T0136 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | Pending | 30 |  | Pending |  |  |  |  | IHS_LSK_064M
306 | T0163 | IHS_LSK_065M | Chunga | 28.2471 | -15.3617 | Lusaka | 2.5 | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Earth Technology | Earth technology | 20 | perkins | 4TNE88-G1A | Mecc Alte | ECO28-1LN/4 | 375 | IPT | DPR 2400B-48 | 250 | Lithium | 300 | 48 | 100 | 3 | GREE | GREE | 12000 | 12000 | 2 | 65 |  | 1 | MTN | T0163 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | Done |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_065M
1447 | T0020 | IHS_LSK_066M | Ngombe | 28.3301 | -15.3636 | Lusaka | 1.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BB | On air | Grid-Gen | Green Field | 50 | Indoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Green Power | Green Power | 10 | perkins | 403D-15T | Leroy Sommer | LSA 040M5 C 6/4 | 1000 | IPT | DPR 2400B-48 | 250 | Wolong | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 110 |  | 1 | MTN | T0020 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | Yes |  |  | Pending | 20 |  | Pending |  |  |  |  | IHS_LSK_066M
178 | T0296 | IHS_LSK_067M | Chilenje | 28.3403 | -15.4446 | Lusaka | 1.5 | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | MPMC | MPMC | 13 | perkins | 403A-15 | Leroy Sommer | LSA 40M5 C 6/4 | 1000 | IPT | DPR 2400B-48 | 250 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 54 |  | 1 | MTN | T0296 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | Done |  | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_067M
638 | T0331 | IHS_LSK_068M | Kanyama Central | 28.2307 | -15.4388 | Lusaka | 4.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G | P1 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 404D-22 | Mecc Alte | ECP 28-1L/4 | 1000 | Power cube | DPR 2400B-48 | 250 | Lithium | 600 | 48 | 100 | 6 | N/A | N/A | N/A | N/A | N/A | 113 |  | 3 | MTNAirtelLiquid Telecom | T0331 | ZM0134 | YES |  | YES | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_068M
305 | T0238 | IHS_LSK_069M | Chudleigh | 28.3418 | -15.3714 | Lusaka | 2 | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G 4G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | CK Works | CK Works | 16 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | IPT | DPR 2400B-48 | 250 | Agisson | 800 | 2 | 800 | 24 | N/A | N/A | N/A | N/A | N/A | 40.2 |  | 1 | MTN | T0238 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | Yes |  |  | yes - Emergency | 20 | 43658 | closed |  |  |  |  | IHS_LSK_069M
1805 | T0303 | IHS_LSK_070M | Zingalume | 28.2293 | -15.3741 | Lusaka | 4.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P1 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Vitalgen | Vitalgen | 30 | perkins | 404A-22 | Mecc Alte | ECP 28-M/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | N/A | N/A | 165 |  | 3 | MTNAirtelLiquid Telecom | T0303 | ZM0430 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_070M
481 | T0098 | IHS_LSK_071M | Kabulonga | 28.3558 | -15.4164 | Lusaka | 4.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P3 | BTS | BB | On air | Gen Only | Green Field | 54 | Indoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | CK Works | CK Works | 30 | perkins | 403A-15 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 12000 | 12000 | 2 | 100 |  | 2 | MTNLiquid Telecom | T0098 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 2 |  |  | Done | 2019-05-22 | No | No | Yes |  |  | yes | 30 |  | Pending |  |  |  |  | IHS_LSK_071M
84 | T0075 | IHS_LSK_072M | Chalala | 28.3231 | -15.4689 | Lusaka | 2 | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G 4G | P1 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Indoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88-G1A | Mecc Alte | ECO28-1LN/4 | 1000 | IPT | DPR 2400B-48 | 250 | Lithium | 200 | 48 | 100 | 2 | CHIGO | CHIGO | 18000 | 18000 | 2 | 85 |  | 1 | MTN | T0075 | 0 | YES |  | Working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | Done | 2019-05-22 | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_072M
1782 | T0320 | IHS_LSK_073M | Woodlands B | 28.3497 | -15.4443 | Lusaka | 2.5 | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G 4G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M4 | 1000 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 67 |  | 1 | MTN | T0320 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_073M
1510 | T0203 | IHS_LSK_074M | Nyunba Yanga | 28.3541 | -15.4364 | Lusaka | 2.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | Yanmar | 4TNE88-G1A | Mecc Alte | ECO28-1LN/4 | 1000 | IPT | DPR 2400B-48 | 250 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 67 |  | 2 | MTNLiquid Telecom | T0203 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_074M
35 | T0028 | IHS_LSK_075M | Bayuni | 28.2497 | -15.4715 | Lusaka | 2 | Lusaka | LUSAKA | Yes | Yes | No | Suburban | 2G 3G 4G | P2 | BTS | Hub | On air | Grid-Gen | Green Field | 36 | Indoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88-G1A | Mecc Alte | ECO 28-1LN/4 | 1000 | IPT | DPR 2400B-48 | 250 | Wolong | 600 | 2 | 600 | 24 | LG | LG | 12000 | 12000 | 2 | 108 |  | 1 | MTN | T0028 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_075M
816 | T0318 | IHS_LSK_076M | Lilanda West | 28.2326 | -15.3633 | Lusaka | 4.5 | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | CK Works | CK Works | 20 | perkins | 403A-15 | Leroy Sommer | LSA 40M5 C 6/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | N/A | N/A | 130 |  | 2 | MTNAirtel | T0318 | ZM0093 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | Done | 2019-05-30 | No | No | Yes |  |  | Pending | 20 |  | Pending |  |  |  |  | IHS_LSK_076M
75 | T0005 | IHS_LSK_077M | Chainama | 28.3568 | -15.3903 | Lusaka | 5.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P3 | HUB | HUB | On air | Grid-Gen | Green Field | 50 | Indoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | CK Works | CK Works | 45 | perkins | 4TNV98-GGEH | Leroy Sommer | TAL 042C J 6/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 246 |  | 4 | MTNAirtelINQLiquid Telecom | T0005 | ZM0172 | YES |  | Working | Mesh | Inala | 2022-08-05 | Yes | Yes |  | 2 |  |  | Done | 2019-05-22 | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_077M
1258 | T0240 | IHS_LSK_078M | Munali Girls (Kaunda Square 2) | 28.3533 | -15.3793 | Lusaka | 1.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 11 | perkins | 403D-15 | Mecc Alte | ECP 28-1L/4 | 1000 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 42.1 |  | 2 | MTNLiquid Telecom | T0240 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_078M
968 | T0148 | IHS_LSK_079M | Makeni Simpson | 28.2262 | -15.4556 | Lusaka | 4.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P3 | HUB | HUB | On air | Grid-Gen | Green Field | 48 | Indoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Lamasat | Lamasat | 30 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 800 | Power cube | ICC330-H1-C1 | 400 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 12000 | 12000 | 2 | 106 |  | 2 | MTNLiquid Telecom | T0148 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_079M
16 | T0001 | IHS_LSK_080M | Athur Wina | 28.3508 | -13.8298 | Lusaka | 4.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | HUB | HUB | On air | Grid-Gen | Green Field | 55 | Indoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Vitalgen | Vitalgen | 30 | perkins | 1103A-33 | Leroy Sommer | TAL 042C J 6/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 185 |  | 2 | MTNLiquid Telecom | T0001 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_080M
445 | T0155 | IHS_LSK_081M | Jack Compound | 28.3002 | -15.4905 | Lusaka | 2 | Lusaka | LUSAKA | Yes | No | No | Urban | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 48 | Indoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88-G1A | Mecc Alte | ECO28-1LN/4 | 1000 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | GREE | GREE | 18000 | 18000 | 2 | 25 |  | 1 | MTN | T0155 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_081M
614 | T0224 | IHS_LSK_082M | Kamwema Meanwood | 28.3487 | -15.3565 | Lusaka | 4.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 1103A-33 | Leroy Sommer | TAL 042C J 6/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Wolong | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 135 |  | 2 | MTNAirtel | T0224 | ZM6731 | N0 |  | No working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_082M
1184 | T0222 | IHS_LSK_083M | Mtendere 2 | 28.3685 | -15.3998 | Lusaka | 4.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | CK Works | CK Works | 30 | perkins | 403A-15 | Mecc Alte | ECP-28-M/4 | 1000 | IPT | DPR 2400B-48 | 250 | Wolong | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 146 |  | 2 | MTNAirtel | T0222 | ZM6188 | N0 |  | Working | Palisade | Inala | 2022-08-05 | Yes | No |  |  |  |  | pending |  | Yes | No | Yes |  |  | Pending | 30 |  | Pending |  |  |  |  | IHS_LSK_083M
86 | T0293 | IHS_LSK_084M | Chalala Rockfield | 28.3467 | -15.4693 | Lusaka | 2.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | CK Works | CK Works | 45 | perkins | 403A-15 | Mecc Alte | LSA 40M5 C 6/4 | 1000 | IPT | DPR 2400B-48 | 250 | Wolong | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 210 |  | 4 | MTNAirtelINQLiquid Telecom | T0293 | ZM0416 | YES |  | Working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | Yes | No | Yes |  |  | Pending | 30 |  | Pending |  |  |  |  | IHS_LSK_084M
636 | T0058 | IHS_LSK_085M | Kanyama (Lusaka West School) | 28.2052 | -15.4378 | Lusaka | 4.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P3 | BB | BB | On air | Grid-Gen | Green Field | 60 | Indoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | HIMOINSA | HIMOINSA | 30 | Yanmar | 4TNV98-GGEH | HIMOINSA | S 160 LB | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | GREE | GREE | 12000 | 12000 | 2 | 163 |  | 2 | MTNAirtel | T0058 | ZM6860 | YES |  | No working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_085M
411 | T0095 | IHS_LSK_086M | Ibex Bahai | 28.3733 | -15.4306 | Lusaka | 4.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 48 | Indoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Vitalgen | Vitalgen | 30 | perkins | 1103A-33 | Leroy Sommer | TAL 042C J 6/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 200 | 48 | 100 | 2 | LG | LG | 12000 | 12000 | 2 | 140 |  | 3 | MTNAirtelLiquid Telecom | T0095 | ZM6854 | YES |  | Working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | Done | 2019-05-22 | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_086M
1696 | T0087 | IHS_LSK_087M | St Charles | 28.2019 | -15.3822 | Lusaka | 2.5 | Lusaka | LUSAKA | Yes | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Lamasat | Lamasat | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 600 | Power cube | ECC500 | 400 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 160 |  | 2 | MTNAirtel | T0087 | ZM6846 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_087M
1482 | T0168 | IHS_LSK_088M | NRDC | 28.3729 | -15.378 | Lusaka | 2.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Vitalgen | Vitalgen | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | SAMSUNG | SAMSUNG | 12000 | 12000 | 2 | 158 |  | 3 | MTNAirtelLiquid Telecom | T0168 | ZM0375 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | Pending | 30 |  | Pending |  |  |  |  | IHS_LSK_088M
1078 | T0363 | IHS_LSK_089M | Meanwood Chamba Valley | 28.3409 | -15.3356 | Lusaka | 2.5 | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 404D-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | IPT | DPR 2400B-48 | 250 | Wolong | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 50 |  | 1 | MTN | T0363 | 0 | N0 |  | No working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_089M
412 | T0146 | IHS_LSK_090M | Ibex Hill | 28.3795 | -15.4028 | Lusaka | 2.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 403A-22 | Leroy Sommer | TAL 040 DJ 6S/4 | 1000 | IPT | DPR 2400B-48 | 250 | Wolong | 600 | 2 | 600 | 24 | GREE | GREE | 12000 | 12000 | 2 | 77 |  | 1 | MTN | T0146 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_090M
957 | T0154 | IHS_LSK_091M | Makeni | 28.238 | -15.4925 | Lusaka | 2.5 | Lusaka | LUSAKA | Yes | No | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 42 | Indoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 12000 | 12000 | 2 | 112 |  | 4 | MTNAirtelINQLiquid Telecom | T0154 | ZM6727 | NO |  | No working | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 2 |  |  | Done | 2019-05-22 | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_091M
583 | T0078 | IHS_LSK_092M | Kamanga | 28.377 | -15.3646 | Lusaka | 2.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P1 | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Wolong | 1200 | 2 | 600 | 48 | GREE | GREE | 12000 | 12000 | 2 | 108 |  | 3 | MTNLiquid TelecomParatus Telecom | T0078 | 0 | N0 |  | No working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_092M
956 | T0145 | IHS_LSK_093M | Makeni | 28.2091 | -15.4741 | Lusaka | 2 | Lusaka | LUSAKA | Yes | No | No | Urban | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 42 | Indoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88-G1A | Leroy Sommer | LSC 28S2 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | CHIGO | CHIGO | 18000 | 18000 | 2 | 120 |  | 4 | MTNAirtelINQLiquid Telecom | T0145 | ZM6728 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | Pending | 20 |  | Pending |  |  |  |  | IHS_LSK_093M
33 | T0219 | IHS_LSK_094M | Bauleni | 28.3814 | -15.4472 | Lusaka | 4.5 | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | HIMOINSA | HIMOINSA | 30 | Yanmar | SK160LB | HIMOINSA | SK160LB | 1000 | Power cube | ICC330-HA1-C10 | 600 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | N/A | N/A | 145 |  | 2 | MTNAirtel | T0219 | ZM0564 | N0 |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_094M
818 | T0138 | IHS_LSK_095M | Lilayai Farms | 28.3372 | -15.499 | Lusaka | 2.5 | Lusaka | LUSAKA | No | No | No | Suburban | 2G 3G 4G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 42 | Indoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | GNM | GNM | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 600 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | GREE | GREE | 12000 | 12000 | 2 | 110 |  | 2 | MTNAirtel | T0138 | ZM6858 | NO |  | Working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_095M
927 | T0135 | IHS_LSK_096M | Lutheran | 28.3872 | -15.3885 | Lusaka | 4.5 | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 48 | Indoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 403A-15 | Leroy Sommer | LSA 40M5 C 6/4 | 1000 | Power cube | ICC330-HA1-C10 | 400 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 89 |  | 3 | MTNAirtelLiquid Telecom | T0135 | ZM0163 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | Done |  | Yes | No | Yes |  |  | Pending | 20 |  | Pending |  |  |  |  | IHS_LSK_096M
1431 | T0081 | IHS_LSK_097M | New Kasama | 28.3787 | -15.458 | Lusaka | 4.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | GN66044U | Mecc Alte | ECO28-VL/4 | 1000 | IPT | DPR 2400B-48 | 250 | Wolong | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 95 |  | 2 | MTNLiquid Telecom | T0081 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | Yes | No | Yes |  |  | Pending | 20 |  | Pending |  |  |  |  | IHS_LSK_097M
1432 | T0150 | IHS_LSK_098M | New Kasama | 28.3662 | -15.4767 | Lusaka | 4.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G | P4 | HUB | HUB | On air | Grid-Gen | Green Field | 54 | Indoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 4TNE88-G1A | Mecc Alte | ECO28-1LN/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 103 |  | 1 | MTN | T0150 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | Pending | 20 |  | Pending |  |  |  |  | IHS_LSK_098M
817 | T0105 | IHS_LSK_099M | Lilayai | 28.2839 | -15.5139 | Lusaka | 2 | Lusaka | LUSAKA | Yes | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 48 | Indoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88-G1A | Mecc Alte | ECO28-1LN/4 | 1000 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | EVO | EVO | 18000 | 18000 | 2 | 103 |  | 3 | MTNAirtelLiquid Telecom | T0105 | ZM6757 | NO |  | Working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | Yes | No | Yes |  |  | Pending | 20 |  | Pending |  |  |  |  | IHS_LSK_099M
1562 | T0039 | IHS_LSK_100M | Rivonia | 28.2001 | -15.3455 | Lusaka | 1.5 | Lusaka | LUSAKA | No | No | No | Suburban | 2G 3G | P4 | BTS | Hub | On air | Grid-Gen | Green Field | 50 | Indoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | MPMC | MPMC | 15 | perkins | 403A-15 | Leroy Sommer | LSA 40M5 C 6/4 | 1000 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 48 |  | 1 | MTN | T0039 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_100M
1555 | T0321 | IHS_LSK_101M | Ranchsdale | 28.3793 | -15.3457 | Lusaka | 2.5 | Lusaka | LUSAKA | Yes | Yes | No | Suburban | 2G 3G 4G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 135 |  | 3 | MTNAirtelLiquid Telecom | T0321 | ZM6663 | N0 |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | Pending | 30 |  | Pending |  |  |  |  | IHS_LSK_101M
1182 | T0290 | IHS_LSK_102M | Mt. Makulu | 28.2358 | -15.5134 | Lusaka | 1.8 | Lusaka | LUSAKA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 404D-22 | Mecc Alte | ECP 28-1L/4 | 1000 | IPT | DPR 2400B-48 | 250 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 91 |  | 3 | MTNAirtelLiquid Telecom | T0290 | ZM6855 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_102M
20 | T0207 | IHS_LSK_103M | Avondale Complex | 28.4006 | -13.7146 | Lusaka | 4.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 404A-22 | Leroy Sommer | TAL 042C J 6/4 | 1000 | Power cube | ICC330-HA1-C10 | 600 | Wolong | 1200 | 2 | 600 | 48 | GREE | GREE | 12000 | 12000 | 2 | 176 |  | 3 | MTNAirtelLiquid Telecom | T0207 | ZM0296 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | Yes |  |  | yes | 30 |  | Pending |  |  |  |  | IHS_LSK_103M
19 | T0073 | IHS_LSK_104M | Avondale | 28.4053 | -14.2418 | Lusaka | 5.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G | P4 | HUB | BB | On air | Grid-Gen | Green Field | 54 | Indoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | CK Works | CK Works | 45 | perkins | 4TNV98-GGEH | Leroy Sommer | TAL A42F J 6S/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 600 | 48 | 100 | 6 | LG | LG | 18000 | 18000 | 2 | 180 |  | 3 | MTNAirtelLiquid Telecom | T0073 | ZM3771 | YES |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_104M
1433 | T0270 | IHS_LSK_105M | New Kasama | 28.3924 | -15.4766 | Lusaka | 4.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P4 | HUB | HUB | On air | Grid-Gen | Green Field | 36 | Outdoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 403D-15 | Leroy Sommer | TAL 042C J 6/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 152 |  | 4 | MTNAirtelINQLiquid Telecom | T0270 | ZM3476 | YES |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_105M
176 | T0006 | IHS_LSK_106M | Chilanga | 28.2704 | -15.5351 | Lusaka | 4.5 | Lusaka | LUSAKA | Yes | No | No | Suburban | 2G 3G 4G | P1 | BB | Hub | On air | Grid-Gen | Green Field | 50 | Indoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 1103A-33 | Leroy Sommer | TAL 042C J 6/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | NARADA | 1200 | 2 | 600 | 48 | GREE | GREE | 12000 | 12000 | 2 | 95 |  | 2 | MTNLiquid Telecom | T0006 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 2 |  |  | Done | 2019-05-22 | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_106M
1449 | T0079 | IHS_LSK_107M | Ngwerere | 28.3611 | -15.3003 | Lusaka | 4.5 | Lusaka | LUSAKA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Indoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Falcon | Falcon | 20 | perkins | 403A-15 | Leroy Sommer | LSA 40M5 C 6/4 | 1000 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | GREE | GREE | 12000 | 12000 | 2 | 189 |  | 2 | MTNAirtel | T0079 | ZM0420 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_107M
963 | T0082 | IHS_LSK_108M | Makeni GRZ School | 28.1756 | -15.4855 | Lusaka | 2 | Lusaka | LUSAKA | Yes | No | No | Urban | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88-G1A | Leroy Sommer | LSC 28S2 | 1000 | IPT | DPR 2400B-48 | 250 | Lithium | 200 | 48 | 100 | 2 | LG | LG | 18000 | 18000 | 2 | 54 |  | 2 | MTNLiquid Telecom | T0082 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_108M
822 | T0072 | IHS_LSK_109M | Linda | 28.2384 | -15.5453 | Lusaka | 4.5 | Lusaka | LUSAKA | No | No | No | Urban | 2G 3G 4G | P2 | BB | Hub | On air | Grid-Gen | Green Field | 44 | Indoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 1103A-33 | Leroy Sommer | TAL 042C J 6/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 170 |  | 3 | MTNAirtelParatus Telecom | T0072 | ZM6863 | YES |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_109M
4 | T0000 | IHS_LSK_110M | Airport | 28.4239 | -13.6351 | Lusaka | 2.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 20 | Indoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | IPT | DPR 2400B-48 | 250 | Agisson | 600 | 2 | 600 | 24 | CHIGO | CHIGO | 18000 | 18000 | 2 | 65 |  | 1 | MTN | T0000 | 0 | YES |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_110M
1778 | T0185 | IHS_LSK_112M | Wilderness (Pebble Brook) | 28.4507 | -15.4315 | Lusaka | 1.5 | Lusaka | LUSAKA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 40 | Indoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 11 | perkins | 404A-22 | Mecc Alte | ECO 28-1LN/4 | 1000 | IPT | DPR 2400B-48 | 250 | Wolong | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 45 |  | 1 | MTN | T0185 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_112M
1722 | T0066 | IHS_LSK_113M | T0066_INTER-AIRPORT | 28.4469 | -15.3255 | Lusaka | N/A | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid Only | Roof Top | RT | Indoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | In House | In House | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | IPT | DPS 2400B-48 | 250 | DENG TA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 95 |  | 1 | MTN | T0066 | 0 |  |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_113M
799 | T0254 | IHS_LSK_115M | Kyindu Ranch | 28.4699 | -15.4737 | Lusaka | 1.5 | Lusaka | LUSAKA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 403D-15 | Mecc Alte | ECP 28-1L/4 | 1000 | IPT | DPR 2400B-48 | 250 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 100 |  | 1 | MTN | T0254 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_115M
922 | T0108 | IHS_LSK_116M | Lusaka West Barrack | 28.11 | -15.3228 | Lusaka |  | Lusaka | LUSAKA | No | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 48 | Outdoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | #N/A | #N/A | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | Lithium | 500 | 48 | 100 | 5 | N/A | N/A | N/A | N/A | N/A | 151 |  | 2 | MTNAirtel | T0108 | ZM6128 | NO |  | No working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | Yes | No | Yes |  |  | Pending | 20 |  | Pending |  |  |  |  | IHS_LSK_116M
1014 | T0263 | IHS_LSK_117M | Mapepe | 28.2561 | -15.6231 | Lusaka | 1.5 | Lusaka | KAFUE | No | No | No | Rural | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | MPMC | MPMC | 13 | perkins | 403A-15 | Leroy Sommer | LSA 40M5 C 6/4 | 1000 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 75 |  | 2 | MTNAirtel | T0263 | ZM0419 | NO |  | YES | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_117M
224 | T0232 | IHS_LSK_119M | Chinyuyu (Hilltop Farms) | 28.1111 | -15.5585 | Lusaka | N/A | Lusaka | KAFUE | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On air | Grid only | Green Field | 36 | Outdoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | In House | In House | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A | N/A | N/A | N/A | 61 |  | 1 | MTN | T0232 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_119M
706 | T0103 | IHS_LSK_120M | Kasisi | 28.4725 | -15.2697 | Lusaka | 2 | Lusaka | LUSAKA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Outdoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88-G1A | Mecc Alte | ECO28-1LN/4 | 1000 | IPT | DPR 2400B-48 | 250 | Wolong | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 60 |  | 1 | MTN | T0103 | 0 | YES |  | No working | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_120M
1517 | T0043 | IHS_LSK_121M | Palabana | 28.5321 | -15.4446 | Lusaka | 2.5 | Lusaka | CHONGWE | No | No | No | Suburban | 2G 3G | P4 | BB | BB | On air | Grid-Gen | Green Field | 50 | Indoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404D-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | IPT | DPR 2400B-48 | 250 | Lithium | 200 | 48 | 100 | 2 | CHIGO | CHIGO | 18000 | 18000 | 2 | 174 |  | 1 | MTN | T0043 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_121M
220 | T0084 | IHS_LSK_123M | Chinyanja basic School | 28.0092 | -15.3908 | Lusaka | 2 | Lusaka | LUSAKA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Indoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Yanmar | Yanmar | 16 | Yanmar | 4TNE88-G1A | Leroy Sommer | LSC 28S2 | 600 | U | DPR 2400B-48 | 250 | Amaron | 600 | 2 | 600 | 24 | LG | LG | 12000 | 12000 | 2 | 85 |  | 2 | MTNAirtel | T0084 | ZM6153 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_123M
518 | T0011 | IHS_LSK_124M | Kafue Gorge | 28.4493 | -15.6818 | Lusaka | 2 | Lusaka | KAFUE | No | No | No | Rural | 2G 3G | P4 | BTS | BB | On air | Grid-Gen | Green Field | 40 | Indoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | LISTER PETTER | LISTER PETTER | 16 | Lister petter | LWP4 | Leroy Sommer | LSA 42.3VS2 J 6/4 | 600 | IPT | DPR 2400B-48 | 250 | Agisson | 800 | 2 | 800 | 24 | GREE | GREE | 12000 | 12000 | 2 | 68 |  | 1 | MTN | T0011 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_124M
616 | T0151 | IHS_LSK_125M | Kanakantapa 2 | 28.6033 | -15.3215 | Lusaka | 2 | Lusaka | LUSAKA | No | No | No | Rural | 2G 3G | P4 | BTS | Hub | On air | Grid-Gen | Green Field | 54 | Indoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 17 | Yanmar | 4TNE88-G1A | Mecc Alte | ECO28-1LN/4 | 600 | IPT | DPR 2400B-48 | 250 | Power safe | 1200 | 2 | 1200 | 24 | LG | LG | 12000 | 12000 | 2 | 42.6 |  | 2 | MTNAirtel | T0151 | ZM3770 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_125M
701 | T0252 | IHS_LSK_126M | Kasenga Resettlement | 28.5464 | -15.2003 | Lusaka | 1.8 | Lusaka | CHONGWE | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Earth Technology | Earth technology | 15 | perkins | 403A-15 | Leroy Sommer | TAL 040F J 6S/4 | 375 | IPT | DPR 2400B-48 | 250 | Amaron | 400 | 2 | 400 | 24 | N/A | N/A | N/A | N/A | N/A | 35 |  | 1 | MTN | T0252 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_126M
512 | T0010 | IHS_LSK_127M | Kafue | 28.2046 | -15.7533 | Lusaka | 4.5 | Lusaka | KAFUE | Yes | No | No | Suburban | 2G 3G | P3 | BB | BB | On air | Grid-Gen | Green Field | 80 | Indoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 4TNE88-G1A | Leroy Sommer | LSC 28S2 | 1000 | Power cube | DPR 2400B-48 | 250 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 197 |  | 1 | MTN | T0010 | 0 | YES |  | No working | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | Yes | No | Yes |  |  | Pending | 20 |  | Pending |  |  |  |  | IHS_LSK_127M
1337 | T0124 | IHS_LSK_128M | Mwembeshi 2BB | 27.9388 | -15.3463 | Lusaka | 2.5 | Lusaka | LUSAKA | No | No | No | Rural | 2G 3G | P4 | BB | BB | On air | Grid-Gen | Green Field | 66 | Indoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | IMG | IMG | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 600 | IPT | DPR 2400B-48 | 250 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 70 |  | 1 | MTN | T0124 | 0 | YES |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_128M
1623 | T0277 | IHS_LSK_129M | Shikoswe East | 28.1751 | -15.7494 | Lusaka | 2.5 | Lusaka | KAFUE | No | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 131 |  | 2 | MTNAirtel | T0277 | ZM3403 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_129M
517 | T0036 | IHS_LSK_130M | Kafue Estates | 28.1642 | -15.7462 | Lusaka | 1.5 | Lusaka | KAFUE | No | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Falcon | Falcon | 13 | perkins | 403A-15 | Leroy Sommer | LSA 40M5 C 6/4 | 560 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | GREE | GREE | 18000 | 18000 | 2 | 145 |  | 1 | MTN | T0036 | 0 | YES |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_130M
1087 | T0156 | IHS_LSK_131M | Mikango Barracks | 28.6318 | -15.5309 | Lusaka | 1.8 | Lusaka | LUSAKA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Indoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 404A-22 | Mecc Alte | ECO28-1LN/4 | 1000 | IPT | DPR 2400B-48 | 250 | Wolong | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 45 |  | 1 | MTN | T0156 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_131M
522 | T0247 | IHS_LSK_132M | Kafue Kaseba | 28.1938 | -15.7911 | Lusaka | N/A | Lusaka | KAFUE | No | No | No | Suburban | 2G 3G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A | N/A | N/A | N/A | 60 |  | 1 | MTN | T0247 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_132M
838 | T0096 | IHS_LSK_133M | Lolanda Water Works | 28.2506 | -15.8125 | Lusaka | 1.5 | Lusaka | KAFUE | No | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 66 | Outdoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 13 | Yanmar | 4TNE88-G1A | Mecc Alte | ECO28-SN/4 | 1000 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 91 |  | 2 | MTNAirtel | T0096 | ZM0590 | YES |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_133M
297 | T0031 | IHS_LSK_134M | Chongwe | 28.6891 | -15.3255 | Lusaka | 2.5 | Lusaka | CHONGWE | No | No | No | Suburban | 2G 3G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | CK Works | CK Works | 20 | perkins | 403D-15 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | IPT | DPR 2400B-48 | 250 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 65 |  | 3 | MTNLiquid TelecomSmartnet | T0031 | 0 | YES |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | Yes |  |  | Pending | 16 |  | Pending |  |  |  |  | IHS_LSK_134M
273 | T2015 | IHS_LSK_135M | Chitema Lesa | 28.8944 | -15.2642 | Lusaka | N/A | Lusaka | Chongwe | No | No | No | Rural | 2G 3G | P4 | BB | BB | On air | Solar-Gen | Green Field | 54 | Indoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Emerson | Cordex | 200 | NARADA | 1200 | 2 | 600 | 48 | GREE | GREE | 12000 | 12000 | 2 | 55 |  | 1 | MTN | T2015 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 2 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  | Consolidated on IHS_LSK_253A Chitemalesa | IHS_LSK_135M
1506 | T2028 | IHS_LSK_136M | Nyautae Hill | 29.3497 | -15.1392 | Lusaka | N/A | Lusaka | CHONGWE | No | No | No | Rural | 2G | P4 | BB | BB | On air | Solar-Gen | Green Field | 66 | Indoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Emerson | Cordex | 200 | BSB | 1500 | 2 | 1500 | 24 | GREE | GREE | 12000 | 12000 | 2 | 35 |  | 1 | MTN | T2028 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  | Consolidated on IHS_LSK_252A Nyautae hill | IHS_LSK_136M
1577 | T2031 | IHS_LSK_137M | Rufunsa | 29.6793 | -15.0761 | Lusaka | 2.5 | Lusaka | CHONGWE | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Solar-Gen | Green Field | 54 | Outdoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Ghaddar | Ghaddar | 20 | perkins | S4L261SDBC | Zanardi | AL 3/4 | 600 | N/A | N/A | N/A | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 35 |  | 1 | MTN | T2031 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | pending |  | No | No | Yes |  |  | Pending | 16 |  | Pending |  |  |  |  | IHS_LSK_137M
1741 | T2034 | IHS_LSK_138M | Trabooka H BB | 29.8075 | -15.0712 | Lusaka | 2.5 | Lusaka | LUANGWA | No | No | No | Rural | 2G | P4 | BB | BB | On air | Solar-Gen | Green Field | 66 | Indoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Ghaddar | Ghaddar | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 600 | Emerson | Cordex | 200 | ROLLS | 1410 | 4 | 1500 | 12 | GREE | GREE | 12000 | 12000 | 2 | 50 |  | 1 | MTN | T2034 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_138M
1498 | T2025 | IHS_LSK_139M | Nyakuseka BB | 30.0516 | -15.0114 | Lusaka | 4.5 | Lusaka | LUANGWA | No | No | No | Rural | 2G | P4 | BB | BB | On air | Solar-Gen | Green Field | 54 | Indoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 45 | perkins | 1103A-33 | Leroy Sommer | TAL 042C J 6/4 | 1000 | Emerson | Cordex | 200 | Agisson | 1600 | 2 | 800 | 48 | GREE | GREE | 12000 | 12000 | 2 | 105 |  | 1 | MTN | T2025 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 2 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_139M
844 | T2019 | IHS_LSK_140M | Luangwa Bridge | 30.2099 | -15.0023 | Lusaka | 2.5 | Lusaka | LUANGWA | No | No | No | Rural | 2G 3G | P4 | BTS | BB | On air | Grid-Gen-solar | Green Field | 54 | Outdoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | CK Works | CK Works | 30 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Emerson | Cordex | 200 | ROLLS | 1410 | 4 | 1500 | 12 | N/A | N/A | N/A | N/A | N/A | 40 |  | 1 | MTN | T2019 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  | Consolidated on IHS_LSK_261A Luangwa bridge | IHS_LSK_140M
848 | T2020 | IHS_LSK_141M | Luangwa High School | 30.2887 | -15.2737 | Lusaka | 2.5 | Lusaka | LUANGWA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen-solar | Green Field | 54 | Indoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Emerson | Cordex | 200 | Coslight | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 35 |  | 1 | MTN | T2020 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_141M
842 | T2018 | IHS_LSK_142M | Luangwa | 30.4028 | -15.6287 | Lusaka | 2 | Lusaka | LUANGWA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Outdoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | Yanmar | 4TNE88-G1A | Mecc Alte | ECO28-1LN/4 | 1000 | IPT | DPR 2400B-48 | 250 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 35 |  | 1 | MTN | T2018 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_142M
373 | T0349 | IHS_LSK_143M | GARDEN HOUSE | 28.215 | -15.417 | Lusaka | 2.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 30 | Outdoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 600 | 48 | 100 | 6 | N/A | N/A | N/A | N/A | N/A | 156 |  | 3 | MTNAirtelLiquid Telecom | T0349 | ZM0085 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_143M
407 | T0350 | IHS_LSK_144M | HILL SIDE SCHOOL | 28.2557 | -15.3677 | Lusaka | 1.8 | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 30 | Outdoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Generator City | Generator City | 15 | Yanmar | 4TNE88-G1A | ALPHAGEN | SLG164 | 1000 | IPT | DPR 2400B-48 | 250 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 53 |  | 1 | MTN | T0350 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_144M
372 | T0351 | IHS_LSK_145M | GARDEN CENTRAL | 28.2885 | -15.3913 | Lusaka | 2.5 | Lusaka | LUSAKA | No | Yes | No | Urban | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 30 | Outdoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Generator City | Generator City | 20 | Yanmar | 4TNE88-G1A | ALPHAGEN | SLG164 | 1000 | IPT | DPR 2400B-48 | 250 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | N/A | N/A | 110 |  | 2 | MTNAirtel | T0351 | ZM0376 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | Yes |  |  | Pending | 20 |  | Pending |  |  |  |  | IHS_LSK_145M
964 | T0365 | IHS_LSK_146M | MAKENI KONGA | 28.2311 | -15.4749 | Lusaka | 1.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 30 | Outdoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Generator City | Generator City | 15 | Yanmar | 4TNE88-G1A | ALPHAGEN | SLG164 | 600 | Power cube | DPR 2400B-48 | 250 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 71 |  | 2 | MTNLiquid Telecom | T0365 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_146M
414 | T0323 | IHS_LSK_147M | IBEX MEANWOOD | 28.4265 | -15.3815 | Lusaka | 2.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 30 | Outdoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Wolong | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 128.2 |  | 3 | MTNAirtelLiquid Telecom | T0323 | ZM6861 | YES |  | No working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_147M
1256 | T0418 | IHS_LSK_148M | Mumpanshya | 29.73 | -15.1067 | Lusaka | 2.5 | Lusaka | RUFUNSA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 55 | Outdoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | CK Works | CK Works | 20 | perkins | 404D-22 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 800 | 2 | 800 | 24 | N/A | N/A | N/A | N/A | N/A | 108 |  | 2 | MTNAirtel | T0418 | ZM0286 | N0 |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_148M
1125 | T0430 | IHS_LSK_149M | Mondengwe (formerly Apollo 56) | 28.5886 | -15.3152 | Lusaka | 2.5 | Lusaka | LUSAKA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 55 | Outdoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | IMG | IMG | 20 | perkins | 404D-22 | Leroy Sommer | TAL 040F J 6S/4 | 600 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 43 |  | 1 | MTN | T0430 | 0 | NO |  | Working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_149M
17 | T0429 | IHS_LSK_150M | Avondale | 28.4028 | -13.6378 | Lusaka | 4.5 | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 55 | Outdoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 403A-15 | Mecc Alte | LSA 4OM5 | 1000 | Power cube | ICC330-HA1-C10 | 600 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | N/A | N/A | 125 |  | 3 | MTNAirtelLiquid Telecom | T0429 | ZM0185 | YES |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | Yes |  |  | Pending | 30 |  | Pending |  |  |  |  | IHS_LSK_150M
416 | T0272 | IHS_LSK_151M | IHS HQ | 28.2875 | -15.4041 | Lusaka | N/A | Lusaka | LUSAKA | Yes | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid only | Green Field | 35 | Outdoor | John Banda | SBC | SBC | MTN | Evans Ngonga | In House | In House | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Power cube | ECC500 | 400 | Lithium | 800 | 48 | 100 | 8 | N/A | N/A | N/A |  | N/A | 170 |  | 3 | MTNAirtelLiquid Telecom | T0272 | ZM0400 |  |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_151M
520 | T0011 | IHS_LSK_152M | Kafue Gorge RPT | 28.4718 | -15.8798 | Lusaka | 1.5 | Lusaka | Kafue | No | No | No | Rural | #N/A | P4 | BTS | BTS | On air | Solar-Gen | Green Field | 72 | Outdoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | RID | RID | 13 | Mitsubishi | S4L261SDBC | Zanardi | AL 3/4 | 1000 | MPPT | Eath Technologies | 3.5 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 201 |  | 2 | MTNAirtel | TX | ZM0597 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_152M
519 | T0469 | IHS_LSK_153M | Kafue Gorge RES | 28.5329 | -15.8828 | Lusaka | 1.8 | Lusaka | KAFUE | No | No | No | Rural | 2G 3G | P3 | BTS | BB | On air | Grid-Gen | Green Field | 72 | Outdoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Lamasat | Lamasat | 15 | perkins | 403A-15 | Leroy Sommer | TAL 040D J 6S/4 | 600 | IPT | DPR 2400B-48 | 250 | Power safe | 1200 | 2 | 1200 | 24 | N/A | N/A | N/A | N/A | N/A | 67 |  | 2 | MTNAirtel | T0011 | ZM0556 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_153M
64 | T0470 | IHS_LSK_154M | Carousel | 28.2807 | -15.4293 | Lusaka | N/A | Lusaka | LUSAKA | No | Yes | No | Suburban | 2G 3G | P4 | BTS | Hub | On air | Grid Only | Roof Top | RT | Outdoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | In House | In House | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | IPT |  | 0 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A |  | N/A | 47 |  | 1 | MTN | T0470 | 0 |  |  |  | n/a | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_154M
804 | T0495 | IHS_LSK_155M | Laughing Waters | 28.1703 | -15.3829 | Lusaka | 1.8 | Lusaka | Lusaka | No | No | No | Urban | P4 | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | CK Works | CK Works | 15 | perkins | 403D-15 | Leroy Sommer | TAL-A40-C J6/4 | 600 | Power cube | ECC500 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 45 |  | 1 | MTN | T0495 | 0 | YES |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_155M
971 | T0496 | IHS_LSK_156M | Makeni west 2 | 28.1761 | -15.5143 | Lusaka | 1.8 | Lusaka | Lusaka | No | No | No | Urban | P4 | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | CK Works | CK Works | 15 | perkins | 403D-15 | Leroy Sommer | TAL-A40-C J6/4 | 400 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 76 |  | 2 | MTNAirtel | T0496 | ZM6953 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_156M
374 | T0497 | IHS_LSK_157M | Garden House | 28.2072 | -15.4027 | Lusaka | 1.8 | Lusaka | Lusaka | No | No | No | Urban | P4 | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 44 | Outdoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | CK Works | CK Works | 15 | perkins | 403D-15 | Leroy Sommer | TAL-A40-C J6/4 | 600 | Power cube | ECC500 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 65 |  | 1 | MTN | T0497 | 0 | YES |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_157M
966 | T0332 | IHS_LSK_159M | Makeni Road | 28.252 | -15.4845 | Lusaka | 1.8 | Lusaka | Lusaka | No | No | No | Urban | P4 | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | CK Works | CK Works | 20 | perkins | 403D-15 | Leroy Sommer | TAL-A40-C J6/4 | 600 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 89 |  | 2 | MTNAirtel | T0502 | ZM0399 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_159M
1734 | T0504 | IHS_LSK_160M | ten miles | 28.2961 | -15.2777 | Lusaka | 1.8 | Lusaka | Lusaka | No | No | No | Urban | P4 | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | CK Works | CK Works | 15 | perkins | 403D-15 | Leroy Sommer | TAL-A40-C J6/4 | 600 | Power cube | ECC500 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 47 |  | 1 | MTN | T0504 | 0 | YES |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_160M
410 | T0510 | IHS_LSK_162M | IBEX | 28.3954 | -15.4135 | Lusaka | 1.8 | Lusaka | Lusaka | Yes | No | No | Urban | P4 | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 55 | Outdoor | Kelly Musama | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 403D-15G | Leroy Sommer | TAL-A40-C J6/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 76 |  | 2 | MTNLiquid Telecom | T0340 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_162M
1651 | T0513 | IHS_LSK_165M | silverest | 28.4729 | -15.379 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | P4 | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | CK Works | CK Works | 20 | perkins | 403D-15 | Leroy Sommer | TAL-A40-C J6/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 35 |  | 1 | MTN | T0513 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_165M
1077 | T0515 | IHS_LSK_166M | Meanwood Chamba Valley | 28.3547 | -15.3347 | Lusaka | 2.5 | Lusaka | lusaka | No | No | No | Urban | P4 | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Malvin Hakokole | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Earth Technology | Earth technology | 15 | perkins | 403D-15 | Leroy Sommer | TAL-A40-C J6/4 | 375 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 41 |  | 1 | MTN | T0534 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_166M
924 | T0517 | IHS_LSK_167M | Lusaka west-Apolo | 28.0776 | -15.3405 | Lusaka | 1.8 | Lusaka | Lusaka | No | No | No | Urban | P4 | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | John Banda | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | CK Works | CK Works | 15 | perkins | 403D-15 | Leroy Sommer | TAL-A40-C J6/4 | 600 | Power cube | ECC500 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 60 |  | 1 | MTN | T0517 | 0 | YES |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_167M
1811 |  | IHS_LSK_168M | CHALALA MALL | 28.3394 | 15.46458 | Lusaka | #N/A | Lusaka | Lusaka | No | No | No | Suburban |  |  | BTS | BTS | On Air | Grid Only | Tube star | 24 | Outdoor | Kelly Musama | Inhouse | Inhouse | MTN | Evans Ngonga | In House | In House | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Power cube |  |  | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 70 |  |  | MTN | #N/A | #N/A |  |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_168M
120 | ZM0001 | IHS_LSK_201A | AIRPORT ROOFTOP | 28.4455 | -14.5157 | Lusaka | N/A | Lusaka | Chongwe | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Roof Top | RT | Indoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Emerson | R48 3200 | 400 | C&D True | 352 | 12 | 176 | 8 | LG | LG | 18000 | 18000 | 2 | 36 |  | 2 | AirtelLiquid Telecom | 0 | ZM0001 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_201A
122 | ZM0002 | IHS_LSK_202A | ASSEMBLY | 28.3184 | -15.449 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | Hub | Hub | On air | Grid-Gen | Green Field | 30 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Vitalgen | Vitalgen | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 70 |  | 1 | Airtel | 0 | ZM0002 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_202A
123 | ZM0003 | IHS_LSK_203A | AVONDALE | 28.396 | -14.2666 | Lusaka | 5.5 | Lusaka | Lusaka | Yes | Yes | Yes | Urban | Platinum | Platinum | BB | BB | On air | Grid-Gen | Green Field | 42 | Indoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | CK Works | CK Works | 45 | perkins | 404A-22 | Leroy Sommer | TAL A42F J 6S/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 600 | 48 | 100 | 6 | LG | LG | 18000 | 18000 | 2 | 37.1 |  | 4 | MTNAirtelINQLiquid Telecom | T0221 | ZM0003 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_203A
124 | ZM0005 | IHS_LSK_204A | CATHEDRAL HILL | 28.3069 | -15.4175 | Lusaka | 4.5 | Lusaka | Lusaka | No | No | Yes | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Roof Top | RT | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Emerson | R48 3200 | 400 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 140 |  | 1 | Airtel | 0 | ZM0005 | 0 |  |  | Mesh | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | yes | 30 |  | Pending |  |  |  |  | IHS_LSK_204A
125 | ZM0007 | IHS_LSK_205A | CHAWAMA | 28.2881 | -15.4579 | Lusaka | 4.5 | Lusaka | Lusaka | No | Yes | No | Urban | Platinum | Platinum | BB | BB | On air | Grid-Gen | Green Field | 42 | Indoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Earth Technology | Earth technology | 30 | perkins | 403D-15T | Leroy Sommer | ECO-28-M/4 | 375 | Power cube | ECC500 | 600 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 95 |  | 3 | MTNAirtelLiquid Telecom | T0319 | ZM0007 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_205A
132 | ZM0008 | IHS_LSK_206A | CHILANGA | 28.276 | -15.5585 | Lusaka | 4.5 | Lusaka | Kafue | Yes | No | No | Suburban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 404A-22 | Mecc Alte | ECO-28-M/4 | 1000 | Power cube | ECC500 | 600 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 18000 | 18000 | 2 | 83 |  | 4 | MTNAirtelINQLiquid Telecom | T0157 | ZM0008 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_206A
133 | ZM0009 | IHS_LSK_207A | CHILENJE | 28.3401 | -15.4417 | Lusaka | 4.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 42 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Earth Technology | Earth technology | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 400 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | FM25000 | FM25000 | 25000 | 25000 | 2 | 112 |  | 2 | AirtelLiquid Telecom | 0 | ZM0009 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_207A
136 | ZM0010 | IHS_LSK_208A | CHILENJE SOUTH | 28.3297 | -15.4494 | Lusaka | 2.5 | Lusaka | Lusaka | Yes | No | Yes | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 44 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 403D-15T | Leroy Sommer | ECO-28-M/4 | 600 | Power cube | ECC500 | 400 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 133 |  | 2 | AirtelLiquid Telecom | 0 | ZM0010 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_208A
137 | ZM0017 | IHS_LSK_209A | DOWN SOWETO | 28.2755 | -15.4237 | Lusaka | 2.5 | Lusaka | Lusaka | No | Yes | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | MPI | MPI | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 600 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 220 |  | 2 | MTNAirtel | T0235 | ZM0017 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_209A
171 | ZM0019 | IHS_LSK_210A | EMMERSDALE | 28.2753 | -15.3876 | Lusaka | 5.5 | Lusaka | Lusaka | No | Yes | Yes | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 45 | perkins | 1103A-33 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 1600 | 48 | 100 | 16 | LG | LG | 18000 | 18000 | 2 | 210 |  | 2 | MTNAirtel | T0164 | ZM0019 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_210A
177 | ZM0020 | IHS_LSK_211A | FAIRVIEW | 28.2931 | -15.4108 | Lusaka | 4.5 | Lusaka | Lusaka | Yes | No | Yes | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 42 | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 404A-22 | Leroy Sommer | TAL 040 DJ 6S/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | CHIGO | CHIGO | 18000 | 18000 | 2 | 104 |  | 2 | AirtelLiquid Telecom | 0 | ZM0020 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_211A
179 | ZM0022 | IHS_LSK_212A | IBEX HILL | 28.3657 | -15.4183 | Lusaka | 5.5 | Lusaka | Lusaka | Yes | No | Yes | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 44 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | CK Works | CK Works | 45 | perkins | 404A-22 | Leroy Sommer | TAL A42F J 6S/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 206.1 |  | 4 | MTNAirtelINQLiquid Telecom | T0217 | ZM0022 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_212A
180 | ZM0024 | IHS_LSK_214A | KABULONGA | 28.3533 | -15.4304 | Lusaka | 4.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 50 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 404A-22 | Leroy Sommer | TAL 042C J 6/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 190 |  | 4 | MTNAirtelINQLiquid Telecom | T0476 | ZM0024 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_214A
181 | ZM0025 | IHS_LSK_215A | KABWATA | 28.3057 | -15.4328 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 42 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 100 |  | 1 | Airtel | 0 | ZM0025 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_215A
182 | ZM0027 | IHS_LSK_216A | KAFUE | 28.205 | -15.7543 | Lusaka | 4.5 | Lusaka | Kafue | Yes | No | No | Suburban | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 60 | Indoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 403D-15T | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG/CHIGO | LG/CHIGO | 18000 | 18000 | 4 | 156 |  | 1 | Airtel | 0 | ZM0027 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_216A
184 | ZM0038 | IHS_LSK_217A | KASUPE | 28.1917 | -15.345 | Lusaka | 1.8 | Lusaka | Kafue | No | No | No | Urban | Silver | Silver | HUB | HUB | On air | Grid-Gen | Green Field | 54 | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 88 |  | 1 | Airtel | 0 | ZM0038 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_217A
197 | ZM0043 | IHS_LSK_218A | LEOPARDS HILL | 28.4192 | -15.4807 | Lusaka | 2.5 | Lusaka | Kafue | Yes | No | No | Suburban | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 56 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 140.1 |  | 5 | MTNAirtelINQLiquid TelecomParatus Telecom | T0037 | ZM0043 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_218A
223 | ZM0044 | IHS_LSK_219A | LIBALA | 28.3187 | -15.4408 | Lusaka | 2.5 | Lusaka | Lusaka | Yes | No | Yes | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 30 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | IMG | IMG | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 600 | Power cube | ECC500 | 400 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 110 |  | 2 | AirtelLiquid Telecom | 0 | ZM0044 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_219A
229 | ZM0045 | IHS_LSK_220A | LILANDA | 28.2431 | -15.3731 | Lusaka | 2 | Lusaka | Kafue | No | No | Yes | Urban | Platinum | Platinum | BB | BB | On air | Grid-Gen | Green Field | 54 | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 16 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 110 |  | 1 | Airtel | 0 | ZM0045 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_220A
243 | ZM0049 | IHS_LSK_221A | NATSAVE | 28.2816 | -15.4116 | Lusaka | 2.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Roof Top | RT | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | CK Works | CK Works | 20 | perkins | 403A-15 | Leroy Sommer | ECO-28-M/4 | 1000 | IPT | DPS 2400B-48 | 250 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | LG18000 | N/A | 163 |  | 2 | AirtelLiquid Telecom | 0 | ZM0049 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | Yes |  |  | yes | 30 |  | Pending |  |  |  |  | IHS_LSK_221A
246 | ZM0051 | IHS_LSK_222A | LUBURMA | 28.2967 | -15.4316 | Lusaka | 2.5 | Lusaka | Lusaka | Yes | No | Yes | Urban | Platinum | Platinum |  | Hub | On air | Grid-Gen | Green Field | 30 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | IMG | IMG | 20 | perkins | 563585Y | Leroy Sommer | ECO-28-M/4 | 600 | Power cube | ECC500 | 400 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 60 |  | 1 | Airtel | 0 | ZM0051 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_222A
252 | ZM0052 | IHS_LSK_223A | LUSAKA AIRPORT | 28.4333 | -15.3167 | Lusaka | N/A | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid Only | Roof Top | RT | Indoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | In House | In House | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Emerson | R48 3200 | 400 | C&D True | 352 | 12 | 176 | 8 | CHIGO | CHIGO | 18000 | 18000 | 2 | 97 |  | 1 | Airtel | 0 | ZM0052 | 0 |  |  | n/a | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_223A
253 | ZM0053 | IHS_LSK_224A | LUSAKA WEST | 28.262 | -15.3983 | Lusaka | 4.5 | Lusaka | Lusaka | No | No | Yes | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Roof Top | RT | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 1103A-33 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 400 | 48 | 100 | 4 | CHIGO | CHIGO | 18000 | 18000 | 2 | 110 |  | 1 | Airtel | 0 | ZM0053 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | Done |  | No | No | Yes |  |  | yes | 30 |  | Pending |  |  |  |  | IHS_LSK_224A
255 | ZM0055 | IHS_LSK_225A | MAKENI | 28.293 | -15.49 | Lusaka | 4.5 | Lusaka | Lusaka | Yes | No | No | Urban | Silver | Silver | BTS | BB/HUB | On air | Grid-Gen | Green Field | 54 | Indoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Ghaddar | Ghaddar | 30 | perkins | CS7.5-20 | Mecc Alte | ECO28-VL/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG/GREE | LG/GREE | 18000 | 18000 | 2 | 93 |  | 2 | AirtelLiquid Telecom | 0 | ZM0055 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_225A
274 | ZM0065 | IHS_LSK_226A | MUNALI | 28.3452 | -15.3861 | Lusaka | 4.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BB | BB | On air | Grid-Gen | Green Field | 42 | Indoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 1103A-33 | Leroy Sommer | TAL 042C J 6/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 66.8 |  | 1 | Airtel | 0 | ZM0065 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_226A
275 | ZM0068 | IHS_LSK_227A | NEW KABULONGA | 28.3419 | -15.4165 | Lusaka | 4.5 | Lusaka | Lusaka | Yes | No | Yes | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 404D-22 | Leroy Sommer | TAL 042C J 6/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 108 |  | 2 | AirtelLiquid Telecom | 0 | ZM0068 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_227A
298 | ZM0069 | IHS_LSK_228A | NEW MAKENI | 28.2285 | -15.4574 | Lusaka | 4.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 56 | Indoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 85 |  | 1 | Airtel | 0 | ZM0069 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_228A
299 | ZM0071 | IHS_LSK_229A | NORTHMEAD | 28.2932 | -15.3951 | Lusaka | 5.5 | Lusaka | Lusaka | No | Yes | No | Urban | Platinum | Platinum | BTS | BB/HUB | On air | Grid-Gen | Green Field | 40 | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | CK Works | CK Works | 45 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 1600 | 48 | 100 | 16 | LG | LG | 18000 | 18000 | 2 | 179 |  | 2 | MTNAirtel | T0310 | ZM0071 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_229A
304 | ZM0074 | IHS_LSK_230A | RHODESPARK | 28.3065 | -15.4049 | Lusaka | 4.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 44 | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | CHIGO | CHIGO | 18000 | 18000 | 2 | 120 |  | 2 | AirtelINQ | 0 | ZM0074 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_230A
307 | ZM0079 | IHS_LSK_231A | SOWETO | 28.2748 | -15.4178 | Lusaka | 4.5 | Lusaka | Lusaka | Yes | Yes | Yes | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 32 | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 1103A-33 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 108 |  | 2 | MTNAirtel | T0198 | ZM0079 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_231A
308 | ZM0080 | IHS_LSK_232A | STANDARD CHARTERED | 28.2823 | -15.4212 | Lusaka | N/A | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Roof Top | RT | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Power cube | ECC500 | 400 | C&D True | 704 | 12 | 176 | 16 | N/A | N/A | N/A | N/A | N/A | 64 |  | 1 | Airtel | 0 | ZM0080 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_232A
310 | ZM0099 | IHS_LSK_233A | CHONGWE | 28.6785 | -15.3246 | Lusaka | 1.8 | Lusaka | Kafue | Yes | No | No | Rural | Silver | Silver | HUB | HUB | On air | Grid-Gen | Green Field | 54 | Indoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 98 |  | 1 | Airtel | 0 | ZM0099 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_233A
311 | ZM0107 | IHS_LSK_234A | ARCADES | 28.3184 | -15.2897 | Lusaka | 5.5 | Lusaka | Lusaka | Yes | No | Yes | Urban | Platinum | Platinum | BB | BB | On air | Grid-Gen | Green Field | 34 | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 45 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG/CHIGO | LG/CHIGO | 18000 | 18000 | 4 | 224 |  | 2 | AirtelLiquid Telecom | 0 | ZM0107 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_234A
312 | ZM0110 | IHS_LSK_235A | SOWETO NORTH | 28.2742 | -15.4134 | Lusaka | 2.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 34 | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 159.2 |  | 1 | Airtel | 0 | ZM0110 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_235A
313 | ZM0111 | IHS_LSK_236A | CHACHACHA | 28.2804 | -15.4185 | Lusaka | N/A | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum |  | BTS | On air | Grid Only | Roof Top | RT | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | In House | CCS | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Power cube | ECC500 | 400 | Power safe | 1200 | 2 | 1200 | 24 | LG | LG | 18000 | 18000 | 2 | 52.5 |  | 1 | Airtel | 0 | ZM0111 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_236A
318 | ZM0112 | IHS_LSK_237A | PREMIUM HOUSE | 28.289 | -15.4226 | Lusaka | N/A | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid Only | Roof Top | RT | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | In House | In House | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Emerson | R48 3200 | 200 | Lithium | 1600 | 48 | 100 | 16 | LG | LG | 18000 | 18000 | 2 | 70 |  | 1 | Airtel | 0 | ZM0112 | 0 |  |  | n/a | Inala | 2022-08-05 | yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_237A
330 | ZM0115 | IHS_LSK_238A | CHAWAMA WEST | 28.2767 | -15.4628 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | Yes | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 30 | Indoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 600 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | FM25000 | FM25000 | 25000 | 25000 | 2 | 65 |  | 1 | Airtel | 0 | ZM0115 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_238A
333 | ZM0117 | IHS_LSK_239A | CHILENJE EAST | 28.3533 | -15.4465 | Lusaka | 4.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 36 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Earth Technology | Earth technology | 30 | perkins | 403D-15T | Mecc Alte | ECP-28-M/4 | 375 | Power cube | ECC500 | 400 | Lead acid | 1600 | 48 | 100 | 16 | LG | LG | 18000 | 18000 | 2 | 109 |  | 2 | AirtelLiquid Telecom | 0 | ZM0117 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_239A
334 | ZM0119 | IHS_LSK_241A | UTH | 28.3118 | -15.4363 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 30 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | Yanmar | 4TNE88-G1A | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | GREE | GREE | 18000 | 18000 | 2 | 110 |  | 1 | Airtel | 0 | ZM0119 | 0 |  |  | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_241A
336 | ZM0123 | IHS_LSK_242A | BandaRO EAST | 28.2608 | -16.2711 | Lusaka | 1.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 30 | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 11 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 160 |  | 1 | Airtel | 0 | ZM0123 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_242A
338 | ZM0131 | IHS_LSK_243A | CHAMBA VALLEY | 28.3604 | -15.3727 | Lusaka | 2.5 | Lusaka | Lusaka | No | Yes | Yes | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 30 | Indoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1600 | 2 | 800 | 48 | GREE | GREE | 18000 | 18000 | 2 | 144.1 |  | 2 | MTNAirtel | T0444 | ZM0131 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_243A
339 | ZM0139 | IHS_LSK_244A | SOWETO WEST | 28.2693 | -15.4209 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 30 | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 403A-15 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | GREE | GREE | 18000 | 18000 | 2 | 64 |  | 1 | Airtel | 0 | ZM0139 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_244A
340 | ZM0140 | IHS_LSK_245A | KABWATA WEST | 28.3017 | -15.4355 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BB | BB | On air | Grid-Gen | Green Field | 30 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 403D-15T | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 90 |  | 1 | Airtel | 0 | ZM0140 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_245A
341 | ZM0162 | IHS_LSK_247A | KALINGALINGA | 28.342 | -15.4041 | Lusaka | 4.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 30 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 404A-22 | Leroy Sommer | TAL 042C J 6/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 137 |  | 2 | AirtelLiquid Telecom | 0 | ZM0162 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_247A
346 | ZM0188 | IHS_LSK_248A | LUANGWA FIERA | 30.3894 | -15.6119 | Lusaka | 2.5 | Lusaka | Luangwa | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Perkins | MPI | 20 | perkins | 404A-22 | Leroy Sommer | ECP-28-M/4 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 25.5 |  | 2 | AirtelTop Star | 0 | ZM0188 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_248A
348 | ZM0203 | IHS_LSK_249A | RUFUNSA | 29.6456 | -15.0771 | Lusaka | 1.5 | Lusaka | Chongwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen-solar | Green Field | 60 | Indoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | New way | New way | 13 | perkins | 404A-22 | Leroy Sommer | TAL 040 DJ 6S/4 | 600 | Emerson | MPPT/Emerson | 250 | BSB | 1500 | 2 | 1500 | 24 | LG | LG | 12000 | 12000 | 2 | 78 |  | 2 | MTNAirtel | T0516 | ZM0203 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_249A
349 | ZM0217 | IHS_LSK_250A | CHIAWA | 29.0379 | -15.9021 | Lusaka | 2 | Lusaka | Kafue | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 58 | Outdoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88-G1A | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 68 |  | 2 | MTNAirtel | T0228 | ZM0217 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_250A
350 | ZM0445 | IHS_LSK_251A | TALABUKU | 29.8078 | -15.0696 | Lusaka | 2.5 | Lusaka | Chongwe | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 50 | Indoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Ghaddar | Ghaddar | 20 | perkins | S4L261SDBC | Leroy Sommer | AL 3/4 | 600 | MPPT | MPPT | 93.75 | BSB | 1500 | 2 | 1500 | 24 | LG | LG | 18000 | 18000 | 2 | 58 |  | 1 | Airtel | 0 | ZM0445 | 0 |  |  | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_251A
364 | ZM0449 | IHS_LSK_252A | NYAUTAYI | 29.3502 | -15.1394 | Lusaka | 4.5 | Lusaka | Chongwe | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 80 | Indoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 45 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | BSB | 1500 | 2 | 1500 | 24 | LG | LG | 18000 | 18000 | 2 | 41 |  | 1 | Airtel | 0 | ZM0449 | 0 |  |  | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 2 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_252A
368 | ZM0450 | IHS_LSK_253A | CHITEMALESA | 28.8944 | -15.2641 | Lusaka | 5.5 | Lusaka | Chongwe | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 70 | Indoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | CK Works | CK Works | 45 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 2400 | 2 | 800 | 72 | GREE | GREE | 18000 | 18000 | 2 | 58.8 |  | 1 | Airtel | 0 | ZM0450 | 0 |  |  | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_253A
371 | ZM0586 | IHS_LSK_254A | NYAKUSEKA HILL | 30.0515 | -15.0116 | Lusaka | N/A | Lusaka | Chongwe | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 70 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | SHELL19"CORDEX3.6KW | SHELL19"CORDEX3.6KW | 200 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 67.3 |  | 1 | Airtel | 0 | ZM0586 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  | Consolidated on IHS_LSK_139M Nyakuseka BB | IHS_LSK_254A
375 | ZM0643 | IHS_LSK_255A | MAKENI KONGA | 28.1651 | -15.4928 | Lusaka | 2.5 | Lusaka | Kafue | No | No | No | Urban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 30 | Outdoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 89 |  | 1 | Airtel | 0 | ZM0643 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_255A
376 | ZM0645 | IHS_LSK_256A | SHORT HORN | 28.1164 | -15.4397 | Lusaka | 2.5 | Lusaka | Kafue | No | No | No | Suburban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | GREE | GREE | 18000 | 18000 | 2 | 74 |  | 2 | MTNAirtel | T0023 | ZM0645 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_256A
381 | ZM0646 | IHS_LSK_257A | PALABANA | 28.5443 | -15.4474 | Lusaka | 2.5 | Lusaka | Chongwe | No | No | No | Suburban | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 50 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Mecc Alte | ECO-28-M/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 50 |  | 1 | Airtel | 0 | ZM0646 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_257A
382 | ZM0647 | IHS_LSK_258A | WATER FALLS | 28.4499 | -15.3866 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Silver | Silver | HUB | HUB | On air | Grid-Gen | Green Field | 50 | Indoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 108 |  | 2 | MTNAirtel | T0278 | ZM0647 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_258A
384 | ZM0648 | IHS_LSK_259A | KANAKANTAPA | 28.6364 | -15.253 | Lusaka | 2.5 | Lusaka | Kafue | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Earth Technology | Earth technology | 15 | perkins | 403A-15 | Leroy Sommer | TAL 040F J 6S/4 | 375 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 54.3 |  | 2 | MTNAirtel | T0251 | ZM0648 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_259A
389 | ZM0649 | IHS_LSK_260A | NAKACHENJE | 28.0634 | -15.4157 | Lusaka | 2.5 | Lusaka | Kafue | No | No | No | Suburban | Silver | Silver |  | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | GREE | GREE | 18000 | 18000 | 2 | 72 |  | 2 | MTNAirtel | T0289 | ZM0649 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_260A
390 | ZM0666 | IHS_LSK_261A | LUANGWA BRIDGE | 30.2117 | -15.0025 | Lusaka | N/A | Lusaka | Chongwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen-solar | Green Field | 70 | Indoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | MPPT | MPPT | 93.75 | BSB | 1500 | 2 | 1500 | 24 | LG | LG | 18000 | 18000 | 2 | 43 |  | 1 | Airtel | 0 | ZM0666 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_261A
399 | ZM0675 | IHS_LSK_262A | CHIAWA ROAD | 28.9361 | -15.9337 | Lusaka | 2.5 | Lusaka | Kafue | No | No | No | Rural | Silver | Silver | HUB | HUB | On air | Grid-Gen | Green Field | 70 | Indoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 403D-15T | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 62 |  | 2 | MTNAirtel | T0227 | ZM0675 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_262A
413 | ZM0698 | IHS_LSK_263A | BUSEKO | 28.2603 | -15.389 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 30 | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Earth Technology | Earth technology | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 375 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | FM25000 | FM25000 | 25000 | 25000 | 2 | 93 |  | 1 | Airtel | 0 | ZM0698 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_263A
428 | ZM0701 | IHS_LSK_264A | ZINGALUME | 28.2307 | -15.38 | Lusaka | 2.5 | Lusaka | Kafue | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 52 | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 94 |  | 1 | Airtel | 0 | ZM0701 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_264A
431 | ZM0702 | IHS_LSK_265A | DOWN TOWN | 28.2844 | -15.4319 | Lusaka | 4.5 | Lusaka | Lusaka | No | No | Yes | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 36 | Outdoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 1103C-33 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Lead acid | 1600 | 48 | 100 | 16 | N/A | N/A | N/A | LG18000 | N/A | 170 |  | 1 | Airtel | 0 | ZM0702 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_265A
432 | ZM0703 | IHS_LSK_266A | MATERO BOYS | 28.2746 | -15.3795 | Lusaka | 2.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | IMG | IMG | 20 | perkins | 1103A-33 | Leroy Sommer | ECO-28-M/4 | 600 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 108 |  | 1 | Airtel | 0 | ZM0703 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_266A
446 | ZM0704 | IHS_LSK_267A | KUOMBOKA | 28.2765 | -15.452 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BB | BB | On air | Grid-Gen | Green Field | 30 | Indoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | Lister petter | LWP4 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 53 |  | 1 | Airtel | 0 | ZM0704 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_267A
450 | ZM0705 | IHS_LSK_268A | KABWATA SERVICE | 28.2991 | -15.4385 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | Yes | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | Yanmar | 4TNE88-G1A | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 102 |  | 1 | Airtel | 0 | ZM0705 | 0 |  |  | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_268A
452 | ZM0706 | IHS_LSK_269A | ARAKAN | 28.3304 | -15.4237 | Lusaka | 2 | Lusaka | Lusaka | Yes | Yes | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 16 | Lister petter | LWP4 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 118 |  | 3 | MTNAirtelLiquid Telecom | T0297 | ZM0706 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_269A
453 | ZM0707 | IHS_LSK_270A | CHELSTON | 28.3825 | -15.3629 | Lusaka | 2.5 | Lusaka | Lusaka | Yes | No | Yes | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Mecc Alte | ECO-28-M/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 75.2 |  | 2 | AirtelLiquid Telecom | 0 | ZM0707 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_270A
454 | ZM0708 | IHS_LSK_271A | KAUNDA SQUARE | 28.3535 | -15.3792 | Lusaka | 4.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | HIMOINSA | HIMOINSA | 30 | Yanmar | SK160LB | HIMOINSA | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 52.7 |  | 1 | Airtel | 0 | ZM0708 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_271A
456 | ZM0714 | IHS_LSK_272A | KANYAMA | 28.261 | -15.4322 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 30 | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 80 |  | 1 | Airtel | 0 | ZM0714 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_272A
458 | ZM0715 | IHS_LSK_273A | CHALIMBANA | 28.7002 | -15.3809 | Lusaka | 2.5 | Lusaka | Chongwe | No | No | No | Suburban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 58 | Indoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | GREE | GREE | 18000 | 18000 | 2 | 65 |  | 2 | MTNAirtel | T0223 | ZM0715 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_273A
461 | ZM0716 | IHS_LSK_274A | IMPALA | 28.2809 | -15.4058 | Lusaka | 2.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 403A-15 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 120 |  | 1 | Airtel | 0 | ZM0716 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_274A
462 | ZM0717 | IHS_LSK_275A | MTENDERE | 28.3627 | -15.3979 | Lusaka | 4.5 | Lusaka | Lusaka | Yes | No | Yes | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 36 | Indoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 404A-22 | Leroy Sommer | TAL 042C J 6/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 126 |  | 2 | AirtelLiquid Telecom | 0 | ZM0717 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_275A
464 | ZM0718 | IHS_LSK_276A | SIKANZE | 28.3043 | -15.4281 | Lusaka | 2.5 | Lusaka | Lusaka | Yes | Yes | No | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 36 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | HIMOINSA | HIMOINSA | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 170 |  | 2 | MTNAirtel | T0239 | ZM0718 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_276A
465 | ZM0719 | IHS_LSK_277A | GARDEN | 28.2941 | -15.3837 | Lusaka | 4.5 | Lusaka | Lusaka | No | Yes | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG/CHIGO | LG/CHIGO | 18000 | 18000 | 4 | 175 |  | 2 | MTNAirtel | T0162 | ZM0719 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | yes | 30 |  | Pending |  |  |  |  | IHS_LSK_277A
480 | ZM0720 | IHS_LSK_278A | OLD KANYAMA | 28.2486 | -15.4389 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 28 | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 403A-15 | Mecc Alte | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 108 |  | 1 | Airtel | 0 | ZM0720 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_278A
483 | ZM0721 | IHS_LSK_279A | CHILENJE SHOPRITE | 28.339 | -15.452 | Lusaka | 4.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 32 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 403D-15T | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 185 |  | 3 | MTNAirtelLiquid Telecom | T0888 | ZM0721 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_279A
491 | ZM0726 | IHS_LSK_280A | CHRISTIAN VOICE | 28.0012 | -15.525 | Lusaka | 2.5 | Lusaka | Kafue | No | No | No | Suburban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 72 |  | 3 | MTNAirtelParatus Telecom | T0234 | ZM0726 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_280A
492 | ZM0727 | IHS_LSK_281A | KAFUE TOWN | 28.1753 | -15.7606 | Lusaka | 4.5 | Lusaka | Kafue | Yes | No | No | Suburban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 42 | Indoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | CHIGO | CHIGO | 18000 | 18000 | 2 | 121 |  | 4 | MTNAirtelLiquid TelecomParatus Telecom | T0357 | ZM0727 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_281A
493 | ZM0774 | IHS_LSK_282A | KASISI | 28.4734 | -15.2672 | Lusaka | 2.5 | Lusaka | Kafue | No | No | No | Suburban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | CHIGO | CHIGO | 18000 | 18000 | 2 | 40.3 |  | 1 | Airtel | 0 | ZM0774 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_282A
494 | ZM0783 | IHS_LSK_283A | MANDA HILL | 28.3071 | -15.3927 | Lusaka | 2 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BB | BB | On air | Grid-Gen | Green Field | 36 | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Lister Petter | Lister Petter | 16 | Lister petter | LWP4 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | CHIGO | CHIGO | 18000 | 18000 | 2 | 110 |  | 3 | AirtelINQLiquid Telecom | 0 | ZM0783 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_283A
506 | ZM0784 | IHS_LSK_284A | RADIAN | 28.2791 | -15.4153 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum |  | Hub | On air | Grid-Gen | Roof Top | RT | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 123 |  | 1 | Airtel | 0 | ZM0784 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_284A
513 | ZM0786 | IHS_LSK_285A | JOHN LAING | 28.259 | -15.4456 | Lusaka | 4.5 | Lusaka | Lusaka | No | Yes | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | Yanmar | 4TNE88-G1A | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 112 |  | 2 | MTNAirtel | T0348 | ZM0786 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_285A
514 | ZM0787 | IHS_LSK_286A | KAMWALA SOUTH | 28.2925 | -15.4654 | Lusaka | 4.5 | Lusaka | Lusaka | No | Yes | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | CK Works | CK Works | 30 | perkins | ENLP30S-3 | Leroy Sommer | TAL 040 DJ 6S/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | SAMSUNG | SAMSUNG | 18000 | 18000 | 2 | 155 |  | 2 | MTNAirtel | T0345 | ZM0787 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_286A
515 | ZM0788 | IHS_LSK_287A | MTENDERE MARKET | 28.352 | -15.4006 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | IMG | IMG | 20 | perkins | 403A-15 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1600 | 2 | 800 | 48 | SAMSUNG | SAMSUNG | 18000 | 18000 | 2 | 45.3 |  | 1 | Airtel | 0 | ZM0788 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_287A
516 | ZM0789 | IHS_LSK_288A | JOHN LAING BP | 28.2727 | -15.4371 | Lusaka | 2 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 16 | perkins | 403D-15T | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 55 |  | 1 | Airtel | 0 | ZM0789 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_288A
521 | ZM0791 | IHS_LSK_290A | SAINT ANNE | 28.249 | -15.4211 | Lusaka | 4.5 | Lusaka | Lusaka | Yes | Yes | Yes | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | FM25000 | FM25000 | 25000 | 25000 | 2 | 167 |  | 3 | MTNAirtelLiquid Telecom | T0287 | ZM0791 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_290A
524 | ZM0808 | IHS_LSK_291A | SOWETO MARKET | 28.2774 | -15.4214 | Lusaka | 4.5 | Lusaka | Lusaka | No | Yes | No | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 36 | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 1600 | 48 | 100 | 16 | N/A | N/A | N/A | LG18000 | N/A | 132 |  | 2 | MTNAirtel | T0213 | ZM0808 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_291A
525 | ZM0832 | IHS_LSK_292A | LUANGWA HIGH SCHOOL | 30.2879 | -15.2737 | Lusaka | 2.5 | Lusaka | Luangwa | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen-solar | Green Field | 80 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Emerson | MPP\Emerson | 250 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 35 |  | 1 | Airtel | 0 | ZM0832 | 0 |  |  | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 2 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_292A
526 | ZM0846 | IHS_LSK_293A | STATE LODGE | 28.4279 | -15.4376 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Silver | Silver | HUB | HUB | On air | Grid-Gen | Green Field | 50 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | IMG | IMG | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 100 |  | 2 | MTNAirtel | T0322 | ZM0846 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_293A
527 | ZM0847 | IHS_LSK_294A | APOLLO | 28.1296 | -14.1331 | Lusaka | 2.5 | Lusaka | Kafue | No | No | No | Suburban | Silver | Silver | BB | BB | On air | Gen Only | Green Field | 50 | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Zanardi | AL 3/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | CHIGO | CHIGO | 18000 | 18000 | 2 | 110 |  | 2 | MTNAirtel | T0330 | ZM0847 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_294A
543 | ZM0848 | IHS_LSK_295A | FAIRVIEW MAKISHI | 28.2897 | -15.4129 | Lusaka | 2 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 16 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 108 |  | 1 | Airtel | 0 | ZM0848 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_295A
548 | ZM0849 | IHS_LSK_296A | MWAIWAKE | 28.3298 | -15.4608 | Lusaka | 4.5 | Lusaka | Lusaka | Yes | Yes | No | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 36 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 230 |  | 3 | MTNAirtelLiquid Telecom | T0260 | ZM0849 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_296A
552 | ZM0850 | IHS_LSK_297A | KAUNDA SQUARE ZNS | 28.3526 | -15.369 | Lusaka | 4.5 | Lusaka | Lusaka | Yes | Yes | Yes | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 36 | Indoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 1103A-33 | Leroy Sommer | TAL 042C J 6/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 4 | 126 |  | 3 | MTNAirtelLiquid Telecom | T0179 | ZM0850 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_297A
580 | ZM0851 | IHS_LSK_298A | CHAISA | 28.2859 | -15.3863 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BB | BB | On air | Grid-Gen | Green Field | 36 | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | GREE | GREE | 18000 | 18000 | 2 | 93 |  | 1 | Airtel | 0 | ZM0851 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_298A
584 | ZM0852 | IHS_LSK_299A | CHALALA | 28.3536 | -15.4589 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | Yes | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 36 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 403A-15 | Leroy Sommer | ECO-28-M/4 | 750 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 140 |  | 1 | Airtel | 0 | ZM0852 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_299A
608 | ZM0853 | IHS_LSK_300A | CHELSTON GREEN | 28.3961 | -15.367 | Lusaka | 4.5 | Lusaka | Lusaka | Yes | No | Yes | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 36 | Indoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 404A-22 | Leroy Sommer | TAL 042C J 6/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 90 |  | 2 | AirtelLiquid Telecom | 0 | ZM0853 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_300A
611 | ZM0854 | IHS_LSK_301A | MANDEVU | 28.2813 | -15.3711 | Lusaka | 2.5 | Lusaka | Lusaka | No | Yes | Yes | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 178 |  | 2 | MTNAirtel | T0312 | ZM0854 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_301A
612 | ZM0855 | IHS_LSK_302A | KK MONUMENT | 28.3324 | -15.4449 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Green Power | Green Power | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 600 | Power cube | ECC500 | 400 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | LG18000 | N/A | 125 |  | 1 | Airtel | 0 | ZM0855 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_302A
613 | ZM0865 | IHS_LSK_303A | MOUNT MAKULU | 28.2354 | -15.5279 | Lusaka | 2.5 | Lusaka | Kafue | No | No | No | Suburban | Silver | Silver | HUB | HUB | On air | Grid-Gen | Green Field | 50 | Indoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Lamasat | Lamasat | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 600 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 77 |  | 1 | Airtel | 0 | ZM0865 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_303A
615 | ZM0871 | IHS_LSK_304A | JAKANA | 28.1031 | -15.5643 | Lusaka | 2.5 | Lusaka | Kafue | No | No | No | Suburban | Silver | Silver | HUB | BB/HUB | On air | Grid-Gen | Green Field | 50 | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Earth Technology | Earth technology | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 375 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | CHIGO | CHIGO | 18000 | 18000 | 2 | 90 |  | 1 | Airtel | 0 | ZM0871 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_304A
635 | ZM0880 | IHS_LSK_305A | KHAL AMAZI | 28.5116 | -15.3551 | Lusaka | 2.5 | Lusaka | Chongwe | No | No | No | Rural | Silver | Silver | HUB | HUB | On air | Grid-Gen | Green Field | 48 | Indoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Green Power | Green Power | 20 | perkins | 403A-15 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 12000 | 12000 | 2 | 68 |  | 2 | MTNAirtel | T0253 | ZM0880 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_305A
639 | ZM0952 | IHS_LSK_306A | POST OFFICE | 28.2825 | -15.4166 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Roof Top | RT | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | C&D True | 1056 | 12 | 176 | 24 | CHIGO | CHIGO | 18000 | 18000 | 2 | 123 |  | 1 | Airtel | 0 | ZM0952 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_306A
640 | ZM0959 | IHS_LSK_307A | CHIBOLYA | 28.2724 | -15.4317 | Lusaka | 1.5 | Lusaka | Lusaka | No | No | Yes | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 36 | Indoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 13 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | GREE | GREE | 18000 | 18000 | 2 | 60 |  | 1 | Airtel | 0 | ZM0959 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_307A
642 | ZM0963 | IHS_LSK_308A | DELL MOTORS | 28.2688 | -15.448 | Lusaka | 4.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 30 | Indoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Lamasat | Lamasat | 30 | perkins | 403D-15T | Mecc Alte | ECP-28-M/4 | 600 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 75 |  | 1 | Airtel | 0 | ZM0963 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_308A
643 | ZM0965 | IHS_LSK_309A | NGOMBE | 28.3296 | -15.365 | Lusaka | 2.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 30 | Indoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | CK Works | CK Works | 20 | perkins | 403A-15 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 101 |  | 2 | AirtelLiquid Telecom | 0 | ZM0965 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_309A
644 | ZM0966 | IHS_LSK_310A | JOHN HOWARD | 28.2842 | -15.4696 | Lusaka | 2.5 | Lusaka | Lusaka | No | Yes | Yes | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 36 | Indoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 403D-15T | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | FM25000 | FM25000 | 25000 | 25000 | 2 | 79 |  | 2 | MTNAirtel | T0275 | ZM0966 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_310A
645 | ZM0974 | IHS_LSK_311A | ZECCO | 28.2366 | -15.3829 | Lusaka | 2.5 | Lusaka | Kafue | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 40 | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 90 |  | 1 | Airtel | 0 | ZM0974 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_311A
661 | ZM0975 | IHS_LSK_312A | NYUMBA YANGA | 28.3625 | -15.4499 | Lusaka | 4.5 | Lusaka | Lusaka | Yes | Yes | Yes | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 34 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | CK Works | CK Works | 30 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 375 | Power cube | ECC500 | 400 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 230 |  | 3 | MTNAirtelLiquid Telecom | T0298 | ZM0975 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_312A
673 | ZM0976 | IHS_LSK_313A | KANYAMA STATION | 28.2559 | -15.4348 | Lusaka | 2.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 30 | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | MPI | MPI | 20 | perkins | 403A-15 | Leroy Sommer | ECO-28-M/4 | 600 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | GREE | GREE | 18000 | 18000 | 2 | 87 |  | 1 | Airtel | 0 | ZM0976 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_313A
683 | ZM0977 | IHS_LSK_314A | KALIKILIKI | 28.3802 | -15.4024 | Lusaka | 2.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 34 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 300 | 48 | 100 | 3 | GREE | GREE | 18000 | 18000 | 2 | 125 |  | 1 | Airtel | 0 | ZM0977 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_314A
691 | ZM0979 | IHS_LSK_315A | MAKENI SABLE | 28.2482 | -15.4522 | Lusaka | 2.5 | Lusaka | Lusaka | No | Yes | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 102 |  | 2 | MTNAirtel | T0288 | ZM0979 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_315A
700 | ZM0981 | IHS_LSK_316A | GEORGE | 28.2375 | -15.3753 | Lusaka | 2.5 | Lusaka | Kafue | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 30 | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | IMG | IMG | 20 | perkins | 4TNE88-G1A | Leroy Sommer | ECO-28-M/4 | 600 | Power cube | ECC500 | 400 | Lithium | 1600 | 48 | 100 | 16 | LG | LG | 18000 | 18000 | 2 | 55 |  | 1 | Airtel | 0 | ZM0981 | 0 |  |  | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 2 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_316A
707 | ZM0982 | IHS_LSK_317A | DESAI BASIC | 28.247 | -15.3746 | Lusaka | 2.5 | Lusaka | Kafue | Yes | No | Yes | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 30 | Outdoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | IMG | IMG | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 600 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | LG18000 | N/A | 88 |  | 1 | Airtel | 0 | ZM0982 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_317A
721 | ZM0989 | IHS_LSK_318A | INTERLAND | 28.3246 | -15.4449 | Lusaka | 1.8 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | CK Works | CK Works | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 650 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 100 |  | 1 | Airtel | 0 | ZM0989 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_318A
731 | ZM0992 | IHS_LSK_319A | CHURDLEIGH | 28.3439 | -15.373 | Lusaka | 2.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | IMG | IMG | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 600 | Power cube | ECC500 | 400 | Lithium | 1600 | 48 | 100 | 16 | LG | LG | 18000 | 18000 | 2 | 81 |  | 2 | AirtelLiquid Telecom | 0 | ZM0992 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_319A
742 | ZM3000 | IHS_LSK_320A | CITY AIRPORT | 28.3319 | -15.4082 | Lusaka | 5.5 | Lusaka | Lusaka | Yes | No | Yes | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 36 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | CK Works | CK Works | 30 | perkins | 404A-22 | Leroy Sommer | TAL A42F J 6S/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 136 |  | 2 | AirtelLiquid Telecom | 0 | ZM3000 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_320A
743 | ZM3001 | IHS_LSK_321A | NORTHMEAD SCHOOL | 28.3005 | -15.3962 | Lusaka | 4.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 30 | Outdoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 1300 | 48 | 100 | 13 | N/A | N/A | N/A | LG18000 | N/A | 167 |  | 3 | MTNAirtelLiquid Telecom | T0520 | ZM3001 | 0 |  | yes | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | Done |  | No | No | Yes |  |  | yes | 30 |  | Pending |  |  |  |  | IHS_LSK_321A
765 | ZM3002 | IHS_LSK_322A | MTENDERE D | 28.362 | -15.4059 | Lusaka | 2 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 30 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | Lister petter | LWP4 | Leroy Sommer | TAL-A40-C J6/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 45.3 |  | 1 | Airtel | 0 | ZM3002 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_322A
780 | ZM3011 | IHS_LSK_323A | KULIMA TOWER | 28.2804 | -15.4229 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Roof Top | RT | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Emerson | R48-3200 | 400 | UPS | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 79 |  | 1 | Airtel | 0 | ZM3011 | 0 |  |  | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_323A
781 | ZM3024 | IHS_LSK_325A | KANYAMA WEST | 28.2341 | -15.4299 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 40 | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | MPI | MPI | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 75 |  | 1 | Airtel | 0 | ZM3024 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_325A
789 | ZM3028 | IHS_LSK_326A | CHIPATA COMPOUND | 28.3001 | -15.3565 | Lusaka | 2 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 16 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 87 |  | 1 | Airtel | 0 | ZM3028 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_326A
792 | ZM3211 | IHS_LSK_327A | LILAYI | 28.2751 | -15.5276 | Lusaka | 2.5 | Lusaka | Kafue | No | No | Yes | Suburban | Silver | Silver | HUB | HUB | On air | Grid-Gen | Green Field | 36 | Indoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 403D-15T | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 56 |  | 2 | MTNAirtel | T0503 | ZM3211 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_327A
793 | ZM3229 | IHS_LSK_328A | MATERO ODDYS | 28.2684 | -15.385 | Lusaka | 4.5 | Lusaka | Lusaka | Yes | No | Yes | Urban | Platinum | Platinum | BB | BB | On air | Grid-Gen | Green Field | 30 | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 179 |  | 2 | MTNAirtel | T0506 | ZM3229 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_328A
798 | ZM3230 | IHS_LSK_329A | JUSTIN KABWE | 28.288 | -15.374 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 30 | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Earth Technology | Earth technology | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 375 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 93 |  | 1 | Airtel | 0 | ZM3230 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_329A
800 | ZM3288 | IHS_LSK_331A | KAFUE ESTATE | 28.1614 | -15.7419 | Lusaka | 2.5 | Lusaka | Kafue | Yes | No | No | Suburban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 403D-15T | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 81 |  | 2 | AirtelLiquid Telecom | 0 | ZM3288 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_331A
807 | ZM3304 | IHS_LSK_332A | MIKANGO | 28.6313 | -15.5306 | Lusaka | 1.5 | Lusaka | Chongwe | No | No | No | Suburban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | CK Works | CK Works | 20 | perkins | 403A-15 | Leroy Sommer | LSA P404 | 600 | Emerson | R483200 | 250 | Power safe | 1200 | 2 | 1200 | 24 | LG | LG | 18000 | 18000 | 2 | 49 |  | 1 | Airtel | 0 | ZM3304 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_332A
809 | ZM3305 | IHS_LSK_333A | KAFUE SUGAR | 27.961 | -15.5841 | Lusaka | 2.5 | Lusaka | Kafue | No | No | No | Suburban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 403A-15 | Leroy Sommer | ECO-28-M/4 | 600 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 45 |  | 2 | MTNAirtel | T0165 | ZM3305 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_333A
810 | ZM3327 | IHS_LSK_334A | MISISI | 28.2794 | -15.4408 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | Yanmar | 4TNE88-G1A | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 52 |  | 1 | Airtel | 0 | ZM3327 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_334A
815 | ZM3328 | IHS_LSK_335A | CITY CLOTHING MICRO | 28.2783 | -15.4202 | Lusaka | N/A | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid Only | Roof Top | RT | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | In House | In House | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Emerson | R48 3200 | 400 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 76 |  | 1 | Airtel | 0 | ZM3328 | 0 |  |  | n/a | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_335A
819 | ZM3329 | IHS_LSK_336A | SUN SOFT MICRO | 28.2809 | -15.4167 | Lusaka | N/A | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid Only | Roof Top | RT | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | In House | In House | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | IPT | DPS 2400B-48 | 250 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 87 |  | 1 | Airtel | 0 | ZM3329 | 0 |  |  | n/a | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_336A
839 | ZM3330 | IHS_LSK_337A | JOHN LAING MARKET | 28.2674 | -15.4413 | Lusaka | 2.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 36 | Indoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 403D-15T | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 83 |  | 1 | Airtel | 0 | ZM3330 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_337A
845 | ZM3331 | IHS_LSK_338A | CHIBOLYA BASIC | 28.2789 | -15.4261 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | LG18000 | N/A | 167 |  | 1 | Airtel | 0 | ZM3331 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_338A
846 | ZM3333 | IHS_LSK_340A | NAMUNUNGA SCHOOL | 28.2726 | -15.4224 | Lusaka | 2.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | LG18000 | N/A | 68 |  | 2 | AirtelLiquid Telecom | 0 | ZM3333 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_340A
847 | ZM3334 | IHS_LSK_341A | DOWNTOWN MICRO | 28.2826 | -15.4295 | Lusaka | N/A | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Roof Top | RT | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Emerson | 0 | 400 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 68 |  | 1 | Airtel | 0 | ZM3334 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_341A
849 | ZM3335 | IHS_LSK_342A | KAMWALA BASIC | 28.2902 | -15.4356 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404D-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 122 |  | 2 | MTNAirtel | T0489 | ZM3335 | 0 |  |  | Palisade | Inala | 2022-08-05 | yes | Yes |  | 2 |  |  | Done | 2019-06-06 | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_342A
869 | ZM3347 | IHS_LSK_343A | SHOPRITE MICRO | 28.2826 | -15.4193 | Lusaka | N/A | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid Only | Roof Top | RT | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | In House | In House | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Power cube | ECC500 | 400 | Lithium | 1600 | 48 | 100 | 16 | N/A | N/A | N/A | N/A | N/A | 56 |  | 1 | Airtel | 0 | ZM3347 | 0 |  |  | n/a | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_343A
888 | ZM3369 | IHS_LSK_344A | CHAINDA CLINIC | 28.4047 | -15.3893 | Lusaka | 2 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 36 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | TAL-A40-C J6/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 60 |  | 2 | MTNAirtel | T0509 | ZM3369 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_344A
919 | ZM3370 | IHS_LSK_345A | CHILULU | 28.2887 | -15.3976 | Lusaka | 2.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | IMG | IMG | 20 | perkins | 404A-22 | Mecc Alte | ECO28-VL/4 | 600 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 89 |  | 2 | AirtelLiquid Telecom | 0 | ZM3370 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_345A
921 | ZM3371 | IHS_LSK_346A | KABANANA MARKET | 28.298 | -15.3652 | Lusaka | 2 | Lusaka | Lusaka | No | Yes | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 16 | perkins | 403A-15 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 110 |  | 2 | MTNAirtel | T0347 | ZM3371 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_346A
923 | ZM3372 | IHS_LSK_347A | KANYAMA CLINIC | 28.2608 | -15.4279 | Lusaka | 2.5 | Lusaka | Lusaka | Yes | Yes | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Earth Technology | Earth technology | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 600 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | LG18000 | N/A | 122 |  | 2 | MTNAirtel | T0344 | ZM3372 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_347A
926 | ZM3373 | IHS_LSK_348A | UNZA VET | 28.3311 | -15.4001 | Lusaka | 4.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 1103A-33 | Leroy Sommer | TAL 042C J 6/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lead acid | 1800 | 48 | 100 | 18 | LG | LG | 18000 | 18000 | 2 | 228 |  | 2 | MTNAirtel | T0405 | ZM3373 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_348A
932 | ZM3374 | IHS_LSK_349A | DAR FARMS | 28.2731 | -15.41 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 42 | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 94 |  | 2 | AirtelINQ | 0 | ZM3374 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_349A
951 | ZM3379 | IHS_LSK_350A | SNOW WHITE | 28.2814 | -15.4546 | Lusaka | 4.5 | Lusaka | Lusaka | No | Yes | No | Urban | Platinum | Platinum | BB | BB | On air | Grid-Gen | Green Field | 36 | Indoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 403D-15T | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 101 |  | 2 | MTNAirtel | T0280 | ZM3379 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | yes | 30 |  | Pending |  |  |  |  | IHS_LSK_350A
955 | ZM3387 | IHS_LSK_351A | RIDGEWAY EXCHANGE | 28.2996 | -15.4166 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 80 |  | 2 | AirtelINQ | 0 | ZM3387 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_351A
958 | ZM3388 | IHS_LSK_352A | KABULONGA GIRLS | 28.3469 | -15.4251 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | Yes | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Vitalgen | Vitalgen | 20 | perkins | 404A-22 | Leroy Sommer | ECP-28-M/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 100 |  | 1 | Airtel | 0 | ZM3388 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_352A
960 | ZM3389 | IHS_LSK_353A | KYINDU RANCH | 28.4452 | -15.4729 | Lusaka | 2.5 | Lusaka | Kafue | No | No | No | Suburban | Silver | Silver | HUB | HUB | On air | Grid-Gen | Green Field | 60 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Earth Technology | Earth technology | 20 | perkins | 403A-15 | Leroy Sommer | TAL 040F J 6S/4 | 375 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 50 |  | 1 | Airtel | 0 | ZM3389 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_353A
961 | ZM3390 | IHS_LSK_354A | ROMA EXCHANGE | 28.3056 | -15.3729 | Lusaka | 4.5 | Lusaka | Lusaka | Yes | Yes | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | LG18000 | N/A | 150 |  | 3 | MTNAirtelLiquid Telecom | T0308 | ZM3390 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_354A
962 | ZM3391 | IHS_LSK_355A | BONAVENTURE RELOCATION | 28.2524 | -15.476 | Lusaka | 2 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 64 | Indoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 16 | perkins | 403D-15T | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 79 |  | 3 | AirtelLiquid TelecomAir-link | 0 | ZM3391 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_355A
965 | ZM3399 | IHS_LSK_356A | LUSAKA WEST NEW | 28.1547 | -15.4284 | Lusaka | 2.5 | Lusaka | Kafue | No | No | No | Suburban | Silver | Silver |  | BTS | On air | Grid-Gen | Green Field | 30 | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 115 |  | 2 | MTNAirtel | T0493 | ZM3399 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_356A
967 | ZM3401 | IHS_LSK_357A | COOPERATIVE COLLEGE | 28.3724 | -15.4541 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | Yes | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 30 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 82 |  | 1 | Airtel | 0 | ZM3401 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_357A
969 | ZM3402 | IHS_LSK_358A | MTENDERE BUS STOP | 28.3564 | -15.4036 | Lusaka | 4.5 | Lusaka | Lusaka | Yes | Yes | No | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 30 | Indoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 1103A-33 | Mecc Alte | ECO-28-M/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 4 | 127.6 |  | 3 | MTNAirtelLiquid Telecom | T0184 | ZM3402 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_358A
970 | ZM3430 | IHS_LSK_360A | ngwerere cov. Improv. (ellensdale) | 28.3813 | -15.2866 | Lusaka | 2.5 | Lusaka | Kafue | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 52 | Indoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Lamasat | Lamasat | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 600 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 94 |  | 2 | MTNAirtel | T0435 | ZM3430 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_360A
993 | ZM3432 | IHS_LSK_361A | SUNNINGDALE | 28.332 | -15.4186 | Lusaka | 2 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum |  | BTS | On air | Grid-Gen | Green Field | 41 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 16 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | CHIGO | CHIGO | 18000 | 18000 | 2 | 65 |  | 2 | AirtelLiquid Telecom | 0 | ZM3432 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_361A
996 | ZM3462 | IHS_LSK_362A | SHIMABALA | 28.2481 | -15.6722 | Lusaka | 2.5 | Lusaka | Kafue | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 60 | Outdoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | Yanmar | 4TNE88-G1A | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 72 |  | 2 | MTNAirtel | T0118 | ZM3462 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_362A
1015 | ZM3517 | IHS_LSK_364A | ST. ANNE-3-RLF (St. Anne Mbasela) | 28.2414 | -15.425 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 100 |  | 1 | Airtel | 0 | ZM3517 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_364A
1038 | ZM3518 | IHS_LSK_365A | SNOW WHITE-1-RLF (Snow White SDA) | 28.2809 | -15.447 | Lusaka | 2 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Vitalgen | Vitalgen | 16 | Yanmar | 4TNE88-G1A | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 67 |  | 1 | Airtel | 0 | ZM3518 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_365A
1040 | ZM3519 | IHS_LSK_366A | OLD KANYAMA-3-RLF (Simoson Makeni) | 28.2389 | -15.4456 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | CK Works | CK Works | 20 | perkins | 403A-15 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 105 |  | 1 | Airtel | 0 | ZM3519 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_366A
1041 | ZM3526 | IHS_LSK_368A | CHILENJE SHOPRITE-3-RLF (Arthur Wina) | 28.3465 | -15.4555 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 36 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | MPI | MPI | 20 | perkins | 403D-15T | Leroy Sommer | ECO-28-M/4 | 600 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 97 |  | 1 | Airtel | 0 | ZM3526 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_368A
1043 | ZM3527 | IHS_LSK_369A | CHAISA-1-RLF (Chaisa Market) | 28.2861 | -15.3805 | Lusaka | 2.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 100 |  | 1 | Airtel | 0 | ZM3527 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_369A
1044 | ZM3529 | IHS_LSK_370A | CHAWAMA-3-RLF (Chawama Basic Sch.) | 28.2839 | -15.4634 | Lusaka | 2.5 | Lusaka | Lusaka | No | Yes | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | MPMC | MPMC | 15 | perkins | CP14 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 52 |  | 2 | MTNAirtel | T0167 | ZM3529 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_370A
1045 | ZM3548 | IHS_LSK_371A | MTENDERE-MKT-3-RLF (Trust Medical Hospital) | 28.353 | -15.4118 | Lusaka | 2 | Lusaka | Lusaka | No | Yes | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | Lister petter | LWP4 | Leroy Sommer | TAL-A40-C J6/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 58.4 |  | 2 | MTNAirtel | T0402 | ZM3548 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_371A
1079 | ZM3570 | IHS_LSK_372A | MAPEPE | 28.2835 | -15.6216 | Lusaka | 2 | Lusaka | Kafue | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Earth Technology | Earth technology | 16 | Yanmar | 4TNE88-G1A | Leroy Sommer | ECO-28-M/4 | 375 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | GREE | GREE | 18000 | 18000 | 2 | 46 |  | 2 | MTNAirtel | T0501 | ZM3570 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_372A
1086 | ZM3600 | IHS_LSK_373A | BAOBAB | 28.2662 | -16.7304 | Lusaka | 4.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 45 | perkins | 403D-15T | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 110 |  | 3 | MTNAirtelLiquid Telecom | T0147 | ZM3600 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_373A
1088 | ZM3713 | IHS_LSK_374A | Silver rest School (CHAINDA EXT COMPLEX) | 28.4723 | -15.3571 | Lusaka | 2.5 | Lusaka | Chongwe | Yes | No | No | Urban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 40 | Indoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | MPI | MPI | 30 | perkins | 404A-22 | Leroy Sommer | ECP-28-M/4 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 54.7 |  | 3 | MTNAirtelAir-link | T0343 | ZM3713 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_374A
1089 | ZM3714 | IHS_LSK_375A | MAKENI WATCH TOWER | 28.1906 | -15.4292 | Lusaka | 1.8 | Lusaka | Kafue | No | Yes | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 403A-15 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 116 |  | 2 | MTNAirtel | T0445 | ZM3714 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_375A
1118 | ZM3716 | IHS_LSK_376A | Kafue Coverage Improvement | 28.1938 | -15.7911 | Lusaka | 4.5 | Lusaka | Kafue | No | No | No | Suburban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 48 | Indoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 403D-15T | Mecc Alte | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 83 |  | 1 | Airtel | 0 | ZM3716 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_376A
1144 | ZM3719 | IHS_LSK_377A | Chelstone Extension | 28.3787 | -15.3264 | Lusaka | 2.5 | Lusaka | Kafue | No | No | No | Urban | Silver | Silver | HUB | HUB | On air | Grid-Gen | Green Field | 18 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | CP14 | Mecc Alte | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 58.9 |  | 2 | MTNAirtel | T0446 | ZM3719 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_377A
1145 | ZM3720 | IHS_LSK_378A | Diplomatic Mission | 28.3123 | -15.4244 | Lusaka | 2.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | LG | LG | 18000 | 18000 | 2 | 76 |  | 2 | AirtelLiquid Telecom | 0 | ZM3720 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_378A
1183 | ZM3721 | IHS_LSK_379A | Bauleni | 28.381 | -15.4433 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | Yes | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 50 | Outdoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 155 |  | 1 | Airtel | 0 | ZM3721 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_379A
1185 | ZM3722 | IHS_LSK_380A | State Lodge Farms | 28.4458 | -15.5066 | Lusaka | 2.5 | Lusaka | Kafue | No | Yes | No | Suburban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404D-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 103 |  | 2 | MTNAirtel | T0230 | ZM3722 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_380A
1186 | ZM3723 | IHS_LSK_381A | New Chalala | 28.3515 | -15.4746 | Lusaka | 2.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 52 | Outdoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 135 |  | 2 | AirtelLiquid Telecom | 0 | ZM3723 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_381A
1187 | ZM3724 | IHS_LSK_382A | Makeni Farms | 28.2757 | -15.5837 | Lusaka | 1.5 | Lusaka | Kafue | No | No | No | Suburban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 46 | Outdoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 47 |  | 2 | MTNAirtel | T0529 | ZM3724 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_382A
1188 | ZM3769 | IHS_LSK_383A | KASENGA RESETTLEMENT | 28.5313 | -15.1974 | Lusaka | 1.8 | Lusaka | Kafue | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | RID | RID | 20 | Mitsubishi | S4L261SDBC | Zanardi | AL 3/4 | 1000 | Power cube | ECC500 | 400 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | N/A | N/A | 57 |  | 1 | Airtel | 0 | ZM3769 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_383A
1189 | ZM3772 | IHS_LSK_384A | Shantumbu | 28.3404 | -15.4836 | Lusaka | 1.8 | Lusaka | Lusaka | No | No | No | Urban | Silver | Silver | HUB | HUB | On air | Grid-Gen | Green Field | 52 | Outdoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | IMG | IMG | 30 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 600 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 210 |  | 3 | MTNAirtelLiquid Telecom | T0442 | ZM3772 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_384A
1192 | ZM3892 | IHS_LSK_385A | CHAINAMA | 28.3785 | -15.3868 | Lusaka | 1.8 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 41 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | CK Works | CK Works | 20 | perkins | 1103A-33 | Leroy Sommer | ECO28-VL/4 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 42.7 |  | 1 | Airtel | 0 | ZM3892 | 0 |  |  | Mesh | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_385A
1251 | ZM3893 | IHS_LSK_386A | Chitemalesa-Nyauti | 29.1974 | -15.2239 | Lusaka | 2.5 | Lusaka | Chongwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404D-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | DCDC-400AS2 | 400 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | N/A | N/A | 48 |  | 2 | MTNAirtel | T0452 | ZM3893 | 0 |  |  | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_386A
1253 | ZM3898 | IHS_LSK_387A | Olympia Extension1 | 28.3066 | -15.3811 | Lusaka | 4.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 403A-15 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 145 |  | 3 | MTNAirtelLiquid Telecom | T0281 | ZM3898 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | yes | 30 |  | Pending |  |  |  |  | IHS_LSK_387A
1254 | ZM3985 | IHS_LSK_388A | MAKENI SOUTH | 28.2108 | -15.4983 | Lusaka | 1.5 | Lusaka | Lusaka | No | No | Yes | Urban | Silver | Silver | HUB | HUB | On air | Grid-Gen | Green Field | 40 | Outdoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 73 |  | 2 | MTNAirtel | T0443 | ZM3985 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_388A
1257 | ZM3986 | IHS_LSK_389A | MAKENI EAST | 28.2629 | -15.4649 | Lusaka | 2.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 40 | Outdoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 96 |  | 4 | MTNAirtelINQLiquid Telecom | T0482 | ZM3986 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_389A
1267 | ZM3988 | IHS_LSK_390A | ALICK NKHATA - Ndeke House | 28.3162 | -14.0935 | Lusaka | 1.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 40 | Outdoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Earth Technology | Earth technology | 11 | perkins | 403A-15 | Mecc Alte | ECP-28-M/4 | 375 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 75 |  | 1 | Airtel | 0 | ZM3988 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_390A
1319 | ZM3989 | IHS_LSK_391A | ROMA NORTH | 28.3097 | -15.3601 | Lusaka | 4.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | CK Works | CK Works | 30 | perkins | 403A-15 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 155 |  | 2 | MTNAirtel | T0236 | ZM3989 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_391A
1321 | ZM3990 | IHS_LSK_392A | KAMANGA | 28.3703 | -15.3601 | Lusaka | 1.5 | Lusaka | Lusaka | No | No | Yes | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 52 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 10 | perkins | 403D-15 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 56 |  | 1 | Airtel | 0 | ZM3990 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_392A
1338 | ZM3991 | IHS_LSK_393A | AVONDALE EAST | 28.4068 | -13.3343 | Lusaka | N/A | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 52 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | N/A | N/A | 20 | N/A | N/A | N/A | N/A | N/A | Power cube | ICC330-H1-C1 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 47.2 |  | 2 | MTNAirtel | T0541 | ZM3991 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_393A
1348 | ZM3992 | IHS_LSK_394A | AIRPORT ROAD | 28.4237 | -14.0732 | Lusaka | 2.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 18 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 120 |  | 2 | AirtelINQ | 0 | ZM3992 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_394A
1353 | ZM3993 | IHS_LSK_395A | BARLASTONE | 28.218 | -16.7251 | Lusaka | 2.5 | Lusaka | Kafue | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 40 | Outdoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Earth Technology | Earth technology | 20 | perkins | 403A-15 | Mecc Alte | ECP-28-M/4 | 375 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 102 |  | 2 | MTNAirtel | T0218 | ZM3993 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_395A
1365 | ZM3995 | IHS_LSK_396A | SHORT HORN_2 | 28.1912 | -15.5391 | Lusaka | 2.5 | Lusaka | Kafue | No | No | No | Suburban | Silver | Silver | HUB | HUB | On air | Grid-Gen | Green Field | 60 | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 87 |  | 2 | MTNAirtel | T0329 | ZM3995 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_396A
1369 | ZM4000 | IHS_LSK_397A | WOODLANDS MICRO | 28.3419 | -15.4372 | Lusaka | 2.5 | Lusaka | Lusaka | No | Yes | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Roof Top | RT | Outdoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | In House | Gen Logic | Gen Logic | 20 | N/A | N/A | N/A | Leroy Sommer | 1000 | Power cube | ECC500 | 400 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | N/A | N/A | 160 |  | 3 | MTNAirtelLusaka Radio | T0175 | ZM4000 | 0 |  |  | n/a | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_397A
1371 | ZM6007 | IHS_LSK_398A | Kapete | 28.713 | -15.2713 | Lusaka | 1.5 | Lusaka | Chongwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 40 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 404A-22 | Leroy Sommer | TAL 040 DJ 6S/4 | 1000 | MPPT | MPPT | 93.75 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | N/A | N/A | 62 |  | 1 | Airtel | 0 | ZM6007 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_398A
1374 | ZM6008 | IHS_LSK_399A | Nangwenya | 28.821 | -15.3692 | Lusaka | 2.5 | Lusaka | Chongwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | S4L261SDBC | Mecc Alte | AL 3/4 | 1000 | Power cube | ECC500 | 150 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 58 |  | 1 | Airtel | 0 | ZM6008 | 0 |  |  | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | Done | 2019-06-03 | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_399A
1377 | ZM6012 | IHS_LSK_400A | LUKWIPA | 29.9018 | -15.0494 | Lusaka | 1.5 | Lusaka | Chongwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 10 | perkins | 4TNE88-G1A | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 0 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 20 |  | 1 | Airtel | 0 | ZM6012 | 0 |  |  | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_400A
1384 | ZM6013 | IHS_LSK_401A | Chinyunyu | 29.0047 | -15.2665 | Lusaka | 1.8 | Lusaka | Chongwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen-solar | Green Field | 40 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | IMG | IMG | 20 | perkins | 403A-15 | Leroy Sommer | ECO-28-M/4 | 600 | Power cube | ECC500 | 400 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 53 |  | 2 | MTNAirtel | T0427 | ZM6013 | 0 |  |  | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_401A
1385 | ZM6047 | IHS_LSK_402A | Mwambilia Village | 28.715 | -15.3445 | Lusaka | 1.5 | Lusaka | Kafue | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 40 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | MPMC | MPMC | 20 | perkins | S4L261SDBC | Leroy Sommer | AL 3/4 | 1000 | MPPT | MPPT | 93.75 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | N/A | N/A | 40 |  | 1 | Airtel | 0 | ZM6047 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_402A
1389 | ZM6070 | IHS_LSK_403A | Shimabala_Mapepe Area | 28.2559 | -15.7192 | Lusaka | 2 | Lusaka | Kafue | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 42 | Outdoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | MPMC | MPMC | 16 | perkins | 403D-15T | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 47 |  | 2 | MTNAirtel | T0528 | ZM6070 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_403A
1391 | ZM6081 | IHS_LSK_404A | Kabanana South_1_Rlf | 28.2909 | -15.3529 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | Yes | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 40 | Outdoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | IMG | IMG | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 600 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 125 |  | 2 | MTNAirtel | T0473 | ZM6081 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_404A
1428 | ZM6082 | IHS_LSK_405A | Kanyama West_1_Rlf | 28.2327 | -15.42 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 40 | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 403A-15 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 86 |  | 1 | Airtel | 0 | ZM6082 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_405A
1430 | ZM6083 | IHS_LSK_406A | Kanyama West 2 Rlf | 28.2448 | -15.4325 | Lusaka | 2.5 | Lusaka | Lusaka | No | Yes | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 40 | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | IMG | IMG | 20 | perkins | 403A-15 | Leroy Sommer | ECO-28-M/4 | 600 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 63 |  | 2 | MTNAirtel | T0346 | ZM6083 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_406A
1434 | ZM6146 | IHS_LSK_407A | Mpango Basic School | 28.7561 | -15.2025 | Lusaka | 2.5 | Lusaka | Chongwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen-solar | Green Field | 70 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Earth Technology | Earth technology | 15 | perkins | S4L261SDBC | Leroy Sommer | TAL 040 DJ 6S/4 | 375 | Power cube | ICC330-H1-C1 | 400 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | N/A | N/A | 63 |  | 2 | MTNAirtel | T0454 | ZM6146 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_407A
1439 | ZM6181 | IHS_LSK_408A | Unza Vet_1 Rlf | 28.3326 | -15.394 | Lusaka | 2.5 | Lusaka | Lusaka | Yes | Yes | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 40 | Outdoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Earth Technology | Earth technology | 20 | perkins | 403A-15 | Leroy Sommer | TAL 040F J 6S/4 | 375 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 153 |  | 3 | MTNAirtelLiquid Telecom | T0405 | ZM6181 | 0 |  |  | Palisade | Inala | 2022-08-05 | yes | Yes |  | 2 |  |  | Done | 2019-05-22 | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_408A
1446 | ZM6187 | IHS_LSK_409A | Matero East_2_Rlf | 28.2643 | -15.3862 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 40 | Outdoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Earth Technology | Earth technology | 20 | perkins | 403A-15 | Leroy Sommer | ECO-28-M/4 | 375 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 85 |  | 1 | Airtel | 0 | ZM6187 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_409A
1448 | ZM6192 | IHS_LSK_411A | Roma_2_Rlf | 28.3298 | -15.374 | Lusaka | 2 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 40 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 16 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 85 |  | 2 | AirtelLiquid Telecom | 0 | ZM6192 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_411A
1450 | ZM6477 | IHS_LSK_412A | KANYAMA WEST_3_Rlf | 28.2309 | -15.4333 | Lusaka | 1.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | CK Works | CK Works | 20 | perkins | 403A-15 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 78 |  | 2 | MTNAirtel | T0487 | ZM6477 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_412A
1451 | ZM6481 | IHS_LSK_413A | KABWATA SERVICE_2_Rlf | 28.2966 | -15.4493 | Lusaka | 4.5 | Lusaka | Lusaka | Yes | Yes | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 403D-15T | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 600 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 160 |  | 3 | MTNAirtelLiquid Telecom | T0292 | ZM6481 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_413A
1452 | ZM6482 | IHS_LSK_414A | INTERLAND_3_Rlf | 28.3151 | -15.449 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 40 | Outdoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 403D-15T | Mecc Alte | ECO-28-M/4 | 1000 | IPT | Delta | 250 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 106 |  | 1 | Airtel | 0 | ZM6482 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_414A
1467 | ZM6489 | IHS_LSK_415A | KAFUE_3_Rlf | 28.1938 | -15.7701 | Lusaka | 2.5 | Lusaka | Kafue | Yes | No | No | Suburban | Silver | Silver | HUB | HUB | On air | Grid-Gen | Green Field | 50 | Outdoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Earth Technology | Earth technology | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 375 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 68.1 |  | 3 | MTNAirtelLiquid Telecom | T0474 | ZM6489 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_415A
1478 | ZM6496 | IHS_LSK_416A | KAMWALA SOUTH-2 rlf | 28.3032 | -15.4706 | Lusaka | 1.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 42 | Outdoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | HIMOINSA | HIMOINSA | 13 | perkins | 403A-15 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 130 |  | 2 | MTNAirtel | T0488 | ZM6496 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_416A
1479 | ZM6575 | IHS_LSK_417A | Bokomo | 28.3386 | -15.23 | Lusaka | 1.5 | Lusaka | Lusaka | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 40 | Outdoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | MPI-Perkins | MPI-Perkins | 13 | Yanmar | 4TNE88-G1A | Leroy Sommer | ECO-28-M/4 | 600 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 73 |  | 2 | MTNAirtel | T0439 | ZM6575 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_417A
1499 | ZM6577 | IHS_LSK_418A | Lwiimba | 28.8184 | -15.505 | Lusaka | 2.5 | Lusaka | Chongwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040 DJ 6S/4 | 1000 | MPPT | MPPT | 187.5 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | N/A | N/A | 69.9 |  | 2 | MTNAirtel | T0462 | ZM6577 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_418A
1507 | ZM6619 | IHS_LSK_419A | Adventure City | 28.4057 | -14.184 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | MPI | MPI | 20 | perkins | 404A-22 | Leroy Sommer | LSA 42.3 VS 2J M/4 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 98 |  | 2 | MTNAirtel | T0438 | ZM6619 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_419A
1509 | ZM6651 | IHS_LSK_420A | Chalala 3G rlf | 28.3258 | -15.4746 | Lusaka | 1.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 50 | Outdoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | MPMC | MPMC | 13 | perkins | 403D-15T | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 197 |  | 2 | AirtelLiquid Telecom | 0 | ZM6651 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_420A
1511 | ZM6659 | IHS_LSK_421A | Chamba valley 3G | 28.3487 | -15.3408 | Lusaka | 1.8 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | HUB | HUB | On air | Grid-Gen | Green Field | 40 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 403A-15 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 1600 | 48 | 100 | 16 | N/A | N/A | N/A | N/A | N/A | 42.2 |  | 2 | AirtelLiquid Telecom | 0 | ZM6659 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_421A
1512 | ZM6714 | IHS_LSK_422A | Freedom (Makeni south end 3G) | 28.2669 | -15.5418 | Lusaka | 1.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 40 | Outdoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 13 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 56 |  | 1 | Airtel | 0 | ZM6714 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_422A
1514 | ZM6751 | IHS_LSK_423A | Unza | 28.3237 | -15.3958 | Lusaka | N/a | Lusaka | Lusaka | Yes | Yes | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | N/a | N/a | 20 | N/a | N/a | N/a | N/a | N/a | Power cube | ICC330-H1-C1 | 400 | Lithium | 350 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 168 |  | 3 | MTNAirtelLiquid Telecom | T0447 | ZM6751 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_423A
1518 | ZM6758 | IHS_LSK_424A | New kasama Cov improv. | 28.3651 | -15.4767 | Lusaka | 1.8 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | CK Works | CK Works | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | LG18000 | N/A | 128 |  | 2 | AirtelLiquid Telecom | 0 | ZM6758 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_424A
1537 | ZM6764 | IHS_LSK_425A | Kamwala south rlf | 28.3091 | -15.4601 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 403A-15 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 100 | 48 | 100 | 1 | N/A | N/A | N/A | N/A | N/A | 195 |  | 3 | MTNAirtelLiquid Telecom | T0475 | ZM6764 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_425A
1545 | ZM6765 | IHS_LSK_426A | Makeni Ecumenical Centre | 28.2494 | -15.4615 | Lusaka | 1.8 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 40 | Outdoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 45 |  | 2 | AirtelLiquid Telecom | 0 | ZM6765 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_426A
1547 | ZM6767 | IHS_LSK_427A | Ngwerere East | 28.3176 | -15.3111 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | Yes | Rural | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Outdoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 1200 | 48 | 100 | 12 | N/A | N/A | N/A | N/A | N/A | 184 |  | 2 | MTNAirtel | T0437 | ZM6767 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_427A
1551 | ZM6778 | IHS_LSK_428A | Gray Zulu makeni (Makeni 3G ) | 28.2314 | -15.47 | Lusaka | 1.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 800 | 2 | 800 | 24 | N/A | N/A | N/A | N/A | N/A | 38 |  | 1 | Airtel | 0 | ZM6778 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_428A
1552 | ZM6779 | IHS_LSK_429A | Waterworks (Makeni south 3G rlf ) | 28.3131 | -15.4887 | Lusaka | 2.5 | Lusaka | Lusaka | Yes | No | No | Urban | Gold | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | GNM | GNM | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 600 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 105 |  | 3 | MTNAirtelLiquid Telecom | T0519 | ZM6779 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_429A
1553 | ZM6780 | IHS_LSK_430A | Nampundwe 3G | 27.9283 | -15.5089 | Lusaka | 1.8 | Lusaka | Lusaka | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Yanmar | Yanmar | 15 | perkins | 403A-15 | Leroy Sommer | ECO-28-M/4 | 600 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 74 |  | 1 | Airtel | 0 | ZM6780 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_430A
1557 | ZM6834 | IHS_LSK_431A | Foxdale Residential - Coverage | 28.3245 | -15.3492 | Lusaka | 4.5 | Lusaka | Lusaka | Yes | Yes | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | CK Works | CK Works | 30 | perkins | 403A-15 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 166 |  | 3 | MTNAirtelLiquid Telecom | T0436 | ZM6834 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_431A
1559 | ZM6835 | IHS_LSK_432A | Roma Exchange 3 rlf | 28.3124 | -15.3774 | Lusaka | 1.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | New Way | New Way | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 56 |  | 2 | AirtelLiquid Telecom | 0 | ZM6835 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_432A
1568 | ZM6848 | IHS_LSK_433A | Garden Motel/Kanyama Area | 28.2344 | -15.4064 | Lusaka | 2.5 | Lusaka | Lusaka | No | Yes | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404D-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 102 |  | 2 | MTNAirtel | T0440 | ZM6848 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_433A
1569 | ZM6861 | IHS_LSK_434A | Meanwood Ibex | 28.4225 | -15.3926 | Lusaka | 1.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | MPMC | MPMC | 30 | perkins | 404A-22 | Leroy Sommer | LSA 40M5 C 6/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 35.1 |  | 3 | MTNAirtelLiquid Telecom | T0510 | ZM6655 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_434A
1571 | ZM6887 | IHS_LSK_435A | Sheki Sheki Road | 28.269 | -15.3935 | Lusaka | 2.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 180 |  | 5 | MTNAirtelINQLiquid TelecomSmartnet | T0498 | ZM6887 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | yes - Emergency | 20 | 43655 | closed |  |  |  |  | IHS_LSK_435A
1572 | ZM6961 | IHS_LSK_436A | Salama | 28.3932 | -15.3932 | Lusaka | 2.5 | Lusaka | Lusaka | Yes | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 404A-22 | Mecc Alte | ECO-28-M/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 205 |  | 3 | MTNAirtelLiquid Telecom | T0491 | ZM6961 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_436A
1573 | ZM0291 | IHS_LSK_437A | G-Greens | 28.3198 | -15.5035 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | CK Works | CK Works | 20 | perkins | 403D-15G | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 96 |  | 3 | MTNAirtelLiquid Telecom | T0505 | ZM0291 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_437A
1578 | ZM0135 | IHS_LSK_439A | TEN MILES WEST | 28.2433 | -15.3033 | Lusaka | 1.8 | Lusaka | Lusaka | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | CK Works | CK Works | 15 | perkins | 403D-15G | Leroy Sommer | ECO-28-M/4 | 600 | Power cube | ECC500 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 170 |  | 2 | MTNAirtel | T0500 | ZM0135 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_439A
1583 | ZM0157 | IHS_LSK_440A | Vorna Valley | 28.4045 | -15.305 | Lusaka | 4.5 | Lusaka | Lusaka | No | No | No | Urban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Vitalgen | Vitalgen | 30 | perkins | 403D-15G | Leroy Sommer | ECO-28-M/4 | 600 | Power cube | ICC330-H1-C1 | 400 | NARADA | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 144.2 |  | 3 | MTNAirtelLiquid Telecom | T0508 | ZM0157 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_440A
1588 | ZM0294 | IHS_LSK_441A | Bonanza | 28.4352 | -15.263 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | P4 | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 130 |  | 4 | MTNAirtelLiquid TelecomParatus Telecom | T0246 | ZM0294 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_441A
1614 | ZM0364 | IHS_LSK_444A | Woodlands Stadium | 28.3453 | -15.4469 | Lusaka | 2 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Yanmar | Yanmar | 16 | Yanmar | 404A-22 | Leroy Sommer | ECO-28-M/4 | 600 | Emerson | R483200 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 115 |  | 1 | Airtel | 0 | ZM0364 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_444A
1618 | ZM0365 | IHS_LSK_445A | Roma Park | 28.3222 | -15.3604 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Emerson | R483200 | 250 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 55 |  | 1 | Airtel | 0 | ZM0365 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_445A
1620 | ZM0369 | IHS_LSK_446A | Chelston Catholic Church | 28.3867 | -15.3707 | Lusaka | 1.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | CK Works | CK Works | 20 | perkins | 404A-22 | Leroy Sommer | ECP-28-M/4 | 800 | Emerson | R483200 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 120 |  | 2 | MTNAirtel | T0543 | ZM0369 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_446A
1622 | ZM0371 | IHS_LSK_447A | Government Farms (Nelson Mandela) | 28.2507 | -15.3549 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Emerson | R483200 | 450 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 166 |  | 1 | Airtel | 0 | ZM0371 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_447A
1625 | ZM0439 | IHS_LSK_448A | PHI | 28.3616 | -15.3865 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Emerson | R483200 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 60 |  | 2 | MTNAirtel | T0556 | ZM0439 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_448A
1626 | ZM0440 | IHS_LSK_449A | Garden Park | 28.2217 | -15.4056 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404D-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Emerson | R483200 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 83 |  | 1 | Airtel | 0 | ZM0440 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_449A
1630 | ZM0443 | IHS_LSK_450A | Shalom School (Mpondamali) | 28.2202 | -15.4249 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404D-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Emerson | R483200 | 250 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 70 |  | 1 | Airtel | 0 | ZM0443 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_450A
1631 | ZM0447 | IHS_LSK_451A | Libala South | 28.3056 | -15.4479 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Emerson | R483200 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 144 |  | 1 | Airtel | 0 | ZM0447 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_451A
1632 | ZM0451 | IHS_LSK_452A | Longacres | 28.315 | -15.418 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 25 | Outdoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404D-22 | Mecc Alte | ECO-28-M/4 | 1000 | Emerson | R483200 | 0 | Narada | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 125 |  | 1 | Airtel | 0 | ZM0451 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_452A
1639 | ZM0453 | IHS_LSK_453A | ETG | 28.2521 | -15.4117 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | CK Works | CK Works | 20 | perkins | 404D-22 | Mecc Alte | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 84 |  | 1 | Airtel | 0 | ZM0453 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_453A
1641 | ZM0457 | IHS_LSK_454A | Dream Valley | 28.3904 | -15.4078 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECP-28-M/4 | 1000 | Power cube | R483200 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 128 |  | 1 | Airtel | 0 | ZM0457 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_454A
1643 | ZM0458 | IHS_LSK_455A | Kwamwena Phase 3 | 28.3443 | -15.3259 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECP-28-M/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 76 |  | 2 | AirtelLiquid Telecom | 0 | ZM0458 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_455A
1644 | ZM0459 | IHS_LSK_456A | Chongwe District Hospital | 28.668 | -15.3383 | Lusaka | 2.5 | Lusaka | Chongwe | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Emerson | R483200 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 60 |  | 1 | Airtel | 0 | ZM0459 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_456A
1648 | ZM0462 | IHS_LSK_457A | KK International Airport | 28.4479 | -15.3209 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Rural | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 44 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | CK Works | CK Works | 20 | perkins | 404A-22 | Leroy Sommer | ECP-28-M/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A |  | N/A | 74 |  | 1 | Airtel | 0 | ZM0462 |  |  |  | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_457A
1650 | ZM0465 | IHS_LSK_458A | Beit Cure | 28.2742 | -15.3623 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 96 |  | 1 | Airtel | 0 | ZM0465 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_458A
1668 | ZM0478 | IHS_LSK_459A | Barn Motel | 28.4545 | -16.098 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECP-28-M/4 | 1000 | Emerson | R483200 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 50 |  | 1 | Airtel | 0 | ZM0478 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_459A
1672 | ZM0548 | IHS_LSK_460A | Helen kaunda | 28.3483 | -15.4044 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Emerson | R483200 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 122 |  | 1 | Airtel | 0 | ZM0548 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_460A
1673 | ZM0549 | IHS_LSK_461A | Chikubabe Jack (Greg Lungu) | 28.2998 | -15.4773 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 58 |  | 1 | Airtel | 0 | ZM0549 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_461A
1688 | ZM0551 | IHS_LSK_462A | Chipichipi | 28.2597 | -15.4408 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Emerson | R483200 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 65 |  | 1 | Airtel | 0 | ZM0551 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_462A
1690 | ZM0552 | IHS_LSK_463A | St. Theresa Chainda | 28.4121 | -15.3902 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECP-28-M/4 | 1000 | Emerson | R483200 | 250 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 56 |  | 1 | Airtel | 0 | ZM0552 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_463A
1691 | ZM0553 | IHS_LSK_464A | Nkoloma Stadium | 28.3744 | -15.3703 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECP-28-M/4 | 1000 | Emerson | R483200 | 250 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 70 |  | 1 | Airtel | 0 | ZM0553 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_464A
1693 | ZM0555 | IHS_LSK_465A | Kafue Green Valley | 28.1827 | -15.7399 | Lusaka | 2.5 | Lusaka | Kafue | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 600 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 71 |  | 1 | Airtel | 0 | ZM0555 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_465A
1699 | ZM0557 | IHS_LSK_466A | Mai Chola | 28.2952 | -15.3416 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404D-22 | Mecc Alte | ECO-28-M/4 | 1000 | Emerson | R483200 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 135 |  | 1 | Airtel | 0 | ZM0557 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_466A
1702 | ZM0558 | IHS_LSK_467A | Matero St. Monicas (Matero St. Marys) | 28.2658 | -15.3782 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Emerson | R483200 | 450 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 130 |  | 1 | Airtel | 0 | ZM0558 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_467A
1712 | ZM0565 | IHS_LSK_469A | Mtendere West | 28.3786 | -15.3953 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ICC330-H1-C1 | 250 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 55 |  | 1 | Airtel | 0 | ZM0565 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_469A
1714 | ZM0566 | IHS_LSK_470A | Kasangula Petroda | 28.2919 | -15.3688 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | IMG | IMG | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 600 | Power cube | ECC500 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 83 |  | 1 | Airtel | 0 | ZM0566 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_470A
1715 | ZM0567 | IHS_LSK_471A | Katima Mulilo Road | 28.3105 | -15.3858 | Lusaka | 2 | Lusaka | Lusaka | No | No | No | Rural | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | John Banda | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | CK Works | CK Works | 16 | Yanmar | 0 | 0 | 0 | 1000 | Emerson | Emmerson | 450 | Agisson | 800 | 2 | 800 | 24 | N/A | N/A | N/A |  | N/A | 65 |  | 1 | Airtel | 0 | ZM0567 |  |  |  | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_471A
1716 | ZM0568 | IHS_LSK_472A | Clema Kanyama | 28.2526 | -15.4266 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404D-22 | Mecc Alte | ECO-28-M/4 | 1000 | Emerson | R483200 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 79 |  | 1 | Airtel | 0 | ZM0568 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_472A
1718 | ZM0569 | IHS_LSK_473A | Chawama Railway | 28.288 | -15.452 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 53 |  | 1 | Airtel | 0 | ZM0569 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_473A
1720 | ZM0570 | IHS_LSK_474A | kwa banda masauko | 28.2407 | -15.4379 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404D-22 | Mecc Alte | ECO-28-M/4 | 1000 | Emerson | R483200 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 95 |  | 1 | Airtel | 0 | ZM0570 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_474A
1727 | ZM0530 | IHS_LSK_475A | Mikango West | 28.5419 | -15.5047 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban | Platinum | Platinum | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 45 |  | 1 | Airtel | 0 | ZM0530 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LSK_475A
1731 | ZM1478 | IHS_LSK_478A | PTC | 28.6907 | -15.3254 | Lusaka | 4.5 | Lusaka | Chongwe | No | No | No | Urban | Silver | Silver | BTS | BTS | On air | Gen Only | Green Field | 50 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 77 |  | 1 | Airtel | 0 | ZM1478 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_LSK_478A
1735 | ZM1479 | IHS_LSK_479A | Lusoke | 28.667 | -15.3219 | Lusaka | 4.5 | Lusaka | Chongwe | No | No | No | Urban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 78 |  | 1 | Airtel | 0 | ZM1479 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_LSK_479A
1761 | ZM1487 | IHS_LSK_480A | Kafue Bata Site & Service | 28.1559 | -15.7556 | Lusaka | 4.5 | Lusaka | Kafue | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 190 |  | 1 | Airtel | 0 | ZM1487 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_LSK_480A
1762 | ZM1394 | IHS_LSK_481A | Mwalubemba | 28.4922 | -15.3063 | Lusaka | 4.5 | Lusaka | Lusaka | No | No | No | Urban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 51 | Outdoor | Malvin Hakokole | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1001 | Power cube | ICC330-H1-C2 |  | Lithium | 300 | 48 | 150 | 3 | N/A | N/A | N/A | N/A | N/A | 77 |  | 1 | Airtel | 0 | ZM1394 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_481A
1763 | ZM1399 | IHS_LSK_482A | Mikango Sec. School | 28.6024 | -15.5125 | Lusaka | 2.5 | Lusaka | Lusaka | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Kelly Musama | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 56 |  | 1 | Airtel | 0 | ZM1399 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_LSK_482A
1768 | ZM1372 | IHS_LSK_483A | Shibuyunji Basic School | 27.8292 | -15.449 | Central | 4.5 | Central | Shibuyunji | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Joseph Mulenga | N/A | N/A | Airtel | Evans Ngonga | CCS | CCS | perkins | [6 empty] | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_LSK_483A
1771 | ZM1395 | IHS_LSK_484A | Chilyabale Primary School | 28.7733 | -15.4237 | Lusaka | 2.5 | Lusaka | Chongwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Gen Only | Green Field | 60 | Outdoor | Malvin Hakokole | CCS | CCS | Airtel | Evans Ngonga | CCS | CCS | perkins |  | 30 | perkins |  |  |  | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [8 empty] | Palisade |  | 2022-09-09 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_484A
1775 | ZM1397 | IHS_LSK_485A | Chanyanya RHC | 28.019 | -15.6704 | Lusaka | 2.5 | Lusaka | Kafue | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Samuel Mumba | N/A | N/A | Airtel | Evans Ngonga | CCS | CCS | perkins | [6 empty] | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_LSK_485A
1824 | ZM1564 | IHS_LSK_486A | Chikuli Primary School | 28.5435 | -15.2897 | Lusaka | 4.5 | Lusaka | Chongwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Gen Only | Green Field | 60 | Outdoor | Malvin Hakokole | CCS | CCS | Airtel | Evans Ngonga | CCS | CCS | perkins |  | 30 | perkins |  |  |  | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 59 | [8 empty] | Palisade |  | 2022-09-10 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LSK_486A
1000 | T3072 | IHS_LUP_001M | Mansa main | 28.9007 | -11.2086 | Northern | 2.5 | LUAPULA | MANSA | Yes | No | No | Suburban | 2G 3G 4G | P2 | BB | BTS | On air | Grid-Gen | Green Field | 70 | Indoor | Kennedy Mwansa | Peter Choongo | Emmanuel Mulayi | MTN | Flavian Mazhambi | In House | In House | Lamasat | Lamasat | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | sumsung | sumsung | 18000 | 18000 | 2 | 105 |  | 3 | MTNLiquid TelecomParatus Telecom | T1171 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  | 16 |  | collected and already in central warehouse |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_001M
1002 | T3376 | IHS_LUP_002M | Mansa South | 28.8954 | -11.2209 | Northern | 2.5 | LUAPULA | MANSA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Kennedy Mwansa | Peter Choongo | Emmanuel Mulayi | MTN | Flavian Mazhambi | In House | In House | CK Works | CK Works | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 95 |  | 2 | MTNAirtel | T3376 | ZM6777 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 24 |  | Reused at Lengwe | pending |  | No | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_LUP_002M
1596 | T3227 | IHS_LUP_003M | Senama | 28.8744 | -11.1829 | Northern | 1.8 | LUAPULA | MANSA | No | No | No | Rural | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Kennedy Mwansa | Peter Choongo | Emmanuel Mulayi | MTN | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Delta | IPT | 250 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | n/a | N/A | 125 |  | 2 | MTNAirtel | T3227 | ZM0426 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_003M
1304 | T3308 | IHS_LUP_004M | Mutende 2 | 28.9552 | -11.2392 | Northern | 1.8 | LUAPULA | MANSA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Kennedy Mwansa | Peter Choongo | Emmanuel Mulayi | MTN | Flavian Mazhambi | In House | In House | IMG | IMG | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Delta | IPT | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 57 |  | 1 | MTN | T3308 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_004M
356 | T3373 | IHS_LUP_005M | Fimpulu | 28.824 | -11.3922 | Northern | 2.5 | LUAPULA | MANSA | No | No | No | Rural | 2G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Kennedy Mwansa | Peter Sinkala | Emmanuel Mulayi | MTN | Flavian Mazhambi | In House | In House | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 45 |  | 1 | MTN | T3373 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_LUP_005M
1004 | T3109 | IHS_LUP_006M | Mansa ZNS | 28.8177 | -10.9499 | Northern | 2.5 | LUAPULA | MANSA | No | No | No | Rural | 2G 3G | P4 | BB | BTS | On air | Grid-Gen | Green Field | 70 | Indoor | Kennedy Mwansa | Peter Sinkala | Emmanuel Mulayi | MTN | Flavian Mazhambi | In House | In House | Lamasat | Lamasat | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 68 |  | 1 | MTN | T3109 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_006M
1202 | T3113 | IHS_LUP_007M | Mufuma | 29.1656 | -11.272 | Northern | 1.8 | LUAPULA | SAMFYA | No | No | No | Rural | 2G | P4 | HUB | BB | On air | Grid-Gen | Green Field | 80 | Indoor | Kennedy Mwansa | Peter Choongo | Emmanuel Mulayi | MTN | Flavian Mazhambi | In House | In House | IMG | IMG | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 75 |  | 2 | MTNAirtel | T3113 | ZM3819 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 24 |  | still on site | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_007M
468 | T3292 | IHS_LUP_008M | Kabelenge | 28.9981 | -10.8935 | Northern | 2 | LUAPULA | MANSA | No | No | No | Rural | 2G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Kennedy Mwansa | Peter Sinkala | Emmanuel Mulayi | MTN | Flavian Mazhambi | In House | In House | ET | ET | 16 | perkins | GU51798V | Leroy Sommer | TAL 040F J 6S/4 | 600 | Delta | IPT | 250 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 35 |  | 1 | MTN | T3292 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 16 |  | still on site | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_008M
268 | T3135 | IHS_LUP_009M | Chisunka BB | 28.7909 | -10.7857 | Northern | 2.5 | LUAPULA | MANSA | No | No | No | Rural | 2G | P4 | BB | BB | On air | Grid-Gen | Green Field | 70 | Indoor | Kennedy Mwansa | Peter Sinkala | Emmanuel Mulayi | MTN | Flavian Mazhambi | In House | In House | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | LSC 128S2 | 600 | Power cube | Powercube | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 65 |  | 2 | MTNAirtel | T3135 | ZM3820 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_LUP_009M
1298 | T3119 | IHS_LUP_010M | Musonda Falls | 28.8094 | -10.7081 | Northern | 1.8 | LUAPULA | MANSA | No | No | No | Rural | 2G 3G | P4 | BTS | BB | On air | Grid-Gen | Green Field | 54 | Outdoor | Kennedy Mwansa | Peter Sinkala | Emmanuel Mulayi | MTN | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 20 | perkins | GL-PM-C1000-15-3P-7320 | Leroy Sommer | ECP-28-1L/1 | 1000 | Delta | IPT | 250 | Power safe | 1200 | 2 | 1200 | 24 | N/A | N/A | N/A | n/a | N/A | 65 |  | 2 | MTNAirtel | T3119 | ZM3810 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  | 10 |  | still on site |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_010M
1590 | T3074 | IHS_LUP_011M | Samfya | 29.5613 | -11.3755 | Northern | 2 | LUAPULA | SAMFYA | No | No | No | Rural | 2G 3G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 80 | Indoor | Kennedy Mwansa | Peter Choongo | Emmanuel Mulayi | MTN | Flavian Mazhambi | In House | In House | CK Works | CK Works | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 71 |  | 2 | MTNINQ | T3074 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | NO | NO |  |  |  | still on site |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_011M
49 | T3131 | IHS_LUP_012M | Bululu BB | 29.1397 | -10.5691 | Northern | 2 | NORTHERN | LUWINGU | No | No | No | Rural | 2G | P4 | BB | BB | On air | Grid-Gen | Green Field | 60 | Indoor | Kennedy Mwansa | Peter Sinkala | Emmanuel Mulayi | MTN | Flavian Mazhambi | In House | In House | Vitalgen | Vitalgen | 16 | perkins | GU51794 | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 31 |  | 1 | MTN | T3131 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  | 4 |  | still on site |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_012M
986 | T3239 | IHS_LUP_013M | Mambilima | 28.6589 | -10.5231 | Northern | 1.8 | LUAPULA | MWENSE | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Outdoor | Kennedy Mwansa | Peter Sinkala | Emmanuel Mulayi | MTN | Flavian Mazhambi | In House | In House | IMG | IMG | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | 36 KW ICC330-HA1-C10 | 600 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | n/a | N/A | 65 |  | 1 | MTN | T3239 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | NO | NO |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_013M
1210 | T3146 | IHS_LUP_014M | Mukabi | 28.8424 | -10.4219 | Northern | 1.8 | LUAPULA | MWENSE | No | No | No | Rural | 2G | P4 | BB | BTS | On air | Solar-Gen | Green Field | 54 | Indoor | Kennedy Mwansa | Peter Sinkala | Emmanuel Mulayi | MTN | Flavian Mazhambi | In House | In House | Vitalgen | Vitalgen | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Cordex | CodexH CX RF HP48-4KW | 350 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 45 |  | 1 | MTN | T3146 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | NO | NO | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_014M
1330 | T3073 | IHS_LUP_015M | Mwanse | 28.7072 | -10.3923 | Northern | 2.5 | LUAPULA | MWENSE | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Indoor | Kennedy Mwansa | Peter Sinkala | Emmanuel Mulayi | MTN | Flavian Mazhambi | In House | In House | Ghadder | Ghadder | 20 | perkins | GV51790V | Leroy Sommer | PRO185 C/4 | 1000 | Delta | IPT | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 66 |  | 1 | MTN | T3073 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_015M
335 | T3136 | IHS_LUP_016M | Diamond S | 29.2629 | -10.4367 | Northern | 2 | NORTHERN | LUWINGU | No | No | No | Rural | 2G | P4 | BB | BB | On air | Grid-Gen | Green Field | 48 | Indoor | Kennedy Mwansa | Peter Sinkala | Emmanuel Mulayi | MTN | Flavian Mazhambi | In House | In House | IMG | IMG | 16 | perkins | GV51794V | Leroy Sommer | TAL 040F J 6S/4 | 600 | Delta | IPT | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 54 |  | 1 | MTN | T3136 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  | 24 |  | still on site |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_016M
887 | T3143 | IHS_LUP_017M | Lukwesa | 28.642 | -10.1671 | Northern | 2 | LUAPULA | MWENSE | No | No | No | Rural | 2G 3G | P4 | BB | BTS | On air | Grid-Gen | Green Field | 54 | Indoor | Kennedy Mwansa | Danny Masumba | Stanley Bwalya | MTN | Flavian Mazhambi | In House | In House | IMG | IMG | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | Power safe | 1200 | 2 | 1200 | 24 | LG | LG | 18000 | 18000 | 2 | 70 |  | 2 | MTNAirtel | T3143 | ZM3816 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  | 14 |  | stolen |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_017M
657 | T3139 | IHS_LUP_018M | Kapala | 28.6409 | -10.0777 | Northern | 2 | LUAPULA | MWENSE | No | No | No | Rural | 2G | P4 | BB | BB | On air | Grid-Gen | Green Field | 54 | Indoor | Kennedy Mwansa | Danny Masumba | Stanley Bwalya | MTN | Flavian Mazhambi | In House | In House | CK Works | CK Works | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | Power safe | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 45 |  | 1 | MTN | T3139 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  | 10 | collected still at regional office | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_018M
222 | T3134 | IHS_LUP_019M | Chinyanta BB | 28.7056 | -10.0134 | Northern | 1.8 | LUAPULA | KAWAMBWA | No | No | No | Rural | 2G | P4 | BB | BB | On air | Grid-Gen | Green Field | 54 | Indoor | Kennedy Mwansa | Danny Masumba | Stanley Bwalya | MTN | Flavian Mazhambi | In House | In House | IMG | IMG | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 59 |  | 1 | MTN | T3134 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_019M
1497 | T3151 | IHS_LUP_020M | Ntumba Chushi | 28.9469 | -9.8344 | Northern | 2 | LUAPULA | KAWAMBWA | No | No | No | Rural | 2G | P4 | BB | BTS | On air | Grid-Gen | Green Field | 66 | Indoor | Kennedy Mwansa | Danny Masumba | Stanley Bwalya | MTN | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 1000 | Delta | IPT | 250 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 43 |  | 1 | MTN | T3151 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_020M
758 | T3104 | IHS_LUP_021M | Kazembe | 28.7599 | -9.8239 | Northern | 1.8 | LUAPULA | KAWAMBWA | No | No | No | Rural | 2G 3G | P4 | BTS | BB | On air | Grid-Gen | Green Field | 54 | Outdoor | Kennedy Mwansa | Danny Masumba | Stanley Bwalya | MTN | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Amaron | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 90 |  | 2 | MTNAirtel | T3104 | ZM6578 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_021M
753 | T3071 | IHS_LUP_022M | Kawambwa | 29.0805 | -9.804 | Northern | 1.8 | LUAPULA | KAWAMBWA | No | No | No | Rural | 2G 3G | P4 | HUB | BTS | On air | Grid-Gen | Green Field | 70 | Indoor | Kennedy Mwansa | Danny Masumba | Stanley Bwalya | MTN | Flavian Mazhambi | In House | In House | IMG | IMG | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 102 |  | 1 | MTN | T3071 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_022M
1070 | T3144 | IHS_LUP_023M | Mbereshi | 28.7955 | -9.7498 | Northern | 2 | LUAPULA | KAWAMBWA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Outdoor | Kennedy Mwansa | Danny Masumba | Stanley Bwalya | MTN | Flavian Mazhambi | In House | In House | CK Works | CK Works | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | n/a | N/A | 63 |  | 1 | MTN | T3144 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | NO | NO | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_023M
754 | T3249 | IHS_LUP_024M | Kawambwa Tea Company | 29.2761 | -9.7511 | Northern | 1.8 | LUAPULA | KAWAMBWA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 70 | Indoor | Kennedy Mwansa | Danny Masumba | Stanley Bwalya | MTN | Flavian Mazhambi | In House | In House | Yanmar | Yanmar | 15 | Yanmar | 0 | Mecc Alte | 0 | 600 | Delta | IPT | 250 | Amaron | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 66 |  | 1 | MTN | T3249 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_024M
1726 | T3153 | IHS_LUP_025M | Tabita | 28.7349 | -9.5747 | Northern | 1.8 | LUAPULA | NCHELENGE | No | No | No | Rural | 2G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Indoor | Kennedy Mwansa | Lazarous kupa Mutamali | Stanley Bwalya | MTN | Flavian Mazhambi | In House | In House | IMG | IMG | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 49 |  | 1 | MTN | T3153 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_025M
1399 | T3021 | IHS_LUP_026M | Nchelenge | 28.7402 | -9.341 | Northern | 2.5 | LUAPULA | NCHELENGE | No | No | No | Rural | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 48 | Indoor | Kennedy Mwansa | Danny Masumba | Stanley Bwalya | MTN | Flavian Mazhambi | In House | In House | Lamasat | Lamasat | 20 | perkins | GV51790R | Leroy Sommer | SAP 40H J6/4 | 600 | Delta | IPT | 250 | Lithium | 400 | 48 | 100 | 4 | sumsung | sumsung | 18000 | 18000 | 2 | 47 |  | 1 | MTN | T3021 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | NO | NO |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_026M
999 | T3409 | IHS_LUP_027M | MANSA EXT | 28.9015 | -11.2017 | Northern | 2 | LUAPULA | MANSA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 30 | Outdoor | Kennedy Mwansa | Peter Choongo | Emmanuel Mulayi | MTN | Flavian Mazhambi | In House | In House | Elcos | Elcos | 13 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 105 |  | 2 | MTNAirtel | T3409 | ZM6955 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_027M
22 | T3484 | IHS_LUP_028M | Bahati | 28.8504 | -14.4921 | Northern | 2 | NORTHERN | MANSA | No | No | No | Rural | 2G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 55 | Outdoor | Kennedy Mwansa | Peter Sinkala | Emmanuel Mulayi | MTN | Flavian Mazhambi | In House | In House | MPI | MPI | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | Amaron | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 70 |  | 1 | MTN | T3484 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 24 |  | still on site | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_028M
1007 | T3555 | IHS_LUP_029M | Mantapala | 28.8993 | -9.5181 | Northern | 2.5 | LUAPULA | Nchelenge | No | No | No | Rural | P4 | P4 | BTS | BTS | On air | Solar-Gen | Green Field | 70 | Outdoor | Kennedy Mwansa | Danny Masumba | Stanley Bwalya | MTN | Flavian Mazhambi | In House | In House | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | n/a | N/A | 65 |  | 2 | MTNAirtel | T3555 | ZM0340 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | NO | NO | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_029M
126 | ZM0174 | IHS_LUP_201A | Chembe | 28.7425 | -11.9478 | Northern | 2 | LUAPULA | Mansa | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Kennedy Mwansa | Peter Sinkala | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | Lamasat | Lamasat | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 98 |  | 2 | MTNAirtel | T3230 | ZM0174 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_201A
159 | ZM0176 | IHS_LUP_202A | Chienge | 29.1621 | -8.6544 | Northern | 1.8 | LUAPULA | Chiengi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Kennedy Mwansa | Lazarous kupa Mutamali | Stanley Bwalya | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 85 |  | 2 | MTNAirtel | T3222 | ZM0176 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_202A
196 | ZM0178 | IHS_LUP_203A | Chilubi Island | 29.8524 | -11.0794 | Northern | 4.5 | LUAPULA | Samfya | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 80 | Indoor | Kennedy Mwansa | Peter Choongo | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 95 |  | 2 | MTNAirtel | T3220 | ZM0178 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  | 48 |  | still on site |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_203A
678 | ZM0183 | IHS_LUP_204A | Kaputa | 29.6764 | -8.4681 | Northern | 2 | LUAPULA | Kaputa | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Kennedy Mwansa | Lazarous kupa Mutamali | Stanley Bwalya | Airtel | Flavian Mazhambi | In House | In House | Lamasat | Lamasat | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 46 |  | 1 | Airtel | 0 | ZM0183 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_204A
752 | ZM0186 | IHS_LUP_205A | Kawambwa | 29.0616 | -9.8011 | Northern | 1.8 | LUAPULA | Kawambwa | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Kennedy Mwansa | Danny Masumba | Stanley Bwalya | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 70 |  | 1 | Airtel | 0 | ZM0186 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_205A
1071 | ZM0194 | IHS_LUP_206A | Mbereshi | 28.7956 | -9.724 | Northern | 1.8 | LUAPULA | Kawambwa | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 70 | Indoor | Kennedy Mwansa | Danny Masumba | Stanley Bwalya | Airtel | Flavian Mazhambi | In House | In House | IMG | IMG | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 107 |  | 2 | AirtelTop Star | 0 | ZM0194 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | NO | NO | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_206A
1340 | ZM0199 | IHS_LUP_207A | Mwense | 28.6945 | -10.387 | Northern | 1.8 | LUAPULA | Mwense | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 70 | Indoor | Kennedy Mwansa | Peter Sinkala | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 15 | perkins | GV51794V | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 50 |  | 1 | Airtel | 0 | ZM0199 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  |  | 6 | collected still at regional office |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_207A
1400 | ZM0202 | IHS_LUP_208A | Nchelenge | 28.7434 | -9.3485 | Northern | 2.5 | LUAPULA | Nchelenge | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 80 | Indoor | Kennedy Mwansa | Danny Masumba | Stanley Bwalya | Airtel | Flavian Mazhambi | In House | In House | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 120 |  | 2 | MTNAirtel | T3556 | ZM0202 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | yes | 30 |  | Pending |  |  |  |  | IHS_LUP_208A
874 | ZM0240 | IHS_LUP_209A | Lubwe | 29.6476 | -11.1127 | Northern | 1.8 | LUAPULA | Samfya | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 50 | Outdoor | Kennedy Mwansa | Peter Choongo | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | - | N/A | 95 |  | 2 | MTNAirtel | T3253 | ZM0240 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  | 24 |  | still on site |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_209A
1273 | ZM0262 | IHS_LUP_210A | Mununga | 29.0476 | -9.0321 | Northern | 4.5 | LUAPULA | Chiengi | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 80 | Indoor | Kennedy Mwansa | Lazarous kupa Mutamali | Stanley Bwalya | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 600 | 48 | 100 | 6 | LG | LG | 18000 | 18000 | 2 | 85 |  | 3 | MTNAirtelTop Star | T3313 | ZM0262 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | NO | NO | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_210A
759 | ZM0265 | IHS_LUP_211A | Kazembe (Mwansabombwe) | 28.7666 | -9.86 | Northern | 1.8 | LUAPULA | Kawambwa | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 80 | Indoor | Kennedy Mwansa | Danny Masumba | Stanley Bwalya | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 40 |  | 1 | Airtel | 0 | ZM0265 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_211A
596 | ZM0428 | IHS_LUP_212A | Kampampi | 28.7402 | -9.4864 | Northern | 2 | LUAPULA | Nchelenge | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 50 | Outdoor | Kennedy Mwansa | Lazarous kupa Mutamali | Stanley Bwalya | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 79 |  | 2 | MTNAirtel | T3466 | ZM0428 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_212A
1098 | ZM0661 | IHS_LUP_213A | Milenge | 29.5017 | -12.4062 | Northern | 1.8 | LUAPULA | Milenge | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Kennedy Mwansa | Peter Choongo | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 20 | Yanmar | 0 | Mecc Alte | 0 | 600 | Power cube | Powercube | 80 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 124 |  | 2 | MTNAirtel | T3221 | ZM0661 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  | 64 |  | still on site |  |  | No | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_LUP_213A
1264 | ZM0738 | IHS_LUP_214A | Munchini | 28.9005 | -11.0967 | Northern | 2 | LUAPULA | Mansa | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 80 | Indoor | Kennedy Mwansa | Peter Sinkala | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 50 |  | 1 | Airtel | 0 | ZM0738 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_214A
469 | ZM0739 | IHS_LUP_215A | Kabengele | 28.9857 | -10.9041 | Northern | 2 | LUAPULA | Mansa | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 70 | Indoor | Kennedy Mwansa | Peter Sinkala | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 47 |  | 1 | Airtel | 0 | ZM0739 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_215A
322 | ZM0740 | IHS_LUP_216A | D.Chipemba (Chibalashi) | 29.2629 | -10.4363 | Northern | 2.5 | LUAPULA | Mwense | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 80 | Indoor | Kennedy Mwansa | Peter Sinkala | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 20 | perkins | GV51794V | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 43 |  | 1 | Airtel | 0 | ZM0740 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_216A
1248 | ZM0741 | IHS_LUP_217A | Mumba | 29.5886 | -10.3459 | Northern | 4.5 | LUAPULA | Luwingu | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 80 | Indoor | Kennedy Mwansa | Peter Sinkala | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | Huawei | Huawei | 18000 | 18000 | 2 | 48 |  | 1 | Airtel | 0 | ZM0741 | Yes |  | Yes | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_217A
1344 | ZM0747 | IHS_LUP_218A | Mwewa | 29.6433 | -10.9386 | Northern | 1.8 | LUAPULA | Samfya | No | No | No | Rural | Silver | Silver | BB | BTS | On air | Grid-Gen | Green Field | 80 | Outdoor | Kennedy Mwansa | Peter Choongo | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 45 |  | 1 | Airtel | 0 | ZM0747 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_218A
489 | ZM0748 | IHS_LUP_219A | Kabuta | 28.9043 | -9.1187 | Northern | 1.8 | LUAPULA | Nchelenge | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 80 | Outdoor | Kennedy Mwansa | Lazarous kupa Mutamali | Stanley Bwalya | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 55 |  | 2 | MTNAirtel | T3293 | ZM0748 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_219A
81 | ZM0840 | IHS_LUP_220A | Chakopo | 28.8829 | -11.2079 | Northern | 4.5 | LUAPULA | Mansa | Yes | No | No | Suburban | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 50 | Indoor | Kennedy Mwansa | Peter Sinkala | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 190 |  | 3 | MTNAirtelLiquid Telecom | T3375 | ZM0840 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | NO | NO | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_220A
553 | ZM1266 | IHS_LUP_221A | Kalisa | 28.9991 | -9.9667 | Northern | 1.8 | LUAPULA | Kawambwa | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 70 | Indoor | Kennedy Mwansa | Danny Masumba | Stanley Bwalya | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | BSB | 1500 | 2 | 1500 | 24 | LG | LG | 18000 | 18000 | 2 | 45 |  | 1 | Airtel | 0 | ZM1266 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  |  | 24 | collected still at regional office |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_221A
1303 | ZM3038 | IHS_LUP_222A | Mutende | 28.9003 | -11.2133 | Northern | 1.8 | LUAPULA | Mansa | No | No | No | Suburban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 40 | Indoor | Kennedy Mwansa | Peter Choongo | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 110 |  | 1 | Airtel | 0 | ZM3038 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_222A
646 | ZM3368 | IHS_LUP_223A | Kanyangala | 29.1024 | -8.8374 | Northern | 2 | LUAPULA | Chiengi | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Kennedy Mwansa | Lazarous kupa Mutamali | Stanley Bwalya | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 55 |  | 2 | MTNAirtel | TX | ZM3368 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_223A
1496 | ZM3426 | IHS_LUP_224A | Ntoto | 28.7876 | -9.2587 | Northern | 1.8 | LUAPULA | Nchelenge | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen-solar | Green Field | 60 | Indoor | Kennedy Mwansa | Lazarous kupa Mutamali | Stanley Bwalya | Airtel | Flavian Mazhambi | In House | In House | RID | RID | 15 | Mitsubishi | 0 | Zanardi | 0 | 600 | Emerson | Network Power | 192/80 | BSB | 1500 | 2 | 1500 | 24 | LG | LG | 18000 | 18000 | 2 | 77 |  | 2 | MTNAirtel | T3319 | ZM3426 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_224A
1285 | ZM3809 | IHS_LUP_225A | Musangu (KAMPALA) | 28.6497 | -10.2465 | Northern | 1.8 | LUAPULA | Mwense | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 50 | Outdoor | Kennedy Mwansa | Lazarous kupa Mutamali | Stanley Bwalya | Airtel | Flavian Mazhambi | In House | In House | IMG | IMG | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 60 |  | 2 | MTNAirtel | T3461 | ZM3809 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_225A
1005 | ZM3811 | IHS_LUP_227A | MANSA ZNS | 28.806 | -10.9161 | Northern | 2.5 | LUAPULA | Mansa | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 70 | Outdoor | Kennedy Mwansa | Peter Sinkala | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 1200 | 48 | 100 | 12 | N/A | N/A | N/A | n/a | N/A | 46 |  | 1 | Airtel | 0 | ZM3811 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_227A
648 | ZM3812 | IHS_LUP_228A | Kanyembo (Tabita) | 28.7446 | -9.6337 | Northern | 2 | LUAPULA | Nchelenge | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Outdoor | Kennedy Mwansa | Lazarous kupa Mutamali | Stanley Bwalya | Airtel | Flavian Mazhambi | In House | In House | Yanmar | Yanmar | 16 | Yanmar | Yanmar | Mecc Alte | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | n/a | N/A | 37 |  | 1 | Airtel | 0 | ZM3812 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | Pending | 16 |  | Pending |  |  |  |  | IHS_LUP_228A
221 | ZM3814 | IHS_LUP_230A | Chinyanta | 28.7064 | -10.0134 | Northern | 1.8 | LUAPULA | Mwense | No | No | No | Rural | Silver | Silver | BTS | BB/HUB | On air | Grid-Gen | Green Field | 50 | Outdoor | Kennedy Mwansa | Danny Masumba | Stanley Bwalya | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 38 |  | 1 | Airtel | 0 | ZM3814 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_230A
656 | ZM3815 | IHS_LUP_231A | Kapala | 28.6413 | -10.0802 | Northern | 1.8 | LUAPULA | Mwense | No | No | No | Rural | Silver | Silver | BTS | BB/HUB | On air | Grid-Gen | Green Field | 50 | Outdoor | Kennedy Mwansa | Danny Masumba | Stanley Bwalya | Airtel | Flavian Mazhambi | In House | In House | Lamasat | Lamasat | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 51 |  | 1 | Airtel | 0 | ZM3815 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_231A
48 | ZM3817 | IHS_LUP_232A | Bululu | 29.1499 | -10.5662 | Northern | 1.8 | LUAPULA | Mwense | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 50 | Outdoor | Kennedy Mwansa | Peter Sinkala | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 15 | perkins | 4TNE88-G1A | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 85 |  | 1 | Airtel | 0 | ZM3817 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  | 12 |  | Collected - And re-used at Kasuba |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_232A
1756 | ZM3848 | IHS_LUP_233A | Twingi | 29.6764 | -11.715 | Northern | 2 | LUAPULA | Samfya | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 70 | Outdoor | Kennedy Mwansa | Peter Choongo | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | Vitalgen | Vitalgen | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 60 |  | 2 | MTNAirtel | T3505 | ZM3848 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_233A
692 | ZM3849 | IHS_LUP_234A | Kasanka | 29.5484 | -11.9884 | Northern | 1.8 | LUAPULA | Samfya | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Kennedy Mwansa | Peter Choongo | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | 0 | 150 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 58 |  | 1 | Airtel | 0 | ZM3849 | Yes |  | Yes | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_234A
1241 | ZM3872 | IHS_LUP_235A | Mulundu | 28.6603 | -10.5229 | Northern | 1.8 | LUAPULA | Mwense | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Kennedy Mwansa | Peter Sinkala | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 49 |  | 1 | Airtel | 0 | ZM3872 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_235A
1305 | ZM3974 | IHS_LUP_236A | MUTENDE-2_RLF | 28.9491 | -11.2267 | Northern | 1.8 | LUAPULA | Mansa | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Kennedy Mwansa | Peter Choongo | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 56 |  | 1 | Airtel | 0 | ZM3974 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_236A
713 | ZM6019 | IHS_LUP_237A | Kasongole | 29.4647 | -8.9099 | Northern | 2.5 | LUAPULA | Kaputa | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen-solar | Green Field | 70 | Outdoor | Kennedy Mwansa | Lazarous kupa Mutamali | Stanley Bwalya | Airtel | Flavian Mazhambi | In House | In House | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400/80 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | n/a | N/A | 48 |  | 2 | MTNAirtel | T3498 | ZM6019 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | NO | NO |  |  | 30 | collected still at regional office |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_237A
247 | ZM6021 | IHS_LUP_238A | Chipili North | 29.1139 | -10.7063 | Northern | 1.8 | LUAPULA | Mwense | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 50 | Outdoor | Kennedy Mwansa | Peter Sinkala | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | Lamasat | Lamasat | 15 | perkins | GV51794V | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 50 |  | 2 | MTNAirtel | T3479 | ZM6021 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_238A
144 | ZM6041 | IHS_LUP_239A | Chibote Mission | 29.5333 | -9.8667 | Northern | 1.8 | LUAPULA | Kawambwa | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Kennedy Mwansa | Peter Sinkala | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | MPPT | FlexMax | 80 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | n/a | N/A | 68 |  | 1 | Airtel | T3508 | ZM6041 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_239A
716 | ZM6053 | IHS_LUP_240A | Kasuba | 29.584 | -10.7639 | Northern | 1.8 | LUAPULA | Luwingu | No | No | No | Rural | Silver | Silver | BB | BTS | On air | Solar-Gen | Green Field | 70 | Outdoor | Kennedy Mwansa | Peter Choongo | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | FlexMax | 120/80 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | n/a | N/A | 51 |  | 1 | Airtel | 0 | ZM6053 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  | 24 |  | still on site |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_240A
684 | ZM6056 | IHS_LUP_241A | Kasaba Mission | 29.7166 | -10.7473 | Northern | 1.8 | LUAPULA | Luwingu | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen-solar | Green Field | 60 | Outdoor | Kennedy Mwansa | Peter Choongo | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | Lamasat | Lamasat | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | Network Power | 120/80 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | n/a | N/A | 40 |  | 1 | Airtel | 0 | ZM6056 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_241A
128 | ZM6087 | IHS_LUP_242A | Chembe Repeater | 28.8043 | -11.7642 | Northern | 1.8 | LUAPULA | Mansa | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Kennedy Mwansa | Peter Sinkala | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | IMG | IMG | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 40 |  | 2 | MTNAirtel | T3230 | ZM6087 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_242A
1001 | ZM6089 | IHS_LUP_243A | Mansa Rp | 28.8185 | -11.4352 | Northern | 1.8 | LUAPULA | Mansa | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Kennedy Mwansa | Peter Sinkala | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 100 | 48 | 100 | 1 | N/A | N/A | N/A | n/a | N/A | 61 |  | 1 | Airtel | 0 | ZM6089 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_243A
714 | ZM6133 | IHS_LUP_244A | KASONGOLE_Museshya | 29.3829 | -8.9783 | Northern | 2.5 | LUAPULA | Kaputa | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 70 | Outdoor | Kennedy Mwansa | Lazarous kupa Mutamali | Stanley Bwalya | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | n/a | N/A | 75 |  | 2 | MTNAirtel | T3497 | ZM6133 | Yes |  | Yes | Palisade | Netco | 2022-08-05 | NO | NO |  |  |  | still on site |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_244A
1469 | ZM6134 | IHS_LUP_245A | Nkoshya | 29.2167 | -9.1333 | Northern | 2.5 | LUAPULA | Kaputa | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen-solar | Green Field | 60 | Outdoor | Kennedy Mwansa | Lazarous kupa Mutamali | Stanley Bwalya | Airtel | Flavian Mazhambi | In House | In House | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | TAL 040 F J 6s/4 | 600 | Power cube | 36 KW ICC330-HA1-C10 | 600 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | n/a | N/A | 65 |  | 2 | MTNAirtel | T3496 | ZM6134 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | NO | NO | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_245A
160 | ZM6139 | IHS_LUP_246A | Chiengi Rp(Nyamwana [Mwinilunga - Kabompo Rd]) | 29.1474 | -8.5201 | Northern | 1.8 | LUAPULA | Chiengi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Kennedy Mwansa | Lazarous kupa Mutamali | Stanley Bwalya | Airtel | Flavian Mazhambi | In House | In House | RID | RID | 20 | Mitsubishi | 0 | Zanardi | 0 | 600 | Power cube | FlexMax | 120/80 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | n/a | N/A | 65 |  | 1 | Airtel | 0 | ZM6139 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_246A
1173 | ZM6164 | IHS_LUP_247A | Mporokoso 2_1 | 29.6154 | -10.07 | Northern | 1.8 | LUAPULA | Kawambwa | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 70 | Outdoor | Kennedy Mwansa | Peter Sinkala | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | RID | RID | 15 | Mitsubishi | 0 | Zanardi | AL3/4 | 600 | MPPT | FlexMax | 80 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | n/a | N/A | 36 |  | 1 | Airtel | 0 | ZM6164 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_247A
38 | ZM6170 | IHS_LUP_248A | BHART_AIRTEL024 | 29.4853 | -11.8345 | Northern | 1.8 | LUAPULA | Milenge | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Grid-Gen | Green Field | 70 | Outdoor | Kennedy Mwansa | SBC | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | RID | RID | 15 | Mitsubishi | 0 | Zanardi | AL3/4 | 600 | MPPT | FlexMax | 80 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | n/a | N/A | 55 |  | 2 | MTNAirtel | TX | ZM6170 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_248A
1099 | ZM6199 | IHS_LUP_249A | Milenge Rp1 | 29.3975 | -12.3393 | Northern | 1.8 | LUAPULA | Milenge | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Kennedy Mwansa | Peter Choongo | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | ET | ET | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | 0 | 150 | Power safe | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 58 |  | 2 | MTNAirtel | T3525 | ZM6199 | Yes |  | Yes | Palisade | Netco | 2022-08-05 | Yes | Yes |  | 24 |  | still on site | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_249A
1100 | ZM6200 | IHS_LUP_250A | Milenge Rp2 | 29.4307 | -12.1495 | Northern | 1.8 | LUAPULA | Milenge | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Kennedy Mwansa | Peter Choongo | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | 0 | 150 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | n/a | N/A | 40 |  | 2 | MTNAirtel | TX | ZM6200 | Yes |  | Yes | Palisade | Netco | 2022-08-05 | Yes | Yes |  |  |  |  | Done |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_250A
1295 | ZM6313 | IHS_LUP_251A | Mushota [Landmark: Catholic Mission/House] | 29.3943 | -9.8152 | Northern | 2.5 | LUAPULA | Kawambwa | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen-solar | Green Field | 50 | Outdoor | Kennedy Mwansa | Danny Masumba | Stanley Bwalya | Airtel | Flavian Mazhambi | In House | In House | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | TAL 040 F J 6s/4 | 600 | Power cube | Network Power | 192/80 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | n/a | N/A | 50 |  | 2 | MTNAirtel | T3374 | ZM6313 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_LUP_251A
219 | ZM6322 | IHS_LUP_252A | Chinsanka (Kanyense Village) | 29.7937 | -11.5685 | Northern | 2.5 | LUAPULA | Samfya | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Kennedy Mwansa | Peter Choongo | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 20 | Yanmar | 0 | Mecc Alte | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | n/a | N/A | 60 |  | 2 | MTNAirtel | T3480 | ZM6322 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | NO | NO |  |  |  | still on site |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_252A
806 | ZM6383 | IHS_LUP_253A | Lengwe [7km for Kawambwa Tea Estate] | 29.3174 | -9.795 | Northern | 1.8 | LUAPULA | Kawambwa | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Grid-Gen | Green Field | 70 | Outdoor | Kennedy Mwansa | Danny Masumba | Stanley Bwalya | Airtel | Flavian Mazhambi | In House | In House | CK Works | CK Works | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Emerson | Network Power | 192 | Amaron | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 45 |  | 1 | Airtel | 0 | ZM6383 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_253A
987 | ZM6389 | IHS_LUP_256A | Mambilima Falls - Mulundu | 28.6833 | -10.6167 | Northern | 1.8 | LUAPULA | Mwense | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 50 | Outdoor | Kennedy Mwansa | Peter Sinkala | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | MPPT | FlexMax | 80 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | n/a | N/A | 45 |  | 1 | Airtel | 0 | ZM6389 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | yes | Yes |  | 24 |  | still on site | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_256A
702 | ZM6450 | IHS_LUP_257A | Kashiba Village | 28.6667 | -10.45 | Northern | 2 | LUAPULA | Mwense | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 70 | Outdoor | Kennedy Mwansa | Peter Sinkala | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | Lamasat | Lamasat | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 75 |  | 2 | MTNAirtel | T3444 | ZM6450 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_257A
1247 | ZM6572 | IHS_LUP_258A | Mumanse | 29.4362 | -11.5968 | Northern | 1.8 | LUAPULA | Milenge | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Kennedy Mwansa | Peter Choongo | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 35 |  | 1 | Airtel | 0 | ZM6572 | Yes |  | Yes | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_258A
1096 | ZM6573 | IHS_LUP_259A | Milambo (wrong Milenge2) | 29.1186 | -11.6823 | Northern | 1.8 | LUAPULA | Milenge | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Kennedy Mwansa | Peter Choongo | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | CK Works | CK Works | 20 | perkins | 0 | Zanardi | 0 | 600 | Power cube | FlexMax | 80 /120 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | n/a | N/A | 45 |  | 1 | Airtel | 0 | ZM6573 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_259A
918 | ZM0285 | IHS_LUP_260A | LUPIYA BOARDER | 29.0023 | -8.5204 | Northern | 2.5 | LUAPULA | Chiengi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 70 | Outdoor | Kennedy Mwansa | Lazarous kupa Mutamali | Stanley Bwalya | Airtel | Flavian Mazhambi | In House | In House | CK Works | CK Works | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 65 |  | 2 | MTNAirtel | T3565 | ZM0285 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_260A
1003 | ZM0167 | IHS_LUP_261A | MANSA SUGAR | 28.6694 | -11.9095 | Northern | 2.5 | LUAPULA | Chembe | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Kennedy Mwansa | Peter Sinkala | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | CK Works | CK Works | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | n/a | N/A | 76 |  | 2 | MTNAirtel | T3553 | ZM0167 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | NO | NO | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_261A
1283 | ZM0247 | IHS_LUP_262A | MUSAILA | 29.4925 | -11.3541 | Northern | 2.5 | LUAPULA | Samfya | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Kennedy Mwansa | Peter Choongo | Emmanuel Mulayi | Airtel | Flavian Mazhambi | In House | In House | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | n/a | N/A | 80 |  | 2 | MTNAirtel | T3566 | ZM0247 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | NO | NO | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_262A
703 | ZM0560 | IHS_LUP_263A | Kashikishi | 28.7429 | -9.3034 | Northern | 2.5 | NORTHERN | Nchelenge | No | No | No | Rural |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 45 | Outdoor | Kennedy Mwansa | Lazarous kupa Mutamali | Stanley Bwalya | Airtel | Flavian Mazhambi | In House | In House | Gen Logic | Gen Logic | 15 | perkins | 0 | 0 | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 65 |  | 1 | Airtel | 0 | ZM0560 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_LUP_263A
1694 | ZM1507 | IHS_LUP_264A | Spark UCZ ST. Peter | 28.8768 | -11.1872 | Northern | 2.5 | LUAPULA | Mansa | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Kennedy Mwansa | Inhouse | Inhouse | Airtel | Flavian Mazhambi | In House | In House | CK Works | CK Works | 20 | perkins |  |  |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 90 |  | 1 | Airtel | 0 | ZM1507 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | NO | NO | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_264A
1287 | ZM1508 | IHS_LUP_265A | Musenga | 28.9101 | -11.2083 | Northern | 2.5 | LUAPULA | Mansa | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Kennedy Mwansa | Inhouse | Inhouse | Airtel | Flavian Mazhambi | In House | In House | CK Works | CK Works | 20 | perkins |  |  |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 86 |  | 1 | Airtel | 0 | ZM1508 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | [8 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_265A
952 | ZM1405 | IHS_LUP_266A | Maiteneke | 28.8836 | -11.2286 | Northern | 2.5 | LUAPULA | Mansa | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Kennedy Mwansa | Inhouse | Inhouse | Airtel | Flavian Mazhambi | In House | In House | CK Works | CK Works | 20 | perkins |  |  |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 85 |  | 1 | Airtel | 0 | ZM1405 |  |  |  |  | Inala | 2022-08-05 | [8 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_LUP_266A
1852 | ZM0949 | IHS_LUP_267A | Mundubi sec sch | 29.5758 | -11.1773 | Luapula | 4.5 | Luapula | Chifunabuli | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Gen Only | Green Field | 60 | Outdoor | Kennedy Mwansa | N/A | N/A | Airtel | Flavian Mazhambi | In House | Lithandi | perkins |  | 30 | perkins |  |  |  | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_LUP_267A
1854 | ZM1555 | IHS_LUP_269A | Kawambwa Tea Estate | 28.6059 | -9.5452 | Luapula | 4.5 | Luapula | Nchelenge | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Gen Only | Green Field | 60 | Outdoor | Kennedy Mwansa | N/A | N/A | Airtel | Flavian Mazhambi | In House | Lithandi | perkins |  | 30 | perkins |  |  |  | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_LUP_269A
1849 | ZM1361 | IHS_LUP_270A | Muwanguni Sec sch | 28.8708 | -11.2768 | Luapula | 4.5 | Luapula | Mansa | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Gen Only | Green Field | 60 | Outdoor | Kennedy Mwansa | N/A | N/A | Airtel | Flavian Mazhambi | In House | Lithandi | perkins |  | 30 | perkins |  |  |  | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_LUP_270A
1847 | ZM1338 | IHS_LUP_271A | Lubunda Basic School | 28.6808 | -10.3162 | Luapula | 4.5 | Luapula | Mwense | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Gen Only | Green Field | 70 | Outdoor | Kennedy Mwansa | N/A | N/A | Airtel | Flavian Mazhambi | In House | Lithandi | perkins |  | 30 | perkins |  |  |  | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_LUP_271A
1850 | ZM1346 | IHS_LUP_272A | Munsa secondary school | 28.8608 | -9.172 | Luapula | 4.5 | Luapula | Nchelenge | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Gen Only | Green Field | 60 | Outdoor | Kennedy Mwansa | N/A | N/A | Airtel | Flavian Mazhambi | In House | Lithandi | perkins |  | 30 | perkins |  |  |  | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_LUP_272A
1848 | ZM1360 | IHS_LUP_273A | Katanshya sec sch | 29.7266 | -11.4586 | Luapula | 4.5 | Luapula | Samfya | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Gen Only | Green Field | 70 | Outdoor | Kennedy Mwansa | N/A | N/A | Airtel | Flavian Mazhambi | In House | Lithandi | perkins |  | 30 | perkins |  |  |  | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_LUP_273A
1863 | ZM0984 | IHS_LUP_274A | Chisenga Islands | -11.3477 | 29.559 | Luapula | 4.5 | Luapula | Samfya | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Solar-Gen | Green Field | 60 | Outdoor | Kennedy Mwansa | N/A | N/A | Airtel | Flavian Mazhambi | In House | Lithandi | perkins | [6 empty] | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_LUP_274A
1866 | ZM1335 | IHS_LUP_275A | Kalobwa Sec Sch | -8.9153 | 29.0649 | Luapula | 4.5 | Luapula | Chiengi | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Gen Only | Green Field |  | Outdoor | Kennedy Mwansa | SBC | SBC | Airtel | Flavian Mazhambi | In House | Lithandi | perkins | Gen Logic | 30 | perkins | [13 empty] | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_LUP_275A
1862 | ZM1341 | IHS_LUP_276A | Katele Primary school | -8.5559 | 29.0569 | Luapula | 4.5 | Luapula | Chiengi | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Kennedy Mwansa | N/A | N/A | Airtel | Flavian Mazhambi | In House | In House | [7 empty] | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_LUP_276A
1853 | ZM1404 | IHS_LUP_277A | Puta Primary school | 29.1481 | -8.6861 | Luapula | 4.5 | Luapula | Chiengi | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Kennedy Mwansa | N/A | N/A | Airtel | Flavian Mazhambi | In House | Lithandi | perkins |  | 30 |  |  |  |  | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_LUP_277A
1677 | T1001 | IHS_NRW_001M | Solwezi Main | 26.3999 | -12.1829 | Copperbelt | 4.5 | NORTH WESTERN | SOLWEZI | Yes | Yes | No | Urban | 2G 3G 4G | P1 | BTS | BB | On air | Grid-Gen | Green Field | 56 | Indoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | CK Works | CK Works | 30 | perkins | DJ83400S | Leroy Sommer | TAL-A42-C J 6S/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 240 | 212 | 4 | MTNINQLiquid TelecomSmartnet | T1001 | 0 | YES |  | YES | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | yes | 30 |  | Pending |  |  |  |  | IHS_NRW_001M
1080 | T1045 | IHS_NRW_002M | Messangera | 26.3869 | -12.1906 | Copperbelt | 2 | NORTH WESTERN | SOLWEZI | No | No | No | Suburban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | IMG | IMG | 16 | perkins | 0 | Leroy Sommer | 0 | 750 | Delta | DPS 2400B-48-5 | 250 | Power safe | 1200 | 2 | 1200 | 24 | LG | LG | 18000 | 18000 | 2 | 50.1 | 50 | 1 | MTN | T1045 | 0 | YES |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_002M
1682 | T1100 | IHS_NRW_003M | Solwezi Trades | 26.3952 | -12.1665 | Copperbelt | 2.5 | NORTH WESTERN | SOLWEZI | No | No | No | Urban | 2G 3G 4G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | Yanmar | 0 | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | n/a | N/A | 91.3 | 90 | 1 | MTN | T1100 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | yes | Yes |  |  |  |  | pending |  | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_003M
1679 | T1091 | IHS_NRW_004M | Solwezi Teachers | 26.4054 | -12.204 | Copperbelt | 2 | NORTH WESTERN | SOLWEZI | No | No | No | Urban | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Mecc Alte | 0 | 600 | Power cube | ICC330-HA1-C10 | 750 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | n/a | N/A | 110 | 110 | 2 | MTNAirtel | T1091 | ZM0290 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | yes | Yes |  | 1 |  |  | Done |  | No | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_NRW_004M
116 | T1011 | IHS_NRW_005M | Chawama Area | 26.379 | -12.1751 | Copperbelt | 2.5 | NORTH WESTERN | SOLWEZI | Yes | Yes | No | Rural | 2G 3G 4G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 42 | Indoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HA1-C10 | 750 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 101 | 100 | 2 | MTNLiquid Telecom | T1011 | 0 | YES |  | YES | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | Done | 2019-07-08 | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_005M
1681 | T1067 | IHS_NRW_006M | Solwezi Town | 26.4177 | -12.1986 | Copperbelt | 1.8 | NORTH WESTERN | SOLWEZI | No | No | No | Urban | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | Yanmar | 0 | Mecc Alte | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 115 | 115 | 2 | MTNAirtel | T1067 | ZM6782 | Yes |  | 0 | Palisade | Inala | 2022-08-05 | yes | Yes |  | 1 |  |  | Done | 2019-07-08 | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_006M
1680 | T1112 | IHS_NRW_007M | Solwezi Technical school | 26.4274 | -12.1752 | Copperbelt | 4.5 | NORTH WESTERN | SOLWEZI | Yes | Yes | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | n/a | N/A | 166.7 | 0 | 5 | MTNAirtelLiquid TelecomParatus TelecomCC Systems | T1112 | ZM6794 | Yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | yes | 30 |  | Pending |  |  |  |  | IHS_NRW_007M
768 | T1081 | IHS_NRW_008M | Kimasala | 26.3836 | -12.1557 | Copperbelt | 4.5 | NORTH WESTERN | SOLWEZI | No | No | No | Rural | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | CK Works | CK Works | 30 | perkins | DJ83400S | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HA1-C10 | 750 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | N/A | N/A | 109 | 109 | 2 | MTNAirtel | T1081 | ZM6807 | YES |  | YES | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_008M
1684 | T1087 | IHS_NRW_009M | Solwezi West (Kandemba Compound) | 26.3677 | -12.1814 | Copperbelt | 2.5 | NORTH WESTERN | SOLWEZI | No | No | No | Suburban | 2G 3G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Earth Technology | Earth technology | 20 | perkins | GU 51798V | Leroy Sommer | 0 | 400 | Power cube | EPW30-48A | 120 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 105.8 | 0 | 2 | MTNAirtel | T1087 | ZM6801 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_009M
504 | T1085 | IHS_NRW_010M | Kabwela | 26.4595 | -12.1174 | Copperbelt | 1.8 | NORTH WESTERN | SOLWEZI | No | No | No | Rural | 2G | P4 | BTS | BTS | On air | Solar-Gen | Green Field | 36 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Lamasat | Lamasat | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | EPW30-48E | N/A | ROLLS | 1410 | 4 | 1410 | 12 | N/A | N/A | N/A | n/a | N/A | 40.5 | 0 | 1 | MTN | T1085 | 0 | YES |  | YES | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_010M
769 | T1024 | IHS_NRW_011M | Kipemba Area | 26.3171 | -12.2148 | Copperbelt | 2.5 | NORTH WESTERN | SOLWEZI | No | Yes | No | Suburban | 2G 3G | P4 | BB | BB | On air | Grid-Gen | Green Field | 54 | Indoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | IMG | IMG | 20 | perkins | GV51794V | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 45.7 | 45 | 2 | MTNParatus Telecom | T1024 | 0 | Yes |  | YES | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_011M
630 | T1000 | IHS_NRW_012M | Kansanshi | 26.4107 | -12.0918 | Copperbelt | N/A | NORTH WESTERN | SOLWEZI | No | Yes | No | Suburban | 2G 3G 4G | P3 | BTS | BB | On air | Grid Only | Green Field | 54 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | In House | n/a | n/a | N/A | N/A | N/A | N/A | N/A | N/A | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 106.8 | 0 | 2 | MTNAirtel | T1000 | ZM0667 | YES |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | Done |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_012M
1329 | T1018 | IHS_NRW_013M | Mwansa Kombwe Village BB | 26.6504 | -12.214 | Copperbelt | 1.8 | NORTH WESTERN | SOLWEZI | No | Yes | No | Rural | 2G 3G | P4 | BB | BB | On air | Grid-Gen | Green Field | 66 | Indoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | IMG | IMG | 20 | perkins | GV51794V | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Power safe | 1200 | 2 | 1200 | 24 | LG | LG | 18000 | 18000 | 2 | 64.5 | 65 | 1 | MTN | T1018 | 0 | Yes |  | YES | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_013M
1016 | T1030 | IHS_NRW_014M | Mapopo | 26.5195 | -12.4087 | Copperbelt | 1.5 | NORTH WESTERN | SOLWEZI | No | No | No | Rural | 2G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Indoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | huawei | Weichai | 13 | Weichai | 0 | xingnuo | 0 | 750 | Delta | DPS 2400B-48-5 | 250 | Power safe | 1200 | 2 | 1200 | 24 | LG | LG | 18000 | 18000 | 2 | 40.1 | 40 | 2 | MTNAirtel | T1030 | ZM3775 | Yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_014M
1301 | T1049 | IHS_NRW_015M | Mutanda Research | 26.2228 | -12.4204 | Copperbelt | 2.5 | NORTH WESTERN | SOLWEZI | No | No | No | Rural | 2G 3G | P4 | BTS | HUB | On air | Grid-Gen | Green Field | 42 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | Wolong | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 54.6 | 54 | 1 | MTN | T1049 | 0 | YES |  | 0 | Palisade | Inala | 2022-08-05 | yes | Yes |  | 1 |  |  | Done | 2019-07-09 | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_015M
1697 | T1028 | IHS_NRW_016M | St Francis | 26.5051 | -12.4789 | Copperbelt | 1.8 | NORTH WESTERN | SOLWEZI | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Lamasat | Lamasat | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 60.2 | 60 | 2 | MTNAirtel | T1028 | ZM3774 | Yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_016M
588 | T1026 | IHS_NRW_017M | Kambazhia | 26.1317 | -12.4074 | Copperbelt | 1.8 | NORTH WESTERN | SOLWEZI | No | Yes | No | Rural | 2G 3G | P4 | BTS | BB | On air | Solar-Gen | Green Field | 42 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | IMG | IMG | 20 | perkins | GV51794V | Leroy Sommer | 0 | 600 | Power cube | ICC330-HA1-C10 | 750 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | n/a | N/A | 60.1 | 60 | 2 | MTNAirtel | T1026 | ZM0412 | Yes |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_017M
770 | T1039 | IHS_NRW_018M | Kipona | 26.1709 | -12.5113 | Copperbelt | 2.5 | NORTH WESTERN | SOLWEZI | No | No | No | Rural | 2G 3G | P4 | BB | BB | On air | Grid-Gen | Green Field | 60 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | Yanmar | 0 | Mecc Alte | 0 | 600 | Power cube | ICC330-HA1-C10 | 750 | Power safe | 1200 | 2 | 1200 | 24 | N/A | N/A | N/A | n/a | N/A | 108.9 | 108 | 1 | MTN | T1039 | 0 | Yes |  | 0 | Palisade | Inala | 2022-08-05 | yes | Yes |  | 1 |  |  | Done |  | Yes | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_NRW_018M
900 | T1020 | IHS_NRW_019M | Lumwana Estates | 25.9192 | -12.2664 | Copperbelt | 1.8 | NORTH WESTERN | SOLWEZI | No | No | No | Suburban | 2G 3G | P4 | BTS | BB | On air | Grid-Gen | Green Field | 80 | Indoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | IMG | IMG | 20 | perkins | GV51794V | Leroy Sommer | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 75.1 | 75 | 3 | MTNAirtelParatus Telecom | T1020 | ZM0407 | Yes |  | YES | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_019M
903 | T1061 | IHS_NRW_020M | Lumwana R1 Gate | 25.8913 | -12.3318 | Copperbelt | 2.5 | NORTH WESTERN | SOLWEZI | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 70 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Earth Technology | Earth technology | 20 | perkins | GU 51798V | Leroy Sommer | 0 | 400 | Emerson | 0 | 300 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | n/a | N/A | 75.1 | 75 | 4 | MTNAirtelLiquid TelecomTop Star | T1061 | ZM6843 | no |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_020M
1724 | T1119 | IHS_NRW_021M | T1119_KILUMBA | 26.8926 | -11.978 | Copperbelt | 2.5 | NORTH WESTERN | SOLWEZI | No | No | No | Rural | 2G 3G | P4 | BTS | BB | On air | Grid-Gen | Green Field | 60 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Emerson | 0 | N/A | ROLLS | 1410 | 4 | 1410 | 12 | N/A | N/A | N/A | n/a | N/A | 69 | 0 | 2 | MTNAirtel | T1119 | ZM0224 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_021M
902 | T1021 | IHS_NRW_022M | Lumwana Plant | 25.8419 | -12.2737 | Copperbelt | 2.5 | NORTH WESTERN | SOLWEZI | No | Yes | No | Suburban | 2G 3G 4G | P4 | BTS | BB | On air | Grid-Gen | Green Field | 70 | Indoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GV51790V | Leroy Sommer | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 115.8 | 115 | 2 | MTNParatus Telecom | T1021 | 0 | Yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_022M
1701 | T1027 | IHS_NRW_023M | St. Dorothy BB | 27.015 | -12.3201 | Copperbelt | 1.8 | NORTH WESTERN | SOLWEZI | No | Yes | No | Rural | 2G 3G | P4 | BB | BB | On air | Grid-Gen | Green Field | 70 | Indoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | Yanmar | GV51790V | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 91 | 48 | 1 | MTN | T1027 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_023M
602 | T1031 | IHS_NRW_024M | Kamuchanga | 26.016 | -12.7962 | Copperbelt | 1.8 | NORTH WESTERN | SOLWEZI | No | No | No | Rural | 2G | P4 | BB | BB | On air | Solar-Gen | Green Field | 60 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | EPW30-48A | 150 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | n/a | N/A | 45.8 | 44 | 1 | MTN | T1031 | 0 | Yes |  | YES | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_024M
905 | T1022 | IHS_NRW_025M | Lumwana Town | 25.6549 | -12.2591 | Copperbelt | 2.5 | NORTH WESTERN | SOLWEZI | No | Yes | No | Suburban | 2G 3G | P4 | BTS | BB | On air | Grid-Gen-solar | Green Field | 80 | Indoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GV51790V | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 18000 | 18000 | 2 | 98.5 | 97.5 | 1 | MTN | T1022 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_025M
1250 | T1107 | IHS_NRW_026M | Mumbezi ZNS | 25.5782 | -12.2483 | Copperbelt | 2 | NORTH WESTERN | SOLWEZI | No | Yes | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Emerson | 0 | 150 | Lithium | 500 | 48 | 100 | 5 | N/A | N/A | N/A | n/a | N/A | 60.1 | 60 | 2 | MTNAirtel | T1107 | ZM0415 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_026M
771 | T1013 | IHS_NRW_027M | Kisasa BB | 25.4969 | -12.1092 | Copperbelt | 4.5 | NORTH WESTERN | SOLWEZI | No | No | No | Rural | 2G 3G | P4 | BB | BB | On air | Grid-Gen | Green Field | 66 | Indoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 116.5 | 115 | 2 | MTNAirtel | T1013 | ZM3585 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_027M
1723 | T1103 | IHS_NRW_028M | T1103_KIPUSHI BORDER | 27.2249 | -11.7635 | Copperbelt | 2.5 | NORTH WESTERN | SOLWEZI | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C10 | 750 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 67.1 | 0 | 2 | MTNAirtel | T1103 | ZM0236 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_028M
572 | T1083 | IHS_NRW_029M | Kalumbila 1 | 25.4263 | -12.2188 | Copperbelt | 2.5 | NORTH WESTERN | SOLWEZI | No | Yes | No | Rural | 2G 3G 4G | P4 | BTS | BB | On air | Grid-Gen | Green Field | 60 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Emerson | 0 | 150 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 76.8 | 0 | 2 | MTNAirtel | T1083 | ZM6799 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_029M
574 | T1114 | IHS_NRW_030M | Kalumbila golf | 25.3895 | -12.2313 | Copperbelt | 2 | NORTH WESTERN | SOLWEZI | No | No | No | Rural | 2G 3G 4G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | IMG | IMG | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 79 | 0 | 3 | MTNAirtelLiquid Telecom | T1114 | ZM6958 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_NRW_030M
571 | T1077 | IHS_NRW_031M | Kalumbila | 25.3818 | -12.2742 | Copperbelt | 2.5 | NORTH WESTERN | SOLWEZI | No | Yes | No | Rural | 2G 3G | P4 | BTS | BB/HUB | On air | Grid-Gen | Green Field | 26 | Indoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | GHADDAR | GHADDAR | 20 | perkins | GV51790V | Leroy Sommer | 0 | 750 | Power cube | ICC330-H1-C10 | 750 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 120.1 | 120 | 2 | INQParatus Telecom | T1077 | 0 | Yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_031M
1155 | T1046 | IHS_NRW_032M | Mpembwe | 25.7824 | -13.0416 | Copperbelt | 2.5 | NORTH WESTERN | SOLWEZI | No | No | No | Rural | 2G | P4 | BB | BTS | On air | Solar-Gen | Green Field | 66 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Emerson | N/A | N/A | ROLLS | 1410 | 4 | 1410 | 12 | N/A | N/A | N/A | n/a | N/A | 50.1 | 50 | 1 | MTN | T1046 | 0 | YES |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | Done |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_032M
576 | T1122 | IHS_NRW_033M | Kalumbila Mine | 25.3079 | -12.2788 | Copperbelt | 2.5 | NORTH WESTERN | SOLWEZI | No | Yes | No | Rural | 2G 3G 4G | P3 | BTS | BB | On air | Grid-Gen | Green Field | 60 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 750 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | n/a | N/A | 101 | 0 | 4 | MTNAirtelLiquid( Former Hai)Paratus Telecom | T1122 | ZM6800 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_NRW_033M
573 | T1084 | IHS_NRW_034M | Kalumbila 2 | 25.2283 | -12.2034 | Copperbelt | 2.5 | NORTH WESTERN | SOLWEZI | No | No | No | Rural | 2G 3G | P4 | BTS | BB | On air | Solar-Gen | Green Field | 36 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 200 | Power cube | EPW30-48A | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 50.2 | 0 | 1 | MTN | T1084 | 0 | Yes |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_034M
67 | T1116 | IHS_NRW_035M | CEC Kabompo Hydro Power | 25.1654 | -12.0722 | Copperbelt | 2.5 | NORTH WESTERN | KABOMPO | No | No | No | Rural | 2G | P4 | BTS | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Emerson | 0 | 150 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | n/a | N/A | 28 | 0 | 1 | MTN | T1116 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_035M
647 | T1033 | IHS_NRW_036M | Kanyangili | 25.458 | -13.0328 | Copperbelt | 2.5 | NORTH WESTERN | MUFUMBWE | No | No | No | Rural | 2G | P4 | BB | BB | On air | Solar-Gen | Green Field | 80 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | IMG | IMG | 20 | perkins | GV51794V | Leroy Sommer | 0 | 600 | Power cube | EPW30-48A | 150 | ROLLS | 1410 | 4 | 1410 | 12 | N/A | N/A | N/A | n/a | N/A | 24 | 35 | 1 | MTN | T1033 | 0 | Yes |  | YES | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_036M
748 | T1038 | IHS_NRW_037M | Kawama Junction | 25.1096 | -13.1317 | Copperbelt | 2.5 | NORTH WESTERN | MUFUMBWE | No | No | No | Rural | 2G | P4 | BB | BB | On air | Grid-Gen-solar | Green Field | 70 | Indoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | GHADDAR | GHADDAR | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Cordex | 0 | 300 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 18000 | 18000 | 2 | 65 | 0 | 1 | MTN | T1038 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_037M
1255 | T1047 | IHS_NRW_038M | Mumfumbwe MTN | 25.0093 | -13.1389 | Copperbelt | 2 | NORTH WESTERN | MUFUMBWE | No | No | No | Rural | 2G 3G | P3 | BB | BTS | On air | Grid-Gen | Green Field | 52 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 3TNE88-G1A | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 45.8 | 45 | 2 | MTNParatus Telecom | T1047 | 0 | YES |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_038M
587 | T1025 | IHS_NRW_039M | Kamayembe MTN | 24.8412 | -13.1882 | Copperbelt | 2.5 | NORTH WESTERN | MUFUMBWE | No | No | No | Rural | 2G | P4 | BB | BB | On air | Grid-Gen-solar | Green Field | 60 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Generator City | Generator City | 20 | Yanmar | 3TNE88-G1A | Leroy Sommer | 0 | 600 | N/A | N/A | N/A | ROLLS | 1410 | 4 | 1410 | 12 | N/A | N/A | N/A | n/a | N/A | 30.4 | 0 | 1 | MTN | T1025 | 0 | Yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_039M
1346 | T1012 | IHS_NRW_040M | Mwinilunga | 24.4308 | -11.7394 | Copperbelt | 1.8 | NORTH WESTERN | MWINILUNGA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 42 | Indoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | Yanmar | 4TNV88 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 60.2 | 60 | 1 | MTN | T1012 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_040M
704 | T1035 | IHS_NRW_041M | Kashima East | 24.6034 | -13.2144 | Copperbelt | N/A | NORTH WESTERN | KABOMPO | No | No | No | Rural | 2G | P4 | BB | BB | On air | Solar-Gen | Green Field | 70 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | Power cube | ICC330-H1-C1 | 400 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | n/a | N/A | 30.6 | 30 | 1 | MTN | T1035 | 0 | Yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  | Consolidated on IHS_NRW_224A | IHS_NRW_041M
1050 | T1044 | IHS_NRW_042M | Mayinga MTN | 24.3343 | -13.4067 | Copperbelt | 2 | NORTH WESTERN | KABOMPO | No | No | No | Rural | 2G 3G | P3 | BB | BB | On air | Grid-Gen | Green Field | 80 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | Yanmar | 3TNE88-G1A | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 45.6 | 45 | 1 | MTN | T1044 | 0 | YES |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_042M
472 | T1014 | IHS_NRW_043M | Kabompo | 24.2071 | -13.5984 | Copperbelt | 1.8 | NORTH WESTERN | KABOMPO | Yes | No | No | Rural | 2G 3G | P3 | BB | BTS | On air | Grid-Gen | Green Field | 66 | Indoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | GV51794V | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | GREE | GREE | 18000 | 18000 | 2 | 50.7 | 50 | 2 | MTNLiquid Telecom | T1014 | 0 | Yes |  | YES | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_043M
473 | T1016 | IHS_NRW_044M | Kabompo MTN BB | 24.1242 | -13.5468 | Copperbelt | 2.5 | NORTH WESTERN | KABOMPO | No | No | No | Rural | 2G | P4 | BB | BB | On air | Grid-Gen | Green Field | 80 | Indoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | CDP | CDP | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | GREE | GREE | 18000 | 18000 | 2 | 30.9 | 30 | 1 | MTN | T1016 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_044M
477 | T1017 | IHS_NRW_045M | Kabulamena | 23.9119 | -13.7866 | Copperbelt | 0 | NORTH WESTERN | KABOMPO | No | No | No | Rural | 2G | P4 | BB | BTS | On air | Solar-Gen | Green Field | 70 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Power cube | EPW50-48A | 150 | ROLLS | 1410 | 4 | 1410 | 12 | N/A | N/A | N/A | n/a | N/A | 30.6 | 30 | 1 | MTN | T1017 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  | Consolidated on IHS_NRW_227A | IHS_NRW_045M
1263 | T1048 | IHS_NRW_046M | Munbeji | 23.6621 | -13.8866 | Copperbelt | 1.5 | WESTERN | MONGU | No | No | No | Rural | 2G | P4 | BB | BB | On air | Grid-Gen | Green Field | 70 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HA1-C10 | 750 | Lithium | 500 | 48 | 100 | 5 | N/A | N/A | N/A | n/a | N/A | 75 | 70 | 2 | MTNAirtel | T1048 | ZM1167 | YES |  | YES | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_046M
1795 | T1080 | IHS_NRW_047M | Zambezi Repeater | 23.3541 | -13.6777 | Copperbelt | 2.5 | NORTH WESTERN | ZAMBEZI | No | No | No | Rural | 2G | P4 | BB | HUB | On air | Solar-Gen | Green Field | 70 | Indoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | GHADDAR | GHADDAR | 20 | perkins | GV51790V | Leroy Sommer | 0 | 600 | Cordex | 0 | 320 | ROLLS | 1410 | 4 | 1410 | 12 | GREE | GREE | 18000 | 18000 | 2 | 30.5 | 30 | 1 | MTN | T1080 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_047M
1793 | T1002 | IHS_NRW_048M | Zambezi | 23.1068 | -13.5436 | Copperbelt | 2 | NORTH WESTERN | ZAMBEZI | No | No | No | Rural | 2G 3G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 70 | Indoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 3TNE88-G1A | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 45 | 0 | 2 | MTNSmartnet | T1002 | 0 | YES |  | YES | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_048M
112 | T1071 | IHS_NRW_049M | Chavuma | 22.6814 | -13.0764 | Copperbelt | 2 | NORTH WESTERN | CHAVUMA | No | No | No | Rural | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 70 | Indoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 3TNE88-G1A | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 91 | 62 | 3 | MTNAirtelTop Star | T1071 | ZM6598 | Yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_049M
619 | T3407 | IHS_NRW_050M | KANDEMBA | 26.3787 | -12.1807 | Copperbelt | 2.5 | NORTH WESTERN | SOLWEZI | No | No | No | Suburban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 30 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Ghadder | Ghadder | 20 | perkins | 0 | Leroy Sommer | 0 | 750 | Power cube | ICC330-HA1-C10 | 250 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | n/a | N/A | 112 | 0 | 2 | MTNAirtel | T3407 | ZM0513 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_050M
470 | T1126 | IHS_NRW_051M | KABITAKA | 26.4803 | -12.1876 | Copperbelt | 1.5 | NORTH WESTERN | SOLWEZI | Yes | No | No | Rural | 2G 3G 4G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | generator city | generator city | 12 | Yanmar | 0 | ALPHAGEN | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | coslight | 400 | 2 | 400 | 24 | N/A | N/A | N/A | n/a | N/A | 112.6 | 0 | 5 | MTNAirtelINQLiquid( Former Hai)Liquid Telecom | T1126 | ZM6949 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_051M
621 | T1135 | IHS_NRW_052M | Kandunda | 26.3921 | -12.1787 | Copperbelt | 2 | NORTH WESTERN | SOLWEZI | No | No | No | Urban | 2G 3G 4G | P1 | BTS | BTS | On air | Grid-Gen | Green Field | 55 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | L/P | 0 | Leroy Sommer | 0 | 750 | Delta | DPS 2400B-48-5 | 250 | coslight | 400 | 2 | 400 | 24 | N/A | N/A | N/A | n/a | N/A | 86.7 | 0 | 1 | MTN | T1135 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | yes | Yes |  | 1 |  |  | Done |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_052M
1438 | T1138 | IHS_NRW_053M | New logistics office | 25.4402 | -12.1924 | Copperbelt | 2.5 | NORTH WESTERN | SOLWEZI | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 55 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | IMG | IMG | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Emerson | 0 | 150 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 54.4 | 0 | 2 | MTNAirtel | T1138 | ZM0410 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_053M
25 | T1137 | IHS_NRW_054M | Banana Township | 25.4094 | -17.1971 | Copperbelt | 2.5 | NORTH WESTERN | SOLWEZI | Yes | No | No | Rural | 2G 3G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 55 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | IMG | IMG | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C10 | 750 | Wolong | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 116 | 0 | 3 | MTNAirtelLiquid Telecom | T1171 | ZM0409 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_054M
1563 | T1136 | IHS_NRW_055M | Roads Camp | 25.3363 | -12.2339 | Copperbelt | 2.5 | NORTH WESTERN | SOLWEZI | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Solar-Gen | Green Field | 55 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-HA1-C10 | N/A | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 75.6 | 0 | 1 | MTN | T1136 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_055M
575 | T1139 | IHS_NRW_056M | Kalumbila Main Gate | 25.5439 | -12.1733 | Copperbelt | 2.5 | NORTH WESTERN | SOLWEZI | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen-solar | Green Field | 55 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Emerson | 0 | 200 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 60.1 | 0 | 1 | MTN | T1139 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_056M
266 | T1125 | IHS_NRW_057M | Chisola Dam Tower | 25.2241 | -12.177 | Copperbelt | 2.5 | NORTH WESTERN | MWINILUNGA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | CK Works | CK Works | 13 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | EPW30-48A | 300 | NARADA | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 40.5 | 0 | 1 | MTN | T1125 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_057M
1742 | T1160 | IHS_NRW_058M | Trident College | 26.3999 | -12.145 | Copperbelt | 2.5 | NORTH WESTERN | SOLWEZI | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | EPW30-48A | 150 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 54 | 0 | 1 | MTN | T1160 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_058M
620 | T1159 | IHS_NRW_059M | Kandemba Rlf | 26.3619 | -12.1908 | Copperbelt | 2.5 | NORTH WESTERN | SOLWEZI | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | EPW30-48A | 150 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 37 | 0 | 1 | MTN | T3407 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_059M
1685 | T1165 | IHS_NRW_062M | Solwezi CBD | 26.4107 | -12.1837 | Copperbelt | 2.5 | NORTH WESTERN | SOLWEZI | No | No | No | Urban | P4 | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 40 | Outdoor | Humphrey Bwalya | SBC | SBC | MTN | Mwenya Banda | CCS | CCS | CK Works | CK Works | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 60.4 | 0 | 1 | MTN | T1165 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_062M
1675 | ZM0078 | IHS_NRW_201A | Solwezi | 26.4039 | -12.1834 | Copperbelt | 4.5 | NORTH WESTERN | Solwezi | No | No | Yes | Urban | Silver | Silver | HUB | BSC | On air | Grid-Gen | Green Field | 70 | Indoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 218.5 | 0 | 4 | AirtelINQLiquid( Former Hai)Liquid Telecom | 0 | ZM0078 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_201A
113 | ZM0179 | IHS_NRW_202A | Chavuma | 22.6947 | -13.0422 | Copperbelt | 1.8 | NORTH WESTERN | Chavuma | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | GNM | GNM | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 39 | 0 | 1 | Airtel | 0 | ZM0179 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_202A
695 | ZM0184 | IHS_NRW_203A | Kasempa | 25.8342 | -13.4601 | Copperbelt | 2.5 | NORTH WESTERN | Kasempa | No | No | No | Suburban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Lamasat | Lamasat | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 52.371 | 0 | 1 | Airtel | 0 | ZM0184 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_203A
1347 | ZM0200 | IHS_NRW_204A | Mwinilunga | 24.4267 | -11.7366 | Copperbelt | 2.5 | NORTH WESTERN | Mwinilunga | Yes | No | No | Suburban | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 50 | Indoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 74.44 | 0 | 2 | AirtelLiquid Telecom | 0 | ZM0200 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_204A
1792 | ZM0206 | IHS_NRW_205A | Zambezi | 23.1054 | -13.5431 | Copperbelt | 1.8 | NORTH WESTERN | Zambezi | No | No | No | Suburban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 54.8 | 0 | 1 | Airtel | 0 | ZM0206 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_205A
1203 | ZM0255 | IHS_NRW_206A | Mufumbwe | 25.0055 | -13.1419 | Copperbelt | 1.8 | NORTH WESTERN | Mufumbwe | No | No | No | Rural | Silver | Silver | BB | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 44.8 | 0 | 1 | Airtel | 0 | ZM0255 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_206A
471 | ZM0283 | IHS_NRW_207A | Kabompo | 24.2052 | -13.5974 | Copperbelt | 1.8 | NORTH WESTERN | Kabompo | No | No | No | Suburban | Silver | Silver | HUB | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | IMG | IMG | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | BATTERY TECH | 0 | 190 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 50.311 | 0 | 1 | Airtel | 0 | ZM0283 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_207A
1008 | ZM0497 | IHS_NRW_208A | Manyinga | 24.3349 | -13.4084 | Copperbelt | 1.8 | NORTH WESTERN | Kabompo | No | No | No | Suburban | Silver | Silver | BB | BTS | On air | Grid-Gen | Green Field | 80 | Indoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 52 | 0 | 2 | AirtelTop Star | 0 | ZM0497 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_208A
114 | ZM0587 | IHS_NRW_209A | Chavuma repeater | 23.0586 | -13.3358 | Copperbelt | 1.8 | NORTH WESTERN | Zambezi | No | No | No | Rural | Silver | Silver | BB | HUB | On air | Solar-Gen | Green Field | 80 | Indoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | GNM | GNM | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 58.2 | 0 | 2 | MTNAirtel | T1082 | ZM0587 | 0 |  | 0 | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_209A
901 | ZM0631 | IHS_NRW_210A | Lumwana Mine | 25.8798 | -12.2592 | Copperbelt | 2 | NORTH WESTERN | Solwezi | No | No | No | Rural | Silver | Silver | BB | EBU_BB | On air | Grid-Gen | Green Field | 60 | Indoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | L/P | 0 | Leroy Sommer | 0 | 750 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 90.23 | 0 | 2 | MTNAirtel | T1068 | ZM0631 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_210A
904 | ZM0690 | IHS_NRW_212A | Lumwana Repeater | 26.3172 | -12.2145 | Copperbelt | 2.5 | NORTH WESTERN | Solwezi | No | No | No | Suburban | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 50 | Indoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 65.3 | 0 | 2 | AirtelCC Systems | 0 | ZM0690 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_212A
1009 | ZM0781 | IHS_NRW_213A | Manyinga Repeater | 24.1209 | -13.5463 | Copperbelt | 2 | NORTH WESTERN | Kabompo | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 80 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Leroy Sommer | 0 | 600 | Emerson | 701 IG4 | 300 | Amaron | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 48 | 0 | 1 | Airtel | 0 | ZM0781 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_213A
278 | ZM0810 | IHS_NRW_214A | Chitokoloki | 23.2129 | -13.8327 | Copperbelt | 1.8 | NORTH WESTERN | Zambezi | No | No | No | Rural | Silver | Silver | BB | BTS | On air | Grid-Gen-solar | Green Field | 60 | Indoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 72 | 0 | 2 | MTNAirtel | T1105 | ZM0810 | 0 |  | 0 | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_214A
544 | ZM0815 | IHS_NRW_215A | Kalene Mission B | 24.2354 | -11.1886 | Copperbelt | 2 | NORTH WESTERN | Mwinilunga | No | No | No | Rural | Silver | Silver | BB | HUB | On air | Grid-Gen | Green Field | 60 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | L/P | 0 | Leroy Sommer | 0 | 750 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 60.12 | 0 | 2 | MTNAirtel | T1201 | ZM0815 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_215A
417 | ZM0817 | IHS_NRW_216A | Ikelenge | 24.277 | -11.2683 | Copperbelt | 2.5 | NORTH WESTERN | Mwinilunga | No | No | No | Rural | Silver | Silver | BB | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | L/P | 0 | Leroy Sommer | 0 | 750 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 51.723 | 0 | 2 | MTNAirtel | T1076 | ZM0817 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_NRW_216A
1683 | ZM0819 | IHS_NRW_217A | Solwezi Trades | 26.3894 | -12.1695 | Copperbelt | 2 | NORTH WESTERN | Solwezi | No | No | No | Urban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 48 | Indoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 77.5 | 0 | 1 | Airtel | 0 | ZM0819 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_217A
767 | ZM0862 | IHS_NRW_219A | Kifubwa | 26.445 | -12.1928 | Copperbelt | 2.5 | NORTH WESTERN | Solwezi | No | Yes | No | Urban | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 70 | Indoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Earth Technology | Earth Technology | 30 | perkins | 0 | Leroy Sommer | 0 | 400 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 117 | 0 | 2 | MTNAirtel | T1072 | ZM0862 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_219A
533 | ZM0882 | IHS_NRW_220A | Kakombe | 26.6509 | -12.2137 | Copperbelt | 4.5 | NORTH WESTERN | Solwezi | No | No | Yes | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 60 | Indoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 72.109 | 0 | 1 | Airtel | 0 | ZM0882 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | yes | Yes |  | 1 |  |  | Done |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_220A
316 | ZM3310 | IHS_NRW_221A | Construction camp | 25.9166 | -12.2538 | Copperbelt | 2 | NORTH WESTERN | Solwezi | Yes | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | L/P | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 111.1 | 0 | 5 | MTNAirtelLiquid( Former Hai)Liquid TelecomSmartnet | T1056 | ZM3310 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_221A
1678 | ZM3344 | IHS_NRW_222A | Solwezi Relief(Messenger) | 26.3894 | -12.1911 | Copperbelt | 1.8 | NORTH WESTERN | Solwezi | No | No | No | Suburban | Silver | Silver | HUB | BTS | On air | Grid-Gen | Green Field | 48 | Indoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | lamasat | lamasat | 15 | perkins | 0 | Leroy Sommer | 0 | 400 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 51.1 | 0 | 1 | Airtel | 0 | ZM3344 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_222A
1794 | ZM3359 | IHS_NRW_223A | Zambezi repeater | 23.3144 | -14.2193 | Copperbelt | 2.5 | NORTH WESTERN | Lukulu | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 80 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GV51794V | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | 0 | N/A | 82.7 | 82 | 2 | MTNAirtel | T1140 | ZM3359 | 0 |  | 0 | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_223A
1206 | ZM3360 | IHS_NRW_224A | Mufumbwe repeater 1 | 24.6024 | -13.2169 | Copperbelt | 4.5 | NORTH WESTERN | Mufumbwe | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 80 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Vitalgen | Vitalgen | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | 0 | N/A | 56 | 0 | 1 | Airtel | 0 | ZM3360 | 0 |  | 0 | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_224A
1207 | ZM3361 | IHS_NRW_225A | Mufumbwe repeater 2 | 24.8214 | -13.1972 | Copperbelt | 2.5 | NORTH WESTERN | Mufumbwe | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 80 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 500 | 48 | 100 | 5 | N/A | N/A | N/A | 0 | N/A | 59 | 0 | 1 | Airtel | 0 | ZM3361 | 0 |  | 0 | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_225A
474 | ZM3362 | IHS_NRW_226A | Kabompo repeater 1 | 23.674 | -13.8611 | Copperbelt | 1.8 | NORTH WESTERN | Zambezi | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen-solar | Green Field | 80 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | LEGEANT | LEGEANT | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 61.6 | 0 | 1 | Airtel | 0 | ZM3362 | 0 |  | 0 | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_226A
475 | ZM3363 | IHS_NRW_227A | Kabompo repeater 2 | 24.082 | -13.6562 | Copperbelt | 4.5 | NORTH WESTERN | Kabompo | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 80 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | CK Works | CK Works | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 500 | 48 | 100 | 5 | N/A | N/A | N/A | 0 | N/A | 55.7 | 56 | 1 | Airtel | 0 | ZM3363 | yes |  | 0 | Palisade | Netco | 2022-08-05 | Yes | Yes |  | 2 |  |  | Done |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_227A
631 | ZM3395 | IHS_NRW_228A | Kansanshi Residential | 26.4051 | -12.1156 | Copperbelt | 2 | NORTH WESTERN | Solwezi | No | No | No | Suburban | Silver | Silver | HUB | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 13 | L/P | 0 | Leroy Sommer | 0 | 750 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 113.8 | 0 | 3 | MTNAirtelLiquid( Former Hai) | T1098 | ZM3395 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_NRW_228A
1205 | ZM3404 | IHS_NRW_229A | Mufumbwe 4 (Kikonge) | 25.2399 | -13.0977 | Copperbelt | 2.5 | NORTH WESTERN | Mufumbwe | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 70 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | Zanardi | 0 | 600 | N/A | 0 | 0 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | 0 | N/A | 49 | 0 | 1 | Airtel | 0 | ZM3404 | 0 |  | 0 | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_229A
1204 | ZM3405 | IHS_NRW_230A | Mufumbwe 3 (Nyansoso) | 25.5641 | -12.9867 | Copperbelt | 2.5 | NORTH WESTERN | Mufumbwe | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 80 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 600 | 48 | 100 | 6 | N/A | N/A | N/A | 0 | N/A | 47.9 | 0 | 1 | Airtel | 0 | ZM3405 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 2 |  |  | Done |  | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_230A
1037 | ZM3406 | IHS_NRW_231A | Matembo Juntion | 26.0108 | -12.786 | Copperbelt | 2.5 | NORTH WESTERN | Solwezi | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 80 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | CK Works | CK Works | 20 | Mitsubishi | SL40 | Zanardi | 0 | 600 | out back | 0 | 0 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | 0 | N/A | 61.1 | 0 | 1 | Airtel | 0 | ZM3406 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_231A
696 | ZM3407 | IHS_NRW_232A | Kasempa Junction (Janyauke) | 25.8961 | -13.1715 | Copperbelt | 1.8 | NORTH WESTERN | Kasempa | No | No | No | Rural | Silver | Silver | BB | HUB | On air | Solar-Gen | Green Field | 70 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | CK Works | CK Works | 20 | Mitsubishi | SL40 | Zanardi | 0 | 600 | out back | 0 | 0 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | 0 | N/A | 60.1 | 0 | 1 | Airtel | 0 | ZM3407 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_232A
898 | ZM3418 | IHS_NRW_233A | Lumwana access | 25.986 | -12.3679 | Copperbelt | 2.5 | NORTH WESTERN | Solwezi | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 70 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | 4 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 750 | Lithium | 500 | 48 | 100 | 5 | N/A | N/A | N/A | 0 | N/A | 75 | 0 | 1 | Airtel | 0 | ZM3418 | yes |  | NW | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_233A
899 | ZM3427 | IHS_NRW_234A | Lumwana East Mukumbi | 25.6543 | -12.2595 | Copperbelt | 2.5 | NORTH WESTERN | Solwezi | No | No | No | Rural | Silver | Silver | BB | BTS | On air | Grid-Gen-solar | Green Field | 80 | Indoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | BATTERY TECH | 0 | 190 | BSB | 1500 | 2 | 1500 | 24 | LG | LG | 18000 | 18000 | 2 | 45.7 | 0 | 1 | Airtel | 0 | ZM3427 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_234A
1300 | ZM3428 | IHS_NRW_235A | Mutanda | 26.2368 | -12.4083 | Copperbelt | 1.8 | NORTH WESTERN | Solwezi | No | No | No | Rural | Silver | Silver | BB | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | Yanmar | 0 | Mecc Alte | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 51.7 | 0 | 2 | AirtelCC Systems | 0 | ZM3428 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_235A
1085 | ZM3508 | IHS_NRW_236A | MIKAMBO Kalilele | 26.8349 | -12.277 | Copperbelt | 1.5 | NORTH WESTERN | Solwezi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 64 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Generator City | Generator City | 12 | perkins | 0 | linz | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 43.873 | 0 | 2 | MTNAirtel | T1151 | ZM3508 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_236A
723 | ZM3836 | IHS_NRW_239A | Katandano ZNS | 26.4314 | -12.0168 | Copperbelt | 2 | NORTH WESTERN | Solwezi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 40 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | IMG | IMG | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 56.8 | 0 | 2 | MTNAirtel | T1104 | ZM3836 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_239A
476 | ZM6028 | IHS_NRW_240A | Kabulamema Mission | 24.0054 | -13.8421 | Copperbelt | 1.8 | NORTH WESTERN | Kabompo | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 35.7 | 0 | 1 | Airtel | 0 | ZM6028 | yes |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_240A
545 | ZM6029 | IHS_NRW_241A | Kalengwa Mine | 24.9928 | -13.4578 | Copperbelt | 2.5 | NORTH WESTERN | Mufumbwe | No | No | No | Rural | Silver | Silver |  | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Emerson | 0 | 150 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | 0 | N/A | 30.1 | 0 | 2 | MTNTop Star | T1143 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_241A
449 | ZM6030 | IHS_NRW_242A | Jimbe Boarder | 24.0348 | -11.1022 | Copperbelt | 1.8 | NORTH WESTERN | Mwinilunga | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen-solar | Green Field | 50 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Lamasat | Lamasat | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 55.6 | 0 | 2 | MTNAirtel | T1202 | ZM6030 | 0 |  | 0 | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_242A
755 | ZM6031 | IHS_NRW_243A | Kawanda (Manyinga) Area | 24.4845 | -13.229 | Copperbelt | 1.8 | NORTH WESTERN | Kabompo | No | No | No | Rural | Silver | Silver | BB | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 35 | 0 | 1 | Airtel | 0 | ZM6031 | yes |  | 0 | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_243A
1491 | ZM6033 | IHS_NRW_244A | NTAMBO MISSION | 24.95 | -12.3667 | Copperbelt | 2.5 | NORTH WESTERN | Mwinilunga | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Power safe | 1200 | 2 | 1200 | 24 | N/A | N/A | N/A | 0 | N/A | 60.1 | 0 | 2 | MTNAirtel | T1148 | ZM6033 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_244A
1591 | ZM6035 | IHS_NRW_245A | Samuteba | 24.6667 | -11.75 | Copperbelt | 2.5 | NORTH WESTERN | Mwinilunga | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 60 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 0 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | 0 | N/A | 88 | 0 | 2 | MTNAirtel | TX | ZM6035 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_245A
1777 | ZM6044 | IHS_NRW_246A | Watopa (Mumbeji) | 23.6307 | -14.0322 | Copperbelt | 2 | NORTH WESTERN | Zambezi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen-solar | Green Field | 50 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Generator city | Generator city | 16 | Yanmar | 3TNE88-G1A | Mecc Alte | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 35 | 0 | 1 | Airtel | 0 | ZM6044 | yes |  | 0 | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_246A
1220 | ZM6048 | IHS_NRW_247A | Mukumbi | 25.7713 | -12.0873 | Copperbelt | 2.5 | NORTH WESTERN | Solwezi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen-solar | Green Field | 70 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | perkins | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | EP50 48A | 300 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | N/A | N/A | 60.1 | 0 | 1 | MTN | T1144 | 0 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_247A
1582 | ZM6054 | IHS_NRW_249A | Sachibondo School (Sachibonda Mission) | 24.4662 | -11.5227 | Copperbelt | 2.5 | NORTH WESTERN | Mwinilunga | No | No | No | Suburban | Silver | Silver |  | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Emerson | 701 IG4 | 300 | Amaron | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 44.2 | 0 | 1 | Airtel | 0 | ZM6054 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_249A
1209 | ZM6055 | IHS_NRW_250A | Mujila | 24.7891 | -11.5208 | Copperbelt | 2.5 | NORTH WESTERN | Mwinilunga | No | No | No | Suburban | Silver | Silver | BTS | BTS | On air | Grid-Gen-solar | Green Field | 50 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | RID | RID | 20 | Mitsubishi | SL40 | Zanardi | 0 | 600 | out back | 0 | 0 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | 0 | N/A | 60.1 | 0 | 1 | Airtel | 0 | ZM6055 | 0 |  | 0 | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_250A
150 | ZM6057 | IHS_NRW_251A | Chibwika [Mwinilunga - Kabompo Rd] | 24.3017 | -12.0674 | Copperbelt | 2.5 | NORTH WESTERN | Mwinilunga | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-HA1-C10 | 750 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | 0 | N/A | 43.1 | 39 | 1 | Airtel | 0 | ZM6057 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_NRW_251A
418 | ZM6090 | IHS_NRW_252A | Ikelenge Rp1 | 24.2702 | -11.3815 | Copperbelt | 2.5 | NORTH WESTERN | Mwinilunga | No | No | No | Rural | Silver | Silver | BB | HUB | On air | Grid-Gen-solar | Green Field | 50 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 70 | 0 | 2 | MTNAirtel | T1152 | ZM6090 | 0 |  | 0 | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_252A
419 | ZM6091 | IHS_NRW_253A | Ikelenge Rpt 2 | 24.3899 | -11.6138 | Copperbelt | 2.5 | NORTH WESTERN | Mwinilunga | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 60 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | REMMY | REMMY | 15 | perkins | 0 | Leroy Sommer | 0 | 700 | Power cube | ICC330-H1-C1 | 400 | Lithium | 600 | 48 | 100 | 6 | N/A | N/A | N/A | 0 | N/A | 55 | 0 | 2 | MTNAirtel | TX | ZM6091 | 0 |  | 0 | Palisade | Netco | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_253A
739 | ZM6092 | IHS_NRW_254A | Katyola (Chimwishi) | 24.5478 | -11.7197 | Copperbelt | 1.5 | NORTH WESTERN | Mwinilunga | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen-solar | Green Field | 40 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | RID | RID | 20 | Mitsubishi | SL40 | Zanardi | 0 | 600 | out back | 0 | 0 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | 0 | N/A | 70 | 0 | 2 | MTNAirtel | T1153 | ZM6092 | 0 |  | 0 | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_NRW_254A
1046 | ZM6094 | IHS_NRW_255A | Matimba (Kalene Rp2) | 24.9739 | -11.7323 | Copperbelt | 2.5 | NORTH WESTERN | Mwinilunga | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 70 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | 0 | N/A | 60 | 0 | 2 | MTNAirtel | TX | ZM6094 | 0 |  | 0 | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_255A
906 | ZM6095 | IHS_NRW_256A | Lumwana West (Kalene Rp3) | 25.1443 | -11.8191 | Copperbelt | 1.8 | NORTH WESTERN | Mwinilunga | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 60 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Earth Technology | Earth Technology | 15 | perkins | 0 | Leroy Sommer | 0 | 400 | Power cube | ICC330-H1-C1 | 400 | Lithium | 500 | 48 | 100 | 5 | N/A | N/A | N/A | 0 | N/A | 70 | 0 | 2 | MTNAirtel | T3433 | ZM6095 | 0 |  | 0 | Palisade | Netco | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  | Consoliadted at IHS_NRW_025M Lumwana town | IHS_NRW_256A
281 | ZM6096 | IHS_NRW_257A | Chitungu (Kalene Rp4) | 25.4011 | -11.9506 | Copperbelt | 2.5 | NORTH WESTERN | Solwezi | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 70 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Vitalgen | Vitalgen | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 500 | 48 | 100 | 5 | N/A | N/A | N/A | 0 | N/A | 62.2 | 0 | 2 | MTNAirtel | T1141 | ZM6096 | 0 |  | 0 | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_257A
760 | ZM6097 | IHS_NRW_258A | Kazhiba (Kisasa Rp) | 25.4756 | -12.0682 | Copperbelt | 1.5 | NORTH WESTERN | Solwezi | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 60 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | 0 | N/A | 54.8 | 0 | 1 | Airtel | 0 | ZM6097 | 0 |  | 0 | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_258A
1010 | ZM6100 | IHS_NRW_259A | manyinga-manyinga RP | 24.3045 | -13.5093 | Copperbelt | 1.8 | NORTH WESTERN | Kabompo | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 80 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | RID | RID | 15 | Mitsubishi | SL40 | Zanardi | 0 | 600 | N/A | 0 | 0 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | 0 | N/A | 35.4 | 0 | 1 | Airtel | 0 | ZM6100 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_259A
950 | ZM6103 | IHS_NRW_260A | Maheba Refugee Camp RP | 25.8779 | -12.4982 | Copperbelt | 1.5 | NORTH WESTERN | Solwezi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Earth Technology | Earth Technology | 20 | perkins | 0 | Leroy Sommer | 0 | 400 | Power cube | ICC330-H1-C1 | 400 | Lithium | 600 | 48 | 100 | 6 | N/A | N/A | N/A | 0 | N/A | 90.2 | 0 | 2 | MTNAirtel | T1146 | ZM6103 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_260A
1602 | ZM6303 | IHS_NRW_262A | Senior Chief Musele's area | 25.3912 | -12.1424 | Copperbelt | 1.5 | NORTH WESTERN | Solwezi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen-solar | Green Field | 70 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | RID | RID | 20 | Mitsubishi | SL40 | Zanardi | 0 | 600 | out back | 0 | 0 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | 0 | N/A | 60.2 | 0 | 1 | Airtel | 0 | ZM6303 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_262A
155 | ZM6305 | IHS_NRW_263A | Chief Mumena's area | 26.1523 | -12.5471 | Copperbelt | 2.5 | NORTH WESTERN | Solwezi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 45.7 | 0 | 1 | Airtel | 0 | ZM6305 | 0 |  | 0 | Mesh | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_263A
1764 | ZM1533 | IHS_NRW_264A | Urban Extension | 26.4041 | -12.1936 | Copperbelt | 2 | NORTH WESTERN | Solwezi | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 150 | 48 | 150 | 1 | N/A | N/A | N/A | N/A | N/A | 80 |  | 2 | MTNAirtel | T1207 | ZM1533 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_NRW_264A
363 | ZM6037 | IHS_NRW_265A | Former Kalumbila Minerals | 25.3793 | -12.2739 | Copperbelt | 2.5 | NORTH WESTERN | Solwezi | No | No | No | Rural | Silver | Silver | HUB | HUB | On air | Grid-Gen | Green Field | 60 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | In House | Gen Logic | Gen Logic | 20 | perkins | 0 | Mecc Alte | 0 | 1000 | Emerson | 701 IG4 | 300 | Power safe | 1200 | 2 | 1200 | 24 |  | N/A | N/A | 0 | N/A | 97 | 0 | 2 | MTNAirtel | 0 | ZM6037 | 0 |  | 0 | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NRW_265A
1576 | ZM1194 | IHS_NRW_266A | Royal Solwezi Hotel | 26.4339 | -12.185 | Copperbelt | 2 | NORTH WESTERN | Solwezi | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 72 |  | 2 | MTNAirtel | T1205 | ZM1194 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_NRW_266A
1294 | ZM1536 | IHS_NRW_267A | Mushitala | 26.4086 | -12.1518 | Copperbelt | 2 | NORTH WESTERN | Solwezi | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 150 | 48 | 150 | 1 | N/A | N/A | N/A | N/A | N/A | 86 |  | 2 | MTNAirtel | T1204 | ZM1536 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_NRW_267A
949 | ZM1535 | IHS_NRW_268A | Magrede Extension | 26.4079 | -12.1704 | Copperbelt | 2 | NORTH WESTERN | Solwezi | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 150 | 48 | 100 | 1 | N/A | N/A | N/A | N/A | N/A | 70 |  | 2 | MTNAirtel | T1203 | ZM1535 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_NRW_268A
1676 | ZM1534 | IHS_NRW_269A | Solwezi Hospital Compound | 26.4234 | -12.1881 | Copperbelt | 2 | NORTH WESTERN | Solwezi | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Humphrey Bwalya | SBC | SBC | Airtel | Mwenya Banda | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 78 |  | 2 | MTNAirtel | T1206 | ZM1534 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_NRW_269A
687 | T3061 | IHS_NTH_001M | Kasama Town | 31.1813 | -10.2061 | Northern | 2.5 | NORTHERN | KASAMA | Yes | Yes | No | Suburban | 2G 3G | P3 | BB | BTS | On air | Grid-Gen | Green Field | 80 | Indoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | n/a | n/a | 20 | n/a | 0 |  | 0 | n/a | n/a | n/a | n/a | Agisson | 600 | 2 | 600 | 24 | Stunz | Stunz | 18000 | 18000 | 2 | 75 |  | 4 | MTNINQParatus TelecomSmartnet | T3061 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_001M
1444 | T3379 | IHS_NTH_002M | New Town Market | 31.1726 | -10.2119 | Northern | 1.8 | NORTHERN | KASAMA | Yes | No | No | Rural | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | JIUAN GENERATOR | JIUAN GENERATOR | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 178 |  | 2 | MTNLiquid Telecom | T3379 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_002M
1717 | T3226 | IHS_NTH_003M | Sumina hill | 31.2031 | -10.2177 | Northern | 1.8 | NORTHERN | KASAMA | Yes | No | No | Rural | 2G 3G | P3 | BTS | Hub | On air | Grid-Gen | Green Field | 60 | Outdoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | JIUAN GENERATOR | JIUAN GENERATOR | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | Lithium | 600 | 48 | 100 | 6 | N/A | N/A | N/A | n/a | N/A | 93 |  | 2 | MTNAirtel | T3226 | ZM6804 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_003M
269 | T3303 | IHS_NTH_004M | Chitambi | 31.167 | -10.2628 | Northern | 2.5 | NORTHERN | KASAMA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Ghadder | Ghadder | 20 | perkins | GV51790V | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 35 |  | 1 | MTN | T3303 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_004M
686 | T3217 | IHS_NTH_005M | Kasama Farm Institute | 31.2085 | -10.3066 | Northern | 1.8 | NORTHERN | KASAMA | No | Yes | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 42 | Outdoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Vitalgen | Vitalgen | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Delta | IPT | 250 | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | n/a | N/A | 97 |  | 2 | MTNAirtel | T3217 | ZM6596 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_005M
1268 | T3064 | IHS_NTH_006M | Mungwi | 31.3694 | -10.1722 | Northern | 2.5 | NORTHERN | MUNGWI | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 80 | Indoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Ghadder | Ghadder | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Delta | IPT | 250 | Amaron | 600 | 2 | 600 | 24 | LG / Sumsung | LG / Sumsung | 18000 | 18000 | 2 | 82 |  | 2 | MTNTop Star | T3064 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_006M
315 | T3063 | IHS_NTH_007M | Coffee Estates | 31.2279 | -10.0189 | Northern | 1.8 | NORTHERN | KASAMA | No | Yes | No | Rural | 2G 3G | P4 | BB | BTS | On air | Grid-Gen | Green Field | 54 | Indoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Lamasat | Lamasat | 15 | perkins | GV51790R | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 41 |  | 1 | MTN | T3063 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_007M
1466 | T3149 | IHS_NTH_008M | Nkolemfumu BB | 31.186 | -10.5796 | Northern | 4.5 | NORTHERN | KASAMA | No | Yes | No | Rural | 2G | P4 | BB | BTS | On air | Grid-Gen | Green Field | 54 | Indoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Delta | IPT | 250 | NARADA | 600 | 2 | 600 | 24 | LG / Sumsung | LG / Sumsung | 18000 | 18000 | 2 | 67 |  | 2 | MTNAirtel | T3149 | ZM3590 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  | 6 |  | collected and already in central warehouse |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_008M
983 | T3062 | IHS_NTH_009M | Malole | 31.5731 | -10.1246 | Northern | 0 | NORTHERN | MUNGWI | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 80 | Indoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Delta | IPT | 250 | Amaron | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 56 |  | 1 | MTN | T3062 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_009M
1272 | T3148 | IHS_NTH_010M | Munkonge BB | 30.7338 | -10.3084 | Northern | 0 | NORTHERN | KASAMA | No | No | No | Rural | 2G | P4 | BB | BTS | On air | Solar-Gen | Green Field | 66 | Indoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Cordex | CodexH CX RF HP48-4KW | 350 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 84 |  | 1 | MTN | T3148 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  | Consolidated on IHS_NTH_221A | IHS_NTH_010M
430 | T3082 | IHS_NTH_011M | Indu BB | 31.1804 | -9.7375 | Northern | 2 | NORTHERN | Mungwi | No | No | No | Rural | 2G | P4 | BB | BTS | On air | Grid-Gen | Green Field | 54 | Indoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 16 | Yanmar | B466 SN07 | Mecc Alte | 0 | 600 | Delta | IPT | 250 | Amaron | 600 | 2 | 600 | 24 | LG / Sumsung | LG / Sumsung | 18000 | 18000 | 2 | 37 |  | 1 | MTN | T3082 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_011M
105 | T3133 | IHS_NTH_012M | Chanda Mkulu BB | 31.1154 | -10.8444 | Northern | 2.5 | NORTHERN | KASAMA | No | Yes | No | Rural | 2G | P4 | BB | BB | On air | Grid-Gen | Green Field | 66 | Indoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Ghadder | Ghadder | 20 | perkins | 0 | Leroy Sommer | 0 | 750 | Power cube | ICC330-H1-C1 | 400 | Amaron | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 34 |  | 1 | MTN | T3133 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_012M
97 | T3132 | IHS_NTH_013M | Chambeshi | 31.0731 | -10.9636 | Northern | 1.8 | NORTHERN | KASAMA | No | Yes | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Outdoor | Francis Muwowo | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Lamasat | Lamasat | 15 | perkins | Gv51798U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Delta | IPT | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 42 |  | 1 | MTN | T3132 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_013M
1587 | T3152 | IHS_NTH_014M | Saladi BB | 30.4149 | -10.2374 | Northern | 2 | NORTHERN | LUWINGU | No | No | No | Rural | 2G | P4 | BB | BTS | On air | Grid-Gen | Green Field | 70 | Indoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | BIA | BIA | 16 | perkins | 0 | Leroy Sommer | 0 | 1000 | Delta | IPT | 250 | Amaron | 600 | 2 | 600 | 24 | LG / Sumsung | LG / Sumsung | 18000 | 18000 | 2 | 43 |  | 1 | MTN | T3152 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_014M
828 | T3142 | IHS_NTH_015M | Litoka Hill BB | 31.2265 | -9.435 | Northern | 1.8 | NORTHERN | MBALA | No | No | No | Rural | 2G | P4 | BB | BTS | On air | Grid-Gen | Green Field | 54 | Indoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Yanmar | Yanmar | 15 | Yanmar | B208/SN07 | Mecc Alte | 0 | 600 | Delta | IPT | 250 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 54 |  | 1 | MTN | T3142 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_015M
423 | T3251 | IHS_NTH_016M | Ilondola | 31.8036 | -10.7135 | Northern | 1.8 | NORTHERN | CHINSALI | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 70 | Outdoor | Francis Muwowo | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Yanmar | Yanmar | 15 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | IPT | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 36 |  | 1 | MTN | T3251 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  | 24 |  | still on site |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_016M
1156 | T3145 | IHS_NTH_017M | Mpepo BB | 31.1303 | -11.1039 | Northern | 2.5 | NORTHERN | MPIKA | No | Yes | No | Rural | 2G | P4 | BB | BTS | On air | Grid-Gen | Green Field | 66 | Indoor | Francis Muwowo | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | CK Works | CK Works | 20 | perkins | Gv51790V | Leroy Sommer | LSA 40M5 J6/4 | 750 | Cordex | CodexH CX RF HP48-4KW | 350 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 42 |  | 1 | MTN | T3145 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | Yes |  |  | yes | 30 |  | Pending |  |  |  |  | IHS_NTH_017M
215 | T3067 | IHS_NTH_018M | Chinsali | 32.0658 | -10.5525 | Northern | 2.5 | NORTHERN | CHINSALI | Yes | No | No | Rural | 2G 3G | P2 | BTS | BB | On air | Grid-Gen | Green Field | 54 | Indoor | Francis Muwowo | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Elcos | Elcos | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | Agisson | 1200 | 2 | 600 | 48 | LG / Sumsung | LG / Sumsung | 18000 | 18000 | 2 | 42 |  | 1 | MTN | T3067 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_018M
1600 | T3124 | IHS_NTH_019M | Senga hill BB | 31.3074 | -9.2473 | Northern | 2.5 | NORTHERN | MBALA | No | No | No | Rural | 2G | P4 | BB | BB | On air | Grid-Gen | Green Field | 66 | Indoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Lamasat | Lamasat | 20 | perkins | GV51790R | Leroy Sommer | LSA 40M5 J6/4 | 600 | Delta | IPT | 250 | NARADA | 1200 | 2 | 600 | 48 | LG / Sumsung | LG / Sumsung | 18000 | 18000 | 2 | 40 |  | 2 | MTNAirtel | T3124 | ZM6594 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_019M
862 | T3278 | IHS_NTH_020M | Lubansenshi | 30.1781 | -10.2211 | Northern | 2 | NORTHERN | LUWINGU | No | No | No | Rural | 2G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | ET | ET | 16 | perkins | GU 51798V | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 65 |  | 1 | MTN | T3278 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_020M
711 | T3140 | IHS_NTH_021M | Kasongo BB | 31.2423 | -11.3064 | Northern | 2.5 | NORTHERN | MPIKA | No | Yes | No | Rural | 2G | P4 | BB | BB | On air | Grid-Gen | Green Field | 66 | Indoor | Francis Muwowo | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 30 | perkins | GV51790U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Delta | IPT | 250 | Agisson | 1200 | 2 | 600 | 48 | LG / Sumsung | LG / Sumsung | 18000 | 18000 | 2 | 54 |  | 1 | MTN | T3140 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_021M
1036 | T3129 | IHS_NTH_022M | Matelo | 31.3917 | -9.0714 | Northern | 2 | NORTHERN | MBALA | No | No | No | Rural | 2G | P4 | BB | BB | On air | Grid-Gen | Green Field | 70 | Outdoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | CK Works | CK Works | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 40 |  | 1 | MTN | T3129 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_022M
1048 | T3110 | IHS_NTH_023M | Matumbo | 32.0499 | -10.9821 | Northern | 2.5 | NORTHERN | CHINSALI | No | No | No | Rural | 2G | P4 | BB | BB | On air | Grid-Gen | Green Field | 66 | Indoor | Francis Muwowo | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 54 |  | 1 | MTN | T3110 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  | 24 |  | still on site |  |  | No | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_NTH_023M
1307 | T3128 | IHS_NTH_024M | Mutipe | 31.6202 | -9.1139 | Northern | 1.8 | NORTHERN | MBALA | No | No | No | Rural | 2G 3G | P4 | BB | BB | On air | Grid-Gen | Green Field | 70 | Outdoor | Kwibisa Mbindawina | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | BIA | BIA | 15 | perkins | GV51794V | Leroy Sommer | TAL 040D J6S/4 | 600 | Delta | IPT | 250 | Power safe | 1200 | 2 | 1200 | 24 | N/A | N/A | N/A | n/a | N/A | 56 |  | 1 | MTN | T3128 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 20 |  | collected and already in central warehouse | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_024M
542 | T3096 | IHS_NTH_025M | Kalantekwe 2 BB | 31.8291 | -11.2013 | Northern | 1.8 | NORTHERN | MPIKA | No | No | No | Rural | 2G 3G | P4 | BB | BTS | On air | Grid-Gen | Green Field | 54 | Indoor | Francis Muwowo | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | JIUAN GENERATOR | JIUAN GENERATOR | 15 | perkins | GK66187R | Leroy Sommer | LSA 42.3VS2 J 6/4 | 600 | Delta | IPT | 250 | NARADA | 600 | 2 | 600 | 24 | LG / Sumsung | LG / Sumsung | 18000 | 18000 | 2 | 43 |  | 1 | MTN | T3096 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  | 46 |  | still on site |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_025M
1493 | T3150 | IHS_NTH_026M | Ntenda BB | 31.3729 | -9.0037 | Northern | 1.8 | NORTHERN | MBALA | No | No | No | Rural | 2G | P4 | BB | BTS | On air | Grid-Gen | Green Field | 70 | Indoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Yanmar | Yanmar | 15 | Yanmar | 4TNE | Mecc Alte | 0 | 600 | Delta | IPT | 250 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 52 |  | 1 | MTN | T3150 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_026M
1265 | T3116 | IHS_NTH_027M | Mundulusi | 32.4038 | -10.2729 | Northern | 4.5 | NORTHERN | ISOKA | No | No | No | Rural | 2G | P4 | BB | BB | On air | Solar-Gen | Green Field | 60 | Indoor | Kwibisa Mbindawina | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | CK Works | CK Works | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Cordex | CodexH CX RF HP48-4KW | 350 | Lithium | 200 | 48 | 100 | 2 | LG | LG | 18000 | 18000 | 2 | 78 |  | 1 | MTN | T3116 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_027M
866 | T3106 | IHS_NTH_028M | Lubu Farm BB | 32.3762 | -10.5428 | Northern | 4.5 | NORTHERN | CHINSALI | No | No | No | Rural | 2G | P4 | BB | BB | On air | Solar-Gen | Green Field | 54 | Indoor | Kwibisa Mbindawina | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 30 | perkins | GV51790V | Leroy Sommer | LSA 40MS J 6/4 | 600 | Cordex | CodexH CX RF HP48-4KW | 350 | Lithium | 200 | 48 | 100 | 2 | LG | LG | 18000 | 18000 | 2 | 74 |  | 1 | MTN | T3106 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_028M
929 | T3070 | IHS_NTH_029M | Luwingu | 29.9137 | -10.2507 | Northern | 2 | NORTHERN | LUWINGU | Yes | No | No | Rural | 2G 3G | P3 | BB | BB | On air | Grid-Gen | Green Field | 54 | Indoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | Amaron | 600 | 2 | 600 | 24 | LG / Sumsung | LG / Sumsung | 18000 | 18000 | 2 | 78 |  | 1 | MTN | T3070 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_029M
1275 | T3117 | IHS_NTH_030M | Munyezi | 31.2719 | -8.9163 | Northern | 2 | NORTHERN | MBALA | No | No | No | Rural | 2G 3G | P4 | BTS | BB | On air | Grid-Gen | Green Field | 54 | Indoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Mecc Alte | 0 | 600 | Delta | IPT | 250 | Agisson | 600 | 2 | 600 | 24 | LG / Sumsung | LG / Sumsung | 18000 | 18000 | 2 | 42 |  | 1 | MTN | T3117 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_030M
913 | T3346 | IHS_NTH_031M | Lunzua Power Station | 31.1658 | -8.9073 | Northern | 2 | NORTHERN | MPULUNGU | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Lamasat | Lamasat | 16 | perkins | GV517094U | Leroy Sommer | TAL 040 DJ 7 S/4 | 600 | Delta | IPT | 250 | C&D True | 1056 | 12 | 176 | 24 | N/A | N/A | N/A | n/a | N/A | 30 |  | 1 | MTN | T3346 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_031M
302 | T3079 | IHS_NTH_032M | Chozi | 32.2282 | -9.3875 | Northern | 2.5 | NORTHERN | NAKONDE | No | Yes | No | Rural | 2G 3G | P4 | BB | BTS | On air | Grid-Gen | Green Field | 66 | Indoor | Kwibisa Mbindawina | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | CK Works | CK Works | 20 | perkins | U 988804 C | Leroy Sommer | TAL 040 F | 1000 | Delta | IPT | 250 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 70 |  | 1 | MTN | T3079 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_032M
185 | T3058 | IHS_NTH_033M | Chileshe | 31.8808 | -9.066 | Northern | 1.8 | NORTHERN | MBALA | No | No | No | Rural | 2G 3G | P4 | BB | BB | On air | Solar-Gen | Green Field | 42 | Outdoor | Kwibisa Mbindawina | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | RID | RID | 20 | Mitsubishi | S4LZ | Zanardi | AL3/4 | 600 | MPPT | FlexMax | 80 | ROLLS | 1410 | 4 | 1460 | 12 | N/A | N/A | N/A | n/a | N/A | 89 |  | 1 | MTN | T3058 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_033M
1725 | T3252 | IHS_NTH_034M | T3252_CHABA (CHILUBI MAIN LAND | 30.0846 | -10.9795 | Northern | 2.5 | NORTHERN | CHILUBI | No | No | No | Rural | 2G | P4 | BTS | BTS | On air | Solar-Gen | Green Field | 70 | Indoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Ghadder | Ghadder | 20 | perkins | 0 | Leroy Sommer | 0 | 750 | Cordex | CodexH CX RF HP48-4KW | 350 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 66 |  | 2 | MTNAirtel | T3252 | ZM0225 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 24 |  | collected and already in central warehouse | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_034M
1172 | T3069 | IHS_NTH_035M | Mporokoso | 30.1224 | -9.3661 | Northern | 2 | NORTHERN | MPOROKOSO | No | No | No | Rural | 2G 3G | P4 | BTS | BB | On air | Grid-Gen | Green Field | 54 | Indoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Elcos | Elcos | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | NARADA | 600 | 2 | 600 | 24 | LG / Sumsung | LG / Sumsung | 18000 | 18000 | 2 | 52 |  | 1 | MTN | T3069 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 2 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_035M
618 | T3138 | IHS_NTH_036M | Kanchibya BB | 31.2923 | -11.5565 | Northern | 2.5 | NORTHERN | MPIKA | No | Yes | No | Rural | 2G | P4 | BB | BB | On air | Grid-Gen | Green Field | 54 | Indoor | Francis Muwowo | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Ghadder | Ghadder | 20 | perkins | 0 | Leroy Sommer | 0 | 750 | Cordex | CodexH CX RF HP48-4KW | 350 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 65 |  | 1 | MTN | T3138 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | Done |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_036M
530 | T3137 | IHS_NTH_037M | Kafwinbi BB | 32.5405 | -10.1752 | Northern | 1.8 | NORTHERN | ISOKA | No | No | No | Rural | 2G | P4 | BB | BB | On air | Grid-Gen | Green Field | 80 | Indoor | Kwibisa Mbindawina | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Metco | Metco | 15 | perkins | GV51798V | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 89 |  | 1 | MTN | T3137 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_037M
1065 | T3065 | IHS_NTH_038M | Mbala | 31.3784 | -8.8515 | Northern | 2.5 | NORTHERN | MBALA | No | No | No | Rural | 2G 3G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Indoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Delta | IPT | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 88 |  | 2 | MTNParatus Telecom | T3065 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_038M
541 | T3095 | IHS_NTH_039M | Kalantekwe 1 BB | 31.6266 | -11.505 | Northern | 2.5 | NORTHERN | MPIKA | No | No | No | Rural | 2G | P4 | BB | BTS | On air | Solar-Gen | Green Field | 66 | Indoor | Francis Muwowo | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 750 | Cordex | CodexH CX RF HP48-4KW | 350 | ROLLS | 1410 | 4 | 1410 | 12 | LG | LG | 18000 | 18000 | 2 | 61 |  | 1 | MTN | T3095 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_039M
435 | T3154 | IHS_NTH_040M | Isanya Coffee | 31.3289 | -8.8237 | Northern | 1.8 | NORTHERN | MBALA | No | No | No | Rural | 2G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 66 | Outdoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Lamasat | Lamasat | 15 | perkins | GV51790R | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 64 |  | 2 | MTNAirtel | T3154 | ZM3731 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_040M
1177 | T3018 | IHS_NTH_041M | Mpulungu | 31.1119 | -8.7638 | Northern | 2 | NORTHERN | MPULUNGU | Yes | No | No | Rural | 2G 3G | P1 | BTS | Hub | On air | Grid-Gen | Green Field | 50 | Indoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | CK Works | CK Works | 15 | perkins | GV 51794U | Leroy Sommer | ECP-3-5L/4 | 600 | Delta | IPT | 250 | Amaron | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 109 |  | 1 | MTN | T3018 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 24 |  | collected and already in central warehouse | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_041M
681 | T3101 | IHS_NTH_043M | Kapwila BB | 32.48 | -9.3081 | Northern | 1.8 | NORTHERN | NAKONDE | No | Yes | No | Rural | 2G 3G | P4 | BB | BB | On air | Grid-Gen | Green Field | 54 | Indoor | Kwibisa Mbindawina | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 15 | Yanmar | 0 | Mecc Alte | 0 | 600 | Delta | IPT | 250 | Lithium | 200 | 48 | 100 | 2 | LG | LG | 18000 | 18000 | 2 | 89 |  | 2 | MTNAirtel | T3101 | ZM0460 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_NTH_043M
1249 | T3147 | IHS_NTH_044M | Mumba BB | 29.5881 | -10.3456 | Northern | 2.5 | NORTHERN | Luwingu | No | No | No | Rural | 2G | P4 | BB | BTS | On air | Solar-Gen | Green Field | 70 | Indoor | Kennedy Mwansa | Peter Sinkala | Emmanuel Mulayi | MTN | Flavian Mazhambi | GNM | Lithandi | Ghadder | Ghadder | 20 | perkins | 0 | Leroy Sommer | 0 | 750 | Cordex | CodexH CX RF HP48-4KW | 350 | ROLLS | 1410 | 4 | 1460 | 12 | LG | LG | 18000 | 18000 | 2 | 61 |  | 1 | MTN | T3147 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | No |  | 2 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_044M
1486 | T3122 | IHS_NTH_045M | Nsansamwenji BB | 32.7508 | -9.832 | Northern | 2.5 | NORTHERN | NAKONDE | No | No | No | Rural | 2G | P4 | BB | BB | On air | Grid-Gen-solar | Green Field | 70 | Indoor | Kwibisa Mbindawina | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Ghadder | Ghadder | 20 | perkins | GV51790V | Leroy Sommer | LSA 40M5 J 6/4 | 750 | Cordex | CodexH CX RF HP48-4KW | 350 | Lithium | 200 | 48 | 100 | 2 | LG | LG | 18000 | 18000 | 2 | 114 |  | 1 | MTN | T3122 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 12 |  | collected and already in central warehouse | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_045M
421 | T3081 | IHS_NTH_046M | Ilonda | 32.6791 | -9.5557 | Northern | 0 | NORTHERN | NAKONDE | No | No | No | Rural | 2G 3G | P4 | BB | BTS | On air | Solar-Gen | Green Field | 54 | Indoor | Kwibisa Mbindawina | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Cordex | CodexH CX RF HP48-4KW | 350 | Lithium | 200 | 48 | 100 | 2 | LG | LG | 18000 | 18000 | 2 | 72 |  | 1 | MTN | T3081 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 12 |  | access challenge | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  | Consolidated IHS_NTH_211A ILONDA | IHS_NTH_046M
1162 | T3216 | IHS_NTH_047M | Mpika Malambwa School | 31.3771 | -11.83 | Northern | 1.8 | NORTHERN | MPIKA | No | Yes | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Francis Muwowo | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 15 | perkins | GU51794U | Leroy Sommer | 63052RSC3. | 600 | Delta | IPT | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 72 |  | 1 | MTN | T3216 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_047M
1163 | T3312 | IHS_NTH_048M | Mpika Tazara | 31.4056 | -11.8454 | Northern | 2 | NORTHERN | MPIKA | Yes | No | No | Rural | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Francis Muwowo | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | CK Works | CK Works | 16 | perkins | 0 | Leroy Sommer | 0 | 1000 | Delta | IPT | 250 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 39 |  | 2 | MTNLiquid Telecom | T3312 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_048M
1160 | T3016 | IHS_NTH_049M | Mpika | 31.467 | -11.8443 | Northern | 2 | NORTHERN | MPIKA | No | Yes | No | Rural | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Indoor | Francis Muwowo | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 74 |  | 1 | MTN | T3016 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_049M
1342 | T3315 | IHS_NTH_050M | Mwenzo ( Nakonde) | 32.673 | -9.3338 | Northern | 1.8 | NORTHERN | NAKONDE | No | Yes | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Kwibisa Mbindawina | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 15 | perkins | GV51794V | Leroy Sommer | LSA 42.3VS2 J6/4 | 600 | Delta | IPT | 250 | Wolong | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 47 |  | 1 | MTN | T3315 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_050M
1488 | T3250 | IHS_NTH_051M | Nsumbu | 30.6464 | -8.551 | Northern | 1.8 | NORTHERN | KAPUTA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Yanmar | Yanmar | 15 | Yanmar | B208/SN07 | Mecc Alte | 0 | 600 | Delta | IPT | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 32 |  | 1 | MTN | T3250 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  | 24 |  | collected and already in central warehouse |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_051M
1360 | T3316 | IHS_NTH_052M | Nakonde ZRA Dryport | 32.7035 | -9.358 | Northern | 1.8 | NORTHERN | NAKONDE | No | Yes | No | Rural | 2G 3G | P4 | BTS | Hub | On air | Grid-Gen | Green Field | 60 | Outdoor | Kwibisa Mbindawina | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 15 | perkins | GV51794V | Leroy Sommer | TAL 040D J6S/4 | 600 | Delta | IPT | 250 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 48 |  | 1 | MTN | T3316 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 10 |  | collected and already in central warehouse | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_052M
1357 | T3382 | IHS_NTH_053M | Nakonde Mukoma | 32.753 | -9.3371 | Northern | 2 | NORTHERN | NAKONDE | Yes | Yes | No | Rural | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Kwibisa Mbindawina | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Waichei | Waichei | 20 | Weichai | 0 | linz | 0 | 600 | Delta | IPT | 250 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 67 |  | 1 | MTN | T3382 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  | 18 |  | collected and already in central warehouse |  |  | No | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_NTH_053M
1355 | T3020 | IHS_NTH_054M | Nakonde | 32.7621 | -9.3227 | Northern | 2.5 | NORTHERN | NAKONDE | Yes | Yes | No | Rural | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 48 | Indoor | Kwibisa Mbindawina | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 147 |  | 1 | MTN | T3020 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_054M
195 | T3066 | IHS_NTH_055M | Chilonga | 31.3368 | -12.034 | Northern | 2.5 | NORTHERN | MPIKA | No | Yes | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Francis Muwowo | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Delta | IPT | 250 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 65 |  | 2 | MTNAirtel | T3066 | ZM3249 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_055M
1175 | T3112 | IHS_NTH_056M | Mpula Mukasenga BB | 31.1612 | -12.1991 | Northern | s | Central | SERENJE | No | Yes | No | Rural | 2G | P4 | BB | BB | On air | Solar-Gen | Green Field | 66 | Indoor | Francis Muwowo | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Vitalgen | Vitalgen | 30 | perkins | GV5190v | Leroy Sommer | LSA 40M5 J6/4 | 750 | Delta | codex | 250 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 64 |  | 1 | MTN | T3112 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_056M
563 | T3097 | IHS_NTH_057M | Kalonje BB | 31.0801 | -12.4179 | Northern | 0 | NORTHERN | MPIKA | No | Yes | No | Rural | 2G | P4 | BB | BB | On air | Solar-Gen | Green Field | 66 | Indoor | Francis Muwowo | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Cordex | CodexH CX RF HP48-4KW | 350 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 82 |  | 2 | MTNLiquid Telecom | T3097 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | NO | NO | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  | Consolidated on IHS_NTH_239A Kalonje | IHS_NTH_057M
679 | T3078 | IHS_NTH_058M | Kaputa | 29.6651 | -8.4762 | Northern | 2 | NORTHERN | KAPUTA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Indoor | Kennedy Mwansa | Lazarous kupa Mutamali | Stanley Bwalya | MTN | Flavian Mazhambi | GNM | Lithandi | GL | Lamasat | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | Power safe | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 40 |  | 1 | MTN | T3078 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  | 14 | collected still at regional office | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_058M
564 | T3098 | IHS_NTH_059M | Kalonje Pump BB | 31.0056 | -12.6091 | Northern | 2 | NORTHERN | MPIKA | No | Yes | No | Rural | 2G | P4 | BB | BB | On air | Grid-Gen | Green Field | 66 | Indoor | Francis Muwowo | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Mecc Alte | 0 | 600 | Delta | IPT | 250 | Agisson | 1200 | 2 | 600 | 48 | LG / Sumsung | LG / Sumsung | 18000 | 18000 | 2 | 72 |  | 2 | MTNLiquid( Former Hai) | T3098 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_059M
1297 | T3118 | IHS_NTH_060M | Muso BB | 30.9342 | -12.759 | Northern | 2 | Central | SERENJE | No | Yes | No | Rural | 2G | P4 | BB | BB | On air | Grid-Gen | Green Field | 66 | Indoor | Francis Muwowo | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | CK Works | CK Works | 16 | Yanmar | 729619-51310 | Mecc Alte | Lsc2852 | 600 | Delta | IPT | 250 | Lithium | 100 | 48 | 100 | 1 | LG | LG | 18000 | 18000 | 2 | 52 |  | 1 | MTN | T3118 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_060M
1687 | T2017 | IHS_NTH_061M | South Luangwa | 31.6198 | -13.1194 | Eastern | 4.5 | EASTERN | LUANGWA | No | No | No | Rural | 2G 3G | P4 | BB | BB | On air | Solar-Gen | Green Field | 42 | Outdoor | Fetus Kalunga | SBC | SBC | MTN | Fetus Kalunga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 0 | Mecc Alte | 0 | 600 | Emerson | EPC48200/2900-HC1 | 250 | Lithium | 800 | 48 | 100 | 8 |  | 0 | N/A |  | 0 | 100 |  | 2 | MTNAirtel | T2017 | ZM3781 | yes |  | not working | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | Done |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_061M
710 | T3470 | IHS_NTH_062M | Kasonde Chisuna | 30.5835 | -10.2392 | Northern | 1.8 | NORTHERN | KASAMA | No | No | No | Rural | 2G | P4 | BTS | BTS | On air | Solar-Gen | Green Field | 55 | Outdoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | RID | RID | 15 | Mitsubishi | S4LZ | Zanardi | AL3/4 | 200 | MPPT | FlexMax | 80 | ROLLS | 1410 | 4 | 1460 | 12 | N/A | N/A | N/A | n/a | N/A | 22 |  | 1 | MTN | T3470 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_062M
1101 | T3471 | IHS_NTH_063M | Milengi Primary | 31.1381 | -10.1907 | Northern | 2.5 | NORTHERN | KASAMA | No | No | No | Rural | 2G | P4 | BTS | BTS | On air | Solar-Gen | Green Field | 55 | Outdoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | Leray Somer | Zanardi | AL3/4 | 200 | MPPT | FlexMax | 80 | ROLLS | 1410 | 4 | 1460 | 12 | N/A | N/A | N/A | n/a | N/A | 56 |  | 1 | MTN | T3471 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_063M
217 | T3481 | IHS_NTH_064M | Chinsali Turn OFF | 32.1513 | -10.6311 | Northern | 1.8 | NORTHERN | CHINSALI | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 55 | Outdoor | Francis Muwowo | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | CK Works | CK Works | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 83 |  | 2 | MTNLiquid( Former Hai) | T3481 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_064M
954 | T3467 | IHS_NTH_065M | Makasa | 31.8719 | -9.674 | Northern | 1.8 | NORTHERN | MUNGWI | No | No | No | Rural | 2G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 55 | Outdoor | Kwibisa Mbindawina | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 73 |  | 2 | MTNAirtel | T3467 | ZM1166 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_065M
437 | T3477 | IHS_NTH_066M | Isoka Turn OFF | 32.6683 | -10.1554 | Northern | 1.8 | NORTHERN | ISOKA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 55 | Outdoor | Kwibisa Mbindawina | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | MPI | MPI | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 104 |  | 2 | MTNAirtel | T3477 | ZM1132 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_066M
267 | T3490 | IHS_NTH_068M | Chisowa | 31.4586 | -11.8175 | Northern | 2 | NORTHERN | MPIKA | No | No | No | Rural | 2G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 55 | Outdoor | Francis Muwowo | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | Lamasat | Lamasat | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 35 |  | 1 | MTN | T3490 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_068M
1808 | T3456 | IHS_NTH_069M | Zombe | 31.4333 | -8.7333 | Northern | 2 | NORTHERN | MBALA | No | No | No | Rural | 2G | P4 | BTS | BTS | On air | Solar-Gen | Green Field | 55 | Outdoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | RID | RID | 16 | Mitsubishi | S4LZ | Zanardi | AL3/4 | 200 | MPPT | FlexMax | 80 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | n/a | N/A | 29 |  | 1 | MTN | T3456 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_069M
1217 | T3464 | IHS_NTH_070M | Mukosa | 31.5574 | -10.1808 | Northern | 2 | NORTHERN | MUNGWI | No | No | No | Rural | 2G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 75 | Outdoor | Samson Nyirenda | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | MPI | MPI | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | MPPT | FlexMax | 80 | ROLLS | 1410 | 4 | 1460 | 12 | N/A | N/A | N/A | n/a | N/A | 58 |  | 1 | MTN | T3464 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_070M
1797 | T3489 | IHS_NTH_071M | Zampalm | 30.6999 | -11.6724 | Northern | 2 | NORTHERN | MPIKA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Solar-Gen | Green Field | 55 | Outdoor | Francis Muwowo | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | RID | RID | 16 | Mitsubishi | S4LZ | Zanardi | AL3/4 | 200 | MPPT | FlexMax | 80 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | n/a | N/A | 25 |  | 2 | MTNINQ | T3489 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_071M
1429 | T3557 | IHS_NTH_072M | New chinsali cbd | 32.0896 | -10.5724 | Northern | 2.5 | NORTHERN | Chinsali | Yes | No | No | Suburban | P4 | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Francis Muwowo | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | CK Works | CK Works | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 100 | 48 | 100 | 1 | N/A | N/A | N/A | n/a | N/A | 69 |  | 1 | MTN | T3557 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_072M
1566 | T3560 | IHS_NTH_073M | Robert makasa un | 32.2213 | -10.6054 | Northern | 2.5 | NORTHERN | Chinsali | No | No | No | Urban | P4 | P4 | BTS | BTS | On air | Grid-Gen | Roof Top | 25 | Outdoor | Kwibisa Mbindawina | SBC | SBC | MTN | Flavian Mazhambi | GNM | Lithandi | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 89 |  | 1 | MTN | T3560 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_073M
1066 | ZM0124 | IHS_NTH_201A | MBALA | 31.3696 | -8.8482 | Northern | 2 | NORTHERN | Mpulungu | Yes | No | No | Rural | Silver | Silver | HUB | HUB | On air | Grid-Gen | Green Field | 60 | Indoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG / Sumsung | LG / Sumsung | 18000 | 18000 | 2 | 91 |  | 1 | Airtel | 0 | ZM0124 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_201A
1178 | ZM0128 | IHS_NTH_202A | MPULUNGU | 31.1124 | -8.7641 | Northern | 2.5 | NORTHERN | Mpulungu | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 70 | Indoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | GV51790V | Leroy Sommer | ECP -28-M/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG / Sumsung | LG / Sumsung | 18000 | 18000 | 2 | 47 |  | 2 | AirtelTop Star | 0 | ZM0128 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_202A
1356 | ZM0130 | IHS_NTH_203A | NAKONDE | 32.7623 | -9.3214 | Northern | 4.5 | NORTHERN | Nakonde | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 60 | Indoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Vitalgen | Vitalgen | 30 | perkins | 1103A33G | Leroy Sommer | LSAP423F | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | Sumsung | Sumsung | 18000 | 18000 | 2 | 220 |  | 2 | MTNAirtel | T3447 | ZM0130 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  | 32 |  | collected and already in central warehouse |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_203A
216 | ZM0177 | IHS_NTH_204A | CHINSALI | 32.0609 | -10.5427 | Northern | 4.5 | NORTHERN | Chinsali | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 50 | Indoor | Francis Muwowo | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 1103A-33 | Leroy Sommer | ECP28VL4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | Sumsung | Sumsung | 18000 | 18000 | 2 | 64 |  | 1 | Airtel | 0 | ZM0177 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_204A
436 | ZM0180 | IHS_NTH_205A | ISOKA | 32.6454 | -10.181 | Northern | 2 | NORTHERN | Isoka | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG / Sumsung | LG / Sumsung | 18000 | 18000 | 2 | 140 |  | 3 | MTNAirtelISO FM | T3068 | ZM0180 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_205A
930 | ZM0192 | IHS_NTH_206A | LUWINGU | 29.924 | -10.2628 | Northern | 4.5 | NORTHERN | Luwingu | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 50 | Indoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 30 | perkins | GL-PM-2-1-M1000-30-7320 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 85 |  | 1 | Airtel | 0 | ZM0192 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_206A
1161 | ZM0195 | IHS_NTH_207A | MPIKA | 31.4088 | -11.8395 | Northern | 4.5 | NORTHERN | Mpika | Yes | No | Yes | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 60 | Indoor | Francis Muwowo | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 30 | perkins | GLPM-2.1M-1000-30-3P-7320 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 120 |  | 1 | Airtel | 0 | ZM0195 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_207A
429 | ZM0221 | IHS_NTH_208A | INDU | 31.1802 | -9.7371 | Northern | 1.8 | NORTHERN | Mungwi | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 60 | Indoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Lamasat | Lamasat | 15 | perkins | GU51794U | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 63 |  | 1 | Airtel | 0 | ZM0221 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_208A
1269 | ZM0251 | IHS_NTH_209A | MUNGWI | 31.3697 | -10.1739 | Northern | 1.8 | NORTHERN | Mungwi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Lamasat | Lamasat | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Emerson | Network Power | 192 | Amaron | 600 | 2 | 600 | 24 | LG / Sumsung | LG / Sumsung | 18000 | 18000 | 2 | 79 |  | 1 | Airtel | 0 | ZM0251 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_209A
1599 | ZM0276 | IHS_NTH_210A | SENGA HILL | 31.2469 | -9.3589 | Northern | 1.8 | NORTHERN | Mpulungu | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 70 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Lamasat | Lamasat | 15 | perkins | GU51794U | Leroy Sommer | LSA 40M5 J6/4 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 54 |  | 2 | AirtelTop Star | 0 | ZM0276 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_210A
422 | ZM0455 | IHS_NTH_211A | ILONDA NEW | 32.6797 | -9.5565 | Northern | 4.5 | NORTHERN | Nakonde | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 80 | Indoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | CK Works | CK Works | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | Huawei | Huawei | 18000 | 18000 | 2 | 146 |  | 1 | Airtel | 0 | ZM0455 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | NO | NO |  |  |  |  | pending |  | No | No | Yes |  |  | yes | 30 |  | Pending |  |  |  |  | IHS_NTH_211A
303 | ZM0463 | IHS_NTH_213A | CHOZI | 32.2311 | -9.3936 | Northern | 2 | NORTHERN | Mbala | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 80 | Indoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Lamasat | Lamasat | 16 | perkins | 580112A | Leroy Sommer | TAL 040D J6S/4 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 103 |  | 1 | Airtel | 0 | ZM0463 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_213A
1487 | ZM0467 | IHS_NTH_214A | NSELUKA | 31.2546 | -9.9343 | Northern | 2.5 | NORTHERN | Mungwi | No | Yes | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 62 | Indoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Lamasat | Lamasat | 20 | perkins | GU51790R | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 140 |  | 2 | MTNAirtel | T3318 | ZM0467 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_214A
617 | ZM0655 | IHS_NTH_215A | KANCHIBIYA | 31.2959 | -11.5487 | Northern | 1.8 | NORTHERN | Mpika | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 80 | Indoor | Francis Muwowo | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | IMG | IMG | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 100 | 48 | 100 | 1 | LG | LG | 18000 | 18000 | 2 | 44 |  | 1 | Airtel | 0 | ZM0655 | Yes |  | Yes | Palisade | Netco | 2022-08-05 | NO | NO |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_215A
984 | ZM0691 | IHS_NTH_216A | MALOLE | 31.5708 | -10.1256 | Northern | 2 | NORTHERN | Mungwi | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 60 | Indoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | Sumsung | Sumsung | 18000 | 18000 | 2 | 55 |  | 1 | Airtel | 0 | ZM0691 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_216A
1477 | ZM0730 | IHS_NTH_217A | NONDO | 31.208 | -9.5294 | Northern | 1.8 | NORTHERN | Mbala | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 60 | Indoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | BIA | BIA | 15 | perkins | GU51784U | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG / Sumsung | LG / Sumsung | 18000 | 18000 | 2 | 67 |  | 2 | MTNAirtel | T3460 | ZM0730 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_217A
199 | ZM0731 | IHS_NTH_218A | CHIMBA "A" | 31.5368 | -9.8924 | Northern | 2.5 | NORTHERN | Mungwi | No | Yes | No | Rural | Silver | Silver | BB | BTS | On air | Solar-Gen | Green Field | 60 | Indoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Emerson | Network Power | 192/80 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 72 |  | 2 | MTNAirtel | T3284 | ZM0731 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | Done |  | Yes | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_NTH_218A
1049 | ZM0733 | IHS_NTH_219A | MATUMBO | 32.0506 | -10.9806 | Northern | 4.5 | NORTHERN | Chinsali | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 80 | Indoor | Francis Muwowo | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 30 | perkins | 2490/1500 | Leroy Sommer | ECP 28-VL/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 54 |  | 1 | Airtel | 0 | ZM0733 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_219A
979 | ZM0742 | IHS_NTH_220A | MALATA | 30.4017 | -10.235 | Northern | 1.8 | NORTHERN | Mporokoso | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 70 | Indoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Lamasat | Lamasat | 15 | perkins | GU51795U | Leroy Sommer | 63052RSC3. | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG / Sumsung | LG / Sumsung | 18000 | 18000 | 2 | 50 |  | 1 | Airtel | 0 | ZM0742 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_220A
1271 | ZM0744 | IHS_NTH_221A | MUNKONGE | 30.7335 | -10.3081 | Northern | 4.5 | NORTHERN | Kasama | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 80 | Indoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 45 |  | 1 | Airtel | 0 | ZM0744 | Yes |  | Yes | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_221A
698 | ZM0745 | IHS_NTH_222A | KASENGA | 30.8674 | -10.0461 | Northern | 2 | NORTHERN | Kasama | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 80 | Indoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 16 | perkins | GV51790V | Leroy Sommer | ECP -28-M/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 50 |  | 1 | Airtel | 0 | ZM0745 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_222A
1067 | ZM0755 | IHS_NTH_223A | MBALA NAKONDE JUNCTION | 31.3735 | -9.0034 | Northern | 1.8 | NORTHERN | Mbala | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 80 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Lamasat | Lamasat | 15 | perkins | 530177A | Leroy Sommer | TAL 040 DJ 6 S/4 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 69 |  | 1 | Airtel | 0 | ZM0755 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_223A
1574 | ZM0756 | IHS_NTH_224A | ROSA MISSION | 31.3633 | -9.6325 | Northern | 1.8 | NORTHERN | Mungwi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 70 | Indoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | RID | RID | 15 | Mitsubishi | Mitsubishi S4L2 | Zanardi | AL 3/4 | 600 | MPPT | FlexMax | 80 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 48 |  | 1 | Airtel | 0 | ZM0756 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | NO | NO |  |  |  | collected and already in central warehouse |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_224A
756 | ZM0757 | IHS_NTH_225A | KAYAMBI | 31.9967 | -9.4569 | Northern | 2 | NORTHERN | Mungwi | No | Yes | No | Rural | Silver | Silver | HUB | BTS | On air | Grid-Gen | Green Field | 80 | Indoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 94 |  | 2 | MTNAirtel | T3254 | ZM0757 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_225A
1592 | ZM0759 | IHS_NTH_226A | SANSAMWENJE | 32.7571 | -9.8187 | Northern | 2.5 | NORTHERN | Isoka | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen-solar | Green Field | 60 | Indoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | CK Works | CK Works | 20 | perkins | Gv51790V | Leroy Sommer | LSA 40M5 J6/4 | 600 | Power cube | FlexMax | 400 | Lithium | 1500 | 48 | 100 | 15 | LG | LG | 18000 | 18000 | 2 | 89 |  | 1 | Airtel | 0 | ZM0759 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_226A
277 | ZM0838 | IHS_NTH_227A | CHITO "A" (Mununga Repeater) | 30.7799 | -12.8528 | Northern | 2.5 | NORTHERN | Mpika | No | No | No | Rural | Silver | Silver | BB | BTS | On air | Solar-Gen | Green Field | 60 | Indoor | Francis Muwowo | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Perkins | Lamasat | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400/80 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 75 |  | 2 | MTNAirtel | T3526 | ZM0838 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | NO | NO |  |  |  | still on site |  |  | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_227A
1274 | ZM0839 | IHS_NTH_228A | MUNUNGA QUARRY | 31.0124 | -12.6618 | Northern | 1.8 | NORTHERN | Mpika | No | No | No | Rural | Silver | Silver | BB | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Francis Muwowo | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Lamasat | Lamasat | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 150 |  | 1 | Airtel | 0 | ZM0839 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_228A
1739 | ZM0841 | IHS_NTH_229A | THENDERE RPT 'A" | 33.2028 | -10.2905 | Northern | 2.5 | NORTHERN | Isoka | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Solar-Gen | Green Field | 80 | Indoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Emerson | Network Power | 80 | BSB | 1500 | 2 | 1500 | 24 | LG | LG | 18000 | 18000 | 2 | 90 |  | 2 | MTNAirtel | TX | ZM0841 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  | 24 |  | access challenge |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_229A
1738 | ZM0842 | IHS_NTH_230A | THENDERE "A" | 33.34 | -10.27 | Northern | 1.8 | NORTHERN | Isoka | No | No | No | Rural | Silver | Silver | HUB | BB | On air | Solar-Gen | Green Field | 80 | Outdoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Vitalgen | Vitalgen | 15 | perkins | Gv51790u | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Emerson | Network Power | 192/80 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | n/a | N/A | 114 |  | 2 | MTNAirtel | T3476 | ZM0842 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  | 24 |  | access challenge |  |  | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_230A
1311 | ZM0843 | IHS_NTH_231A | MUYOMBE "A" | 33.4534 | -10.5739 | Northern | 2.5 | NORTHERN | Isoka | No | No | No | Rural | Silver | Silver | HUB | HUB | On air | Grid-Gen-solar | Green Field | 50 | Outdoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Lamasat | Lamasat | 20 | perkins | GV 51790R | Leroy Sommer | 0 | 600 | Power cube | 0 | 150 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | n/a | N/A | 174 |  | 2 | MTNAirtel | T3442 | ZM0843 | Yes |  | Yes | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_231A
264 | ZM0844 | IHS_NTH_232A | CHISHIMBA FALLS | 30.9285 | -10.1025 | Northern | 2 | NORTHERN | Kasama | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 16 | Yanmar | B267-SN07 | Mecc Alte | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 200 |  | 2 | MTNAirtel | T3255 | ZM0844 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_232A
1233 | ZM0845 | IHS_NTH_233A | MULENGA HILL (Kasama Town) | 31.2003 | -10.2206 | Northern | 4.5 | NORTHERN | Kasama | Yes | No | No | Suburban | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 50 | Indoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG / Sumsung | LG / Sumsung | 18000 | 18000 | 2 | 198 |  | 2 | MTNAirtel | T3539 | ZM0845 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_233A
805 | ZM3077 | IHS_NTH_235A | LAURA SCHOOL | 31.1712 | -10.2134 | Northern | 2 | NORTHERN | Kasama | No | No | No | Suburban | Silver | Silver | HUB | BTS | On air | Grid-Gen | Green Field | 40 | Indoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 1200 | 48 | 100 | 12 | LG | LG | 18000 | 18000 | 2 | 107 |  | 2 | MTNAirtel | T3301 | ZM3077 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_235A
1629 | ZM3089 | IHS_NTH_236A | SHIWANGANDU "A" | 31.8289 | -11.2018 | Northern | 2.5 | NORTHERN | Chinsali | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 80 | Indoor | Francis Muwowo | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Vitalgen | Vitalgen | 20 | perkins | Gv51790U | Leroy Sommer | TAL 040F J 6/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG / Sumsung | LG / Sumsung | 18000 | 18000 | 2 | 75 |  | 2 | AirtelFrank Furt | 0 | ZM3089 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  | 24 |  | access challenge |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_236A
539 | ZM3090 | IHS_NTH_237A | KALALANTHEKWE "A' | 31.6267 | -11.5044 | Northern | 0 | NORTHERN | Chinsali | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 80 | Indoor | Francis Muwowo | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | Emerson | Network Power | 192/80 | Lithium | 200 | 48 | 100 | 2 | LG | LG | 18000 | 18000 | 2 | 54 |  | 1 | Airtel | 0 | ZM3090 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  | Consolidated IHS_NTH_039M | IHS_NTH_237A
1176 | ZM3212 | IHS_NTH_238A | MPULAMUSENGA "A" | 31.161 | -12.1985 | Northern | 0 | NORTHERN | Mpika | No | No | No | Rural | Silver | Silver | BB | BTS | On air | Solar-Gen | Green Field | 60 | Indoor | Francis Muwowo | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Cordex | 0 | 320 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 45 |  | 1 | Airtel | 0 | ZM3212 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | NO | NO |  |  |  | still on site |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  | Consolidated on IHS_NTH_056m | IHS_NTH_238A
562 | ZM3248 | IHS_NTH_239A | KALONJE | 31.0804 | -12.4179 | Northern | 4.5 | NORTHERN | Mpika | No | No | Yes | Rural | Silver | Silver | BB | BTS | On air | Solar-Gen | Green Field | 60 | Indoor | Francis Muwowo | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 30 | perkins | Di32038 | Leroy Sommer | LSAP423F | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 105 |  | 1 | Airtel | 0 | ZM3248 | Yes |  | Yes | Palisade | Netco | 2022-08-05 | NO | NO |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_239A
873 | ZM3250 | IHS_NTH_241A | LUBWA MISSION "A" | 31.981 | -10.5998 | Northern | 2 | NORTHERN | Chinsali | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 80 | Indoor | Francis Muwowo | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | Gv51790u | Leroy Sommer | ECP-28VL4. | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG / Sumsung | LG / Sumsung | 18000 | 18000 | 2 | 75 |  | 2 | MTNAirtel | T3469 | ZM3250 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_241A
565 | ZM3366 | IHS_NTH_242A | KALUKANYA | 31.2276 | -9.4283 | Northern | 2 | NORTHERN | Mpulungu | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 50 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Lamasat | Lamasat | 16 | perkins | GU51794U | Leroy Sommer | TAL 040D J 6S/4 | 600 | Emerson | Network Power | 192 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | n/a | N/A | 50 |  | 1 | Airtel | 0 | ZM3366 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | NO | NO | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_242A
660 | ZM3450 | IHS_NTH_243A | KAPATU | 30.2881 | -9.4178 | Northern | 2.5 | NORTHERN | Mporokoso | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Solar-Gen | Green Field | 80 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | Gv51790V | Leroy Sommer | LSA 40M5 J6/4 | 600 | Emerson | FlexMax | 80 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | n/a | N/A | 65 |  | 2 | MTNAirtel | T3473 | ZM3450 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 24 |  | collected and already in central warehouse | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_243A
529 | ZM3451 | IHS_NTH_244A | KAFWAMBE | 30.7083 | -9.6926 | Northern | 1.8 | NORTHERN | Mporokoso | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 80 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Vitalgen | Vitalgen | 15 | perkins | GV51790V | Leroy Sommer | TAL 040 FJ 6s/4 | 1000 | Emerson | Network Power | 192/80 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | n/a | N/A | 39 |  | 2 | MTNAirtel | T3494 | ZM3451 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_244A
1339 | ZM3728 | IHS_NTH_245A | Mweniwisi | 33.1428 | -10.0848 | Northern | 1.8 | NORTHERN | Isoka | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Lamasat | Lamasat | 15 | perkins | GV51794V | Leroy Sommer | TAL 040D J6S/4 | 600 | Power cube | 0 | 250 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | n/a | N/A | 58 |  | 1 | Airtel | 0 | ZM3728 | Yes |  | Yes | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_245A
1299 | ZM3729 | IHS_NTH_246A | Muswilo | 31.265 | -8.8016 | Northern | 2 | NORTHERN | Mpulungu | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 70 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 16 | perkins | Gv51790u | Leroy Sommer | 0 | 600 | Emerson | FlexMax | 80 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | n/a | N/A | 52 |  | 2 | MTNAirtel | T3314 | ZM3729 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  | 12 |  | collected and already in central warehouse |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_246A
276 | ZM3732 | IHS_NTH_247A | Chitimukulu | 31.6331 | -10.0072 | Northern | 2 | NORTHERN | Mungwi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 16 | Yanmar | 0 | Mecc Alte | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 74 |  | 2 | MTNAirtel | T3287 | ZM3732 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_247A
980 | ZM3779 | IHS_NTH_248A | MALATA LUWINGU | 30.1805 | -10.2231 | Northern | 2 | NORTHERN | Luwingu | No | No | No | Rural | Silver | Silver | BB | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 16 | perkins | B096-507 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 48 |  | 1 | Airtel | 0 | ZM3779 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  | 12 |  | Collected and Re-used at Lubansenshi |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_248A
1619 | ZM3780 | IHS_NTH_249A | Shauli (ZAIN_ZM0213) | 32.2494 | -10.3579 | Northern | 2 | NORTHERN | Chinsali | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen-solar | Green Field | 60 | Outdoor | Francis Muwowo | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Vitalgen | Vitalgen | 16 | perkins | 0 | Leroy Sommer | 0 | 1000 | Emerson | Network Power | 192/80 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | n/a | N/A | 54 |  | 2 | MTNAirtel | T3509 | ZM3780 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_249A
1157 | ZM3782 | IHS_NTH_250A | MPEPO BB | 31.1299 | -11.1028 | Northern | 0 | NORTHERN | Mpika | No | No | No | Rural | Silver | Silver | BB | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Francis Muwowo | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Power cube | ICC330-H1-C1 | 192 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 42 |  | 1 | Airtel | 0 | ZM3782 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_250A
1308 | ZM3783 | IHS_NTH_251A | MUTIPE | 31.6224 | -9.1116 | Northern | 1.8 | NORTHERN | Mbala | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 70 | Outdoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Lamasat | Lamasat | 15 | perkins | GV51794V | Leroy Sommer | TAL 040D J6S/4 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 45 |  | 1 | Airtel | 0 | ZM3783 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_251A
186 | ZM3784 | IHS_NTH_252A | CHILESHE | 31.8773 | -9.0633 | Northern | 1.8 | NORTHERN | Mbala | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 15 | perkins | Gv51790V | Leroy Sommer | LSA 40M5 J6/4 | 600 | Emerson | FlexMax | 120/80 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | n/a | N/A | 93 |  | 1 | Airtel | 0 | ZM3784 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_252A
867 | ZM3785 | IHS_NTH_253A | LUBU FARM BB | 32.3755 | -10.5414 | Northern | 0 | NORTHERN | Chinsali | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 60 | Outdoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Emerson | Network Power | 192/80 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | n/a | N/A | 112 |  | 1 | Airtel | 0 | ZM3785 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  | Consolidated IHS_NTH_028M | IHS_NTH_253A
1266 | ZM3786 | IHS_NTH_254A | MUNDULUSI BB | 32.4042 | -10.2703 | Northern | 0 | NORTHERN | Chinsali | No | No | No | Rural | Silver | Silver | BB | BTS | On air | Solar-Gen | Green Field | 80 | Outdoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Emerson | Network Power | 150/80 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 53 |  | 1 | Airtel | 0 | ZM3786 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  | Consolidated IHS_NTH_027M | IHS_NTH_254A
712 | ZM3787 | IHS_NTH_255A | KASONGO BB | 31.242 | -11.3065 | Northern | 2 | NORTHERN | Mpika | No | No | Yes | Rural | Silver | Silver | BB | BTS | On air | Grid-Gen | Green Field | 70 | Outdoor | Francis Muwowo | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | IMG | IMG | 16 | perkins | GU51794U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 45 |  | 1 | Airtel | 0 | ZM3787 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_255A
100 | ZM3788 | IHS_NTH_256A | CHAMBISHI | 31.0684 | -10.9512 | Northern | 2 | NORTHERN | Mpika | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Grid-Gen | Green Field | 62 | Outdoor | Francis Muwowo | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Lamasat | Lamasat | 16 | perkins | GU51794U | Leroy Sommer | TAL 040D J 6S/4 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 65 |  | 1 | Airtel | 0 | ZM3788 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_256A
1601 | ZM3789 | IHS_NTH_257A | SENGA MATELO | 31.3598 | -9.1912 | Northern | 2 | NORTHERN | Mpulungu | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 16 | perkins | GLPM-C1000-15-3P-7320 | Leroy Sommer | 0 | 1000 | Emerson | Network Power | 192/80 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | n/a | N/A | 70.8 |  | 2 | MTNAirtel | T3554 | ZM3789 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_257A
82 | ZM3818 | IHS_NTH_258A | Chalabesa (Mukabi) | 31.0177 | -11.3793 | Northern | 2 | NORTHERN | Mpika | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 72 | Outdoor | Francis Muwowo | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Lamasat | Lamasat | 16 | perkins | GK66187R | Leroy Sommer | LSA 423VS2 J 6/4 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 75 |  | 2 | MTNAirtel | T3492 | ZM3818 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_258A
200 | ZM3833 | IHS_NTH_259A | Chimbamilonga | 29.9966 | -8.4021 | Northern | 2.5 | NORTHERN | Kaputa | No | No | No | Rural | Silver | Silver | HUB | HUB | On air | Solar-Gen | Green Field | 80 | Outdoor | Kennedy Mwansa | Lazarous kupa Mutamali | Stanley Bwalya | Airtel | Flavian Mazhambi | GNM | Lithandi | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | Huawei/MPPT | 150/80 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | n/a | N/A | 48 |  | 2 | MTNAirtel | TX | ZM3833 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  |  | 18 | collected still at regional office |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_259A
1746 | ZM3871 | IHS_NTH_260A | Tungati (CHIENGI 2_2) | 29.3057 | -8.5518 | Northern | 2.5 | NORTHERN | Chiengi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 70 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | Gv51790V | Leroy Sommer | LSA 40M5 J6/4 | 600 | Power cube | FlexMax | 120/80 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 90 |  | 2 | MTNAirtel | T3458 | ZM3871 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  | 48 |  | collected and already in central warehouse |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_260A
600 | ZM3900 | IHS_NTH_261A | Kampumbu (Muyombe 2_2) | 32.8641 | -10.3081 | Northern | 1.8 | NORTHERN | Isoka | No | No | No | Rural | Silver | Silver | BTS | BB/HUB | On air | Solar-Gen | Green Field | 60 | Outdoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | RID | RID | 20 | Mitsubishi | S4LZ | Zanardi | AL 3/4 | 600 | MPPT | FlexMax | 80 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | n/a | N/A | 138 |  | 1 | Airtel | 0 | ZM3900 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 2 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_261A
424 | ZM3902 | IHS_NTH_262A | ILONDOLA MISSION | 31.7892 | -10.7405 | Northern | 1.8 | NORTHERN | Chinsali | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Francis Muwowo | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 45 |  | 1 | Airtel | 0 | ZM3902 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_262A
270 | ZM3907 | IHS_NTH_263A | CHITAMBI | 31.1688 | -10.2674 | Northern | 1.8 | NORTHERN | Kasama | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | BIA | BIA | 15 | perkins | GU51794U | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 44 |  | 1 | Airtel | 0 | ZM3907 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_263A
1484 | ZM3973 | IHS_NTH_264A | Nsambo (Chakopa_3_RLF) | 29.9473 | -10.8074 | Northern | 2 | NORTHERN | Chilubi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 80 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | IMG | IMG | 16 | perkins | GU51794U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | FlexMax | 120/80 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | n/a | N/A | 38 |  | 2 | MTNAirtel | T3439 | ZM3973 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  | 24 |  | collected and already in central warehouse |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_264A
1102 | ZM3975 | IHS_NTH_265A | MILIMA | 31.2673 | -10.1241 | Northern | 1.8 | NORTHERN | Mungwi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | MPI | MPI | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 71 |  | 2 | MTNAirtel | T3515 | ZM3975 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_265A
1341 | ZM3976 | IHS_NTH_266A | MWENZO | 32.666 | -9.3276 | Northern | 1.8 | NORTHERN | Nakonde | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Lamasat | Lamasat | 15 | perkins | GV51794V | Leroy Sommer | LSA 42.3VS2 J6/4 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 64 |  | 1 | Airtel | 0 | ZM3976 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_266A
1068 | ZM3977 | IHS_NTH_267A | MBALA ZAF | 31.3357 | -8.8663 | Northern | 1.8 | NORTHERN | Mpulungu | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | RID | RID | 15 | Mitsubishi | S4L2 | Zanardi | AL3/4 | 600 | Emerson | Network Power | 192 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | n/a | N/A | 82 |  | 2 | MTNAirtel | T3309 | ZM3977 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_267A
218 | ZM3978 | IHS_NTH_268A | CHINSALI-2_RLF | 32.1121 | -10.5703 | Northern | 2 | NORTHERN | Chinsali | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 70 | Outdoor | Francis Muwowo | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Lamasat | Lamasat | 20 | perkins | GK66187R. | Leroy Sommer | 25A42.3V52S 6/4 IP23. | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 100 | 48 | 100 | 1 | N/A | N/A | N/A | n/a | N/A | 75 |  | 2 | MTNAirtel | T3286 | ZM3978 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | NO | NO | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_268A
933 | ZM3979 | IHS_NTH_269A | LWITIKILA | 31.4774 | -11.7073 | Northern | 2 | NORTHERN | Mpika | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Francis Muwowo | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 1000 | Delta | IPT | 250 | Lithium | 100 | 48 | 100 | 1 | N/A | N/A | N/A | n/a | N/A | 72 |  | 2 | MTNAirtel | T3305 | ZM3979 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_269A
1359 | ZM3980 | IHS_NTH_270A | NAKONDE ZRA | 32.6852 | -9.3623 | Northern | 1.8 | NORTHERN | Nakonde | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 100 | 48 | 100 | 1 | N/A | N/A | N/A | n/a | N/A | 48 |  | 1 | Airtel | 0 | ZM3980 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_270A
689 | ZM3981 | IHS_NTH_271A | KASAMA TOWN1 | 31.0906 | -10.2247 | Northern | 1.8 | NORTHERN | Kasama | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | CK Works | CK Works | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 49 |  | 1 | Airtel | 0 | ZM3981 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_271A
175 | ZM3982 | IHS_NTH_272A | CHILA | 31.3833 | -8.8144 | Northern | 1.8 | NORTHERN | Mpulungu | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | RID | RID | 15 | Mitsubishi | 0 | Zanardi | 0 | 600 | Emerson | Network Power | 192 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | n/a | N/A | 68.2 |  | 2 | MTNAirtel | T3337 | ZM3982 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_272A
884 | ZM3984 | IHS_NTH_274A | LUKASHYA | 31.2692 | -10.2383 | Northern | 1.8 | NORTHERN | Mungwi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | BIA | BIA | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Delta | IPT | 250 | Power safe | 1200 | 2 | 1200 | 24 | N/A | N/A | N/A | n/a | N/A | 45 |  | 1 | Airtel | 0 | ZM3984 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_274A
685 | ZM3998 | IHS_NTH_275A | Kasama Airport | 31.1569 | -10.1351 | Northern | 2 | NORTHERN | Kasama | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | JIUAN GENERATOR | JIUAN GENERATOR | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 84 |  | 1 | Airtel | 0 | ZM3998 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | Yes | No |  | 2 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_275A
1164 | ZM3999 | IHS_NTH_276A | Mpika2 | 31.4538 | -11.8562 | Northern | 2 | NORTHERN | Mpika | Yes | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Francis Muwowo | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 115 |  | 3 | MTNAirtelLiquid Telecom | T3448 | ZM3999 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_276A
991 | ZM6014 | IHS_NTH_277A | Mambwe Mission | 31.6951 | -9.1899 | Northern | 1.8 | NORTHERN | Mbala | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen-solar | Green Field | 80 | Outdoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Lamasat | Lamasat | 15 | perkins | GV51794V | Leroy Sommer | TAL 040D J6S/4 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | n/a | N/A | 89 |  | 2 | MTNAirtel | T3418 | ZM6014 | Yes |  | Yes | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_277A
466 | ZM6016 | IHS_NTH_279A | Kabanda | 31.2859 | -10.8657 | Northern | 1.8 | NORTHERN | Chinsali | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen-solar | Green Field | 60 | Outdoor | Francis Muwowo | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Green Power | Green Power | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Emerson | FlexMax | 200/80 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | n/a | N/A | 36 |  | 1 | Airtel | 0 | ZM6016 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_279A
786 | ZM6017 | IHS_NTH_280A | Kopa | 30.7826 | -11.7333 | Northern | 1.8 | NORTHERN | Mpika | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Francis Muwowo | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | GNM | GNM | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | FlexMax | 400/80 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | n/a | N/A | 74 |  | 2 | MTNAirtel | T3486 | ZM6017 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  | 24 |  | still on site |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_280A
1624 | ZM6034 | IHS_NTH_282A | Shikulu Musonda (Bemba Makasa 1_6 Rpt) | 31.0607 | -9.5543 | Northern | 1.8 | NORTHERN | Mbala | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | CK Works | CK Works | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 42 |  | 1 | Airtel | 0 | ZM6034 | Yes |  | Yes | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_282A
1234 | ZM6050 | IHS_NTH_283A | Mulilansolo Mission | 32.2489 | -10.0684 | Northern | 1.5 | NORTHERN | Chinsali | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Elcos | Elcos | 12 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 45 |  | 1 | MTN | T3417 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_283A
787 | ZM6106 | IHS_NTH_284A | Kopa rpt | 31.1785 | -11.7617 | Northern | 1.8 | NORTHERN | Mpika | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Francis Muwowo | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | GNM | GNM | 20 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | FlexMax | 150/80 | Lithium | 100 | 48 | 100 | 1 | N/A | N/A | N/A | n/a | N/A | 44 |  | 2 | MTNAirtel | TX | ZM6106 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  | 24 |  | still on site |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_284A
671 | ZM6121 | IHS_NTH_285A | Kapishya | 31.5805 | -11.1856 | Northern | 2 | NORTHERN | Chinsali | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Francis Muwowo | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 52 |  | 1 | Airtel | 0 | ZM6121 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_285A
309 | ZM6122 | IHS_NTH_286A | Chunga Farm | 32.4849 | -9.8225 | Northern | 2.5 | NORTHERN | Chinsali | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | GLPMC1000 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 45 |  | 1 | MTN | T3520 | 0 | Yes |  | Yes | Palisade | Netco | 2022-08-05 | Yes | Yes |  | 2 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_286A
725 | ZM6123 | IHS_NTH_287A | Katenshya Mission | 31.0598 | -9.64 | Northern | 1.8 | NORTHERN | Mporokoso | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Metco | Metco | 15 | perkins | S4LZ | Leroy Sommer | AL 3/4 | 600 | Emerson | Network Power | 192 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 42 |  | 1 | MTN | T3533 | 0 | Yes |  | Yes | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_287A
654 | ZM6125 | IHS_NTH_288A | Kaombwe | 32.8829 | -9.478 | Northern | 2 | NORTHERN | Nakonde | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | GN66044V | Leroy Sommer | ECO 28-VL/4 | 1000 | Power cube | 0 | 150 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | n/a | N/A | 38 |  | 1 | MTN | T3463 | 0 | Yes |  | Yes | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_288A
1286 | ZM6127 | IHS_NTH_289A | Musanza | 32.5572 | -9.2881 | Northern | 2 | NORTHERN | Nakonde | No | No | No | Rural | Silver | Silver | BB | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 16 | perkins | GV51790V | Leroy Sommer | ECO-VL/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | n/a | N/A | 79 |  | 1 | Airtel | 0 | ZM6127 | Yes |  | Yes | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_289A
1435 | ZM6135 | IHS_NTH_290A | New Kaseshya | 30.7674 | -11.1895 | Northern | 1.8 | NORTHERN | Kasama | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 70 | Outdoor | Francis Muwowo | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | n/a | N/A | 36 |  | 1 | MTN | T3465 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | NO | NO | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_290A
1312 | ZM6162 | IHS_NTH_291A | Muyombe 2_1 Kapililonga | 32.7274 | -9.9927 | Northern | 1.8 | NORTHERN | Isoka | No | No | No | Rural | Silver | Silver | BTS | BB | On air | Solar-Gen | Green Field | 50 | Outdoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | CK Works | CK Works | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Emerson | Network Power | 192/80 | Lithium | 100 | 48 | 100 | 1 | N/A | N/A | N/A | n/a | N/A | 92 |  | 2 | MTNAirtel | T3523 | ZM6162 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_291A
953 | ZM6166 | IHS_NTH_293A | Makaka Village (ZAIN_ZM0202_1) | 29.9339 | -8.3771 | Northern | 1.8 | NORTHERN | Kaputa | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Kennedy Mwansa | Lazarous kupa Mutamali | Stanley Bwalya | Airtel | Flavian Mazhambi | GNM | Lithandi | RID | RID | 15 | Mitsubishi | 0 | Zanardi | 0 | 600 | MPPT | FlexMax | 192/80 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | n/a | N/A | 35 |  | 1 | Airtel | 0 | ZM6166 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_293A
39 | ZM6167 | IHS_NTH_294A | BHART_AIRTEL025 | 30.0102 | -10.4543 | Northern | 1.8 | NORTHERN | Luwingu | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | RID | RID | 15 | Mitsubishi | 54L2 | Zanardi | AL3/4 | 600 | MPPT | FlexMax | 192/80 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | n/a | N/A | 38 |  | 1 | Airtel | T3524 | ZM6167 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_294A
1490 | ZM6168 | IHS_NTH_295A | NSUMBU_1 | 30.1381 | -10.6874 | Northern | 1.8 | NORTHERN | Luwingu | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | RID | RID | 15 | Mitsubishi | 0 | Zanardi | 0 | 600 | MPPT | FlexMax | 192/80 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | n/a | N/A | 38 |  | 1 | Airtel | 0 | ZM6168 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_295A
37 | ZM6172 | IHS_NTH_296A | Bemba Makasa 1_2 | 30.2308 | -8.3768 | Northern | 1.8 | NORTHERN | Kaputa | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Lamasat | Lamasat | 15 | perkins | GV51794V | Leroy Sommer | AL4/4 | 600 | Power cube | FlexMax | 120/80 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | n/a | N/A | 35 |  | 1 | Airtel | 0 | ZM6172 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  | 24 |  | collected and already in central warehouse |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_296A
1789 | ZM6173 | IHS_NTH_297A | Zain ZM0202_2 (Chapi Village) Katwatwa | 29.8771 | -8.7987 | Northern | 1.8 | NORTHERN | Kaputa | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 15 | perkins | GV 51790V | Leroy Sommer | ECP -28-M/4 | 1000 | Emerson | Network Power | 192/80 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 64 |  | 1 | Airtel | 0 | ZM6173 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_297A
1361 | ZM6189 | IHS_NTH_299A | NAKONDE_1_Rlf | 32.7635 | -9.3073 | Northern | 2 | NORTHERN | Nakonde | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 16 | perkins | GV51794V | Leroy Sommer | AL 3/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 104 |  | 2 | MTNAirtel | T3545 | ZM6189 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_299A
1362 | ZM6190 | IHS_NTH_300A | NAKONDE_3_Rlf | 32.7523 | -9.3331 | Northern | 2 | NORTHERN | Nakonde | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 40 | Outdoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 16 | perkins | GV51790V | Leroy Sommer | ECP 28-M/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 100 | 48 | 100 | 1 | N/A | N/A | N/A | n/a | N/A | 89 |  | 1 | Airtel | 0 | ZM6190 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_300A
680 | ZM6197 | IHS_NTH_301A | Kaputa Zicta | 29.6401 | -8.996 | Northern | 1.8 | NORTHERN | Kaputa | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Lamasat | Lamasat | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | 0 | 150 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 55 |  | 1 | Airtel | 0 | ZM6197 | Yes |  | Yes | Palisade | Netco | 2022-08-05 | No | No |  | 20 |  | collected and already in central warehouse |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_301A
201 | ZM6198 | IHS_NTH_302A | Chimbamilonga Rp | 30.397 | -8.5058 | Northern | 1.8 | NORTHERN | Kaputa | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Solar-Gen | Green Field | 80 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | RID | RID | 15 | Mitsubishi | S4L2 | Zanardi | AL3/4 | 600 | MPPT | FlexMax | 80 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | n/a | N/A | 55 |  | 3 | MTNAirtelFrank Furt | T3493 | ZM6198 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No |  | 48 |  | collected and already in central warehouse |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_302A
263 | ZM6318 | IHS_NTH_303A | Chishela & Kampinda - Chimbamilonga | 29.9464 | -8.6383 | Northern | 1.8 | NORTHERN | Kaputa | No | No | No | Rural | Silver | Silver | HUB | HUB | On air | Solar-Gen | Green Field | 60 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Green Power | Green Power | 15 | perkins | Gv51790V | Leroy Sommer | LSA 40M5 J6/4 | 600 | Power cube | FlexMax | 400/80 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | n/a | N/A | 45 |  | 1 | Airtel | 0 | ZM6318 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | NO | NO | [6 empty] | No | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_NTH_303A
280 | ZM6327 | IHS_NTH_304A | Chitoshi | 30.1986 | -10.1031 | Northern | 1.8 | NORTHERN | Mporokoso | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 80 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 15 | perkins | 0 | Leroy Sommer | 0 | 1000 | Emerson | Network Power | 192 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | n/a | N/A | 58 |  | 2 | MTNAirtel | T3478 | ZM6327 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_304A
1483 | ZM6338 | IHS_NTH_305A | Nsama | 29.9584 | -8.8929 | Northern | 1.8 | NORTHERN | Kaputa | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Solar-Gen | Green Field | 80 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 15 | perkins | GN66045U | Leroy Sommer | ECO-28-m/4 | 1000 | Power cube | 0 | 150 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | n/a | N/A | 57 |  | 2 | MTNAirtel | T3459 | ZM6338 | Yes |  | Yes | Palisade | Netco | 2022-08-05 | No | No |  | 24 |  | collected and already in central warehouse |  |  | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_305A
262 | ZM6339 | IHS_NTH_306A | Chishela | 30.1421 | -8.5381 | Northern | 1.8 | NORTHERN | Kaputa | No | No | No | Rural | Silver | Silver | BB | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Vitalgen | Vitalgen | 15 | perkins | GV15794U | Leroy Sommer | TAL 040 F J 6s/4 | 600 | Power cube | 0 | 150 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | n/a | N/A | 74 |  | 2 | MTNAirtel | T3495 | ZM6339 | Yes |  | Yes | Palisade | Netco | 2022-08-05 | No | No |  | 24 |  | collected and already in central warehouse |  |  | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_306A
597 | ZM6340 | IHS_NTH_307A | Kampinda | 29.7667 | -8.7833 | Northern | 2.5 | NORTHERN | Kaputa | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 80 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 20 | perkins | GV 51780V | Leroy Sommer | ECP -28-m/4 | 1000 | Power cube | 0 | 150 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | n/a | N/A | 78 |  | 2 | MTNAirtel | T3474 | ZM6340 | Yes |  | Yes | Palisade | Netco | 2022-08-05 | Yes | Yes |  | 24 |  | collected and already in central warehouse | pending |  | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_307A
1489 | ZM6365 | IHS_NTH_308A | Nsumbu | 30.448 | -8.5164 | Northern | 2 | NORTHERN | Kaputa | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 80 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | n/a | N/A | 62 |  | 2 | MTNAirtel | TX | ZM6365 | Yes |  | Yes | Palisade | Netco | 2022-08-05 | No | No |  | 24 |  | collected and already in central warehouse |  |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_308A
550 | ZM6395 | IHS_NTH_309A | Kalinda | 33.45 | -10.4667 | Northern | 1.8 | NORTHERN | Isoka | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Grid-Gen-solar | Green Field | 80 | Outdoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | RID | RID | 15 | Mitsubishi | S4LZ | Zanardi | AL 3/4 | 600 | MPPT | FlexMax | 80 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | n/a | N/A | 67 |  | 2 | MTNAirtel | TX | ZM6395 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_309A
1154 | ZM6414 | IHS_NTH_310A | Mpemba | 33.2902 | -10.5394 | Northern | 1.8 | NORTHERN | Isoka | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 70 | Outdoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | CK Works | CK Works | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | 0 | 150 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | n/a | N/A | 89 |  | 2 | MTNAirtel | T3488 | ZM6414 | Yes |  | Yes | Palisade | Netco | 2022-08-05 | Yes | Yes |  | 2 |  |  | Done |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_310A
931 | ZM6418 | IHS_NTH_311A | Lwena Mission | 30.2 | -10.65 | Northern | 2 | NORTHERN | Luwingu | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 16 | perkins | GL-c100-20-3P-7320 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | n/a | N/A | 25 |  | 1 | Airtel | 0 | ZM6418 | Yes |  | Yes | Mesh | Netco | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_311A
1471 | ZM6419 | IHS_NTH_312A | Nkula | 31.9178 | -10.6402 | Northern | 2.5 | NORTHERN | Chinsali | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 70 | Outdoor | Francis Muwowo | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Lamasat | Lamasat | 20 | perkins | Gv51794u | Leroy Sommer | TAL 040D J 6S/4 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 32 |  | 1 | MTN | T3511 | 0 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_312A
202 | ZM6421 | IHS_NTH_313A | Chimbele | 32.05 | -10.7833 | Northern | 1.8 | NORTHERN | Chinsali | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 80 | Outdoor | Francis Muwowo | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | MPI | MPI | 15 | perkins | 0 | Leroy Sommer | 0 | 600 | Emerson | Network Power | 192 | Power safe | 1200 | 2 | 1200 | 24 | N/A | N/A | N/A | n/a | N/A | 45 |  | 1 | Airtel | 0 | ZM6421 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_313A
1237 | ZM6443 | IHS_NTH_314A | Mulilo | 33.0294 | -10.5759 | Northern | 2 | NORTHERN | Chama | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | CK Works | CK Works | 16 | perkins | 0 | Leroy Sommer | 0 | 600 | Power cube | 0 | 150 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | n/a | N/A | 52 |  | 1 | Airtel | 0 | ZM6443 | Yes |  | Yes | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_314A
688 | ZM6473 | IHS_NTH_315A | Kasama Town_3_Rlf (Chiba) | 31.1819 | -10.2225 | Northern | 2 | NORTHERN | Kasama | No | No | No | Suburban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 37 |  | 1 | Airtel | 0 | ZM6473 | Yes |  | Yes | Mesh | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_315A
1047 | ZM6495 | IHS_NTH_316A | Matipa Parish | 30.3 | -10.85 | Northern | 1.8 | NORTHERN | Chilubi | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | RID | RID | 15 | Mitsubishi | 0 | Zanardi | 0 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | n/a | N/A | 35 |  | 1 | Airtel | 0 | ZM6495 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | NO | NO | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_316A
1226 | ZM6606 | IHS_NTH_317A | Mukunta | 31.5681 | -9.1726 | Northern | 1.8 | NORTHERN | Kasama | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Lamasat | Lamasat | 15 | perkins | GV51794V | Leroy Sommer | TAL 040D J6S/4 | 600 | Power cube | ICC330-H1-C1 | 400 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | n/a | N/A | 79 |  | 2 | MTNAirtel | TX | ZM6606 | Yes |  | Yes | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_317A
134 | ZM6776 | IHS_NTH_318A | Chiba 3G | 31.1802 | -10.2357 | Northern | 2 | NORTHERN | Kasama | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 16 | perkins | GV51790V | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | n/a | N/A | 66 |  | 2 | MTNAirtel | T3335 | ZM6776 | Yes |  | Yes | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_NTH_318A
697 | ZM1492 | IHS_NTH_319A | Kasenda School | 31.1863 | -10.2138 | Northern | 2 | NORTHERN | Kasama | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 200 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 98 |  | 1 | Airtel | ZM1519 | ZM1492 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_NTH_319A
69 | ZM1493 | IHS_NTH_320A | Central Town | 31.1788 | -10.1995 | Northern | 2.5 | NORTHERN | Kasama | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Samson Nyirenda | SBC | Lithandi | Airtel | Flavian Mazhambi | GNM | Lithandi |  |  | 20 | perkins |  |  |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 75 |  | 1 | Airtel | 0 | ZM1493 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_NTH_320A
260 | ZM1491 | IHS_NTH_321A | Chisanga Two | 31.2033 | -10.2329 | Northern | 2.5 | NORTHERN | Kasama | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Samson Nyirenda | SBC | SBC | Airtel | Flavian Mazhambi | GNM | GNM | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 67 |  | 1 | Airtel | ZM1486 | ZM1491 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_NTH_321A
1069 | ZM1513 | IHS_NTH_322A | Mbala Zambia Compound | 31.3498 | -15.2875 | Northern | 2.5 | NORTHERN | Mbala | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Francis Muwowo | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 62 |  | 1 | Airtel | ZM1513 | ZM1513 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_NTH_322A
1358 | ZM1520 | IHS_NTH_323A | Nakonde New Stadium | 32.7677 | -12.9921 | Northern | 2.5 | NORTHERN | Nakonde | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Kwibisa Mbindawina | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 100 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 72 |  | 1 | Airtel | ZM1520 | ZM1520 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_NTH_323A
978 | ZM1521 | IHS_NTH_324A | Malalo Compund | 32.7528 | -9.3213 | Northern | 2.5 | NORTHERN | Nakonde | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Kwibisa Mbindawina | GNM | Lithandi | Airtel | Flavian Mazhambi | GNM | Lithandi |  |  | 20 | perkins |  |  |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 200 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 69 |  | 1 | Airtel | 0 | ZM1521 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_NTH_324A
1864 | ZM1336 | IHS_NTH_325A | Lambwe Chomba Village | -8.4179 | 29.5885 | Northern | 4.5 | Northern | Kaputa | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 70 | Outdoor | Kennedy Mwansa | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 30 | perkins |  |  |  | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_NTH_325A
1865 | ZM1415 | IHS_NTH_326A | Kalaba village | -8.4179 | 29.8789 | Northern | 4.5 | Northern | Kaputa | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Solar-Gen | Green Field | 70 | Outdoor | Kennedy Mwansa | SBC | SBC | Airtel | Flavian Mazhambi | GNM | Lithandi | Gen Logic | Gen Logic | 30 | perkins |  |  |  | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_NTH_326A
1855 | ZM1365 | IHS_NTH_327A | Kakungu primary sch | 31.7653 | -8.9425 | Northern | 4.5 | Northern | Mbala | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Solar-Gen | Green Field | 60 | Outdoor |  | N/A | N/A | Airtel | Flavian Mazhambi | GNM | Lithandi | perkins |  | 30 |  |  |  |  | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_NTH_327A
1851 | ZM1370 | IHS_NTH_328A | Mukupa Kaoma | 30.2477 | -10.8251 | Northern | 4.5 | Northern | Kapata | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Gen Only | Green Field | 70 | Outdoor |  | N/A | N/A | Airtel | Flavian Mazhambi | GNM | Lithandi | perkins |  | 30 | perkins |  |  |  | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_NTH_328A
244 | T0132 | IHS_STR_001M | Chipembi Road | 25.8608 | -17.8507 | Southern | 1.5 | SOUTHERN | LIVINGSTONE | Yes | No | No | Urban | 2G 3G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 13 | Yanmar | 4TNE88-G1A | Mecc Alte | ECO28-SN/4 | 600 | Delta | DPS 2400B-48-5 | 250 | coslight | 400 | 2 | 400 | 24 | N/A | N/A | N/A | NA | N/A | 44 |  | 1 | MTN | T0132 | 0 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_001M
835 | T0333 | IHS_STR_002M | Livingstone Town Centre | 25.8526 | -17.8451 | Southern | 1.8 | SOUTHERN | LIVINGSTONE | Yes | No | No | Urban | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Earth Technology | Earth technology | 15 | perkins | GU51790U | Leroy Sommer | LSA 40M5 J 6/4 | 600 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | NA | N/A | 60 |  | 2 | MTNLiquid Telecom | T0333 | 0 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | yes |  |  | Pending | n/a |  | Pending |  |  |  |  | IHS_STR_002M
1019 | T0264 | IHS_STR_003M | Maramba | 25.8737 | -17.8467 | Southern | 1.8 | SOUTHERN | LIVINGSTONE | Yes | No | No | Urban | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Falcon | Falcon | 15 | perkins | GU51798U | Leroy Sommer | LSA 40M5 J 6/4 | 600 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | NA | N/A | 40 |  | 1 | MTN | T0264 | 0 | Yes |  |  | Palisade | Inala | 2022-08-05 | Yes | No |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_003M
823 | T0106 | IHS_STR_004M | Linda | 25.8728 | -17.8589 | Southern | 2.5 | SOUTHERN | LIVINGSTONE | Yes | No | No | Urban | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Outdoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GU51794U | Leroy Sommer | LSA 40M5 J 6/4 | 1000 | Delta | DPS 2400B-48-5 | 250 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | NA | N/A | 90 |  | 2 | MTNAirtel | T0106 | ZM6883 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | yes |  |  | Pending | n/a |  | Pending |  |  |  |  | IHS_STR_004M
829 | T0013 | IHS_STR_005M | Livingstone | 25.8571 | -17.8335 | Southern | 4.5 | SOUTHERN | LIVINGSTONE | Yes | Yes | No | Urban | 2G 3G 4G | P3 | BB | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 2490/1500 | Mecc Alte | ECP 28-VL/4 | 1000 | Delta | DPS 2400B-48-5 | 250 | Wolong | 1200 | 2 | 600 | 48 | window/LG and CHIGO | window/LG and CHIGO | 18000 | 18000 | 2 | 110 |  | 5 | MTNAirtelINQLiquid TelecomParatus Telecom | T0013 | ZM6784 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_005M
325 | T0093 | IHS_STR_006M | Dambwa Central | 25.8428 | -17.8558 | Southern | 1.5 | SOUTHERN | LIVINGSTONE | Yes | No | No | Urban | 2G 3G | P4 | BTS | BB | On air | Grid-Gen | Green Field | 48 | Outdoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Falcon | Falcon | 13 | perkins | GU51798U | Leroy Sommer | LSA 40M5 J 6/4 | 600 | Delta | DPS 2400B-48-5 | 250 | Amaron | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | NA | N/A | 100 |  | 2 | MTNAirtel | T0093 | ZM0209 | Yes |  |  | Palisade | Inala | 2022-08-05 | Yes | No |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_006M
1695 | T0120 | IHS_STR_007M | Spur Shopping Centre | 25.855 | -17.8711 | Southern | 1.8 | SOUTHERN | LIVINGSTONE | Yes | No | No | Urban | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Outdoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | GU51794U | Mecc Alte | ECO28-SN/4 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | NA | N/A | 65 |  | 2 | MTNINQ | T0120 | 0 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | yes |  |  | yes | 15 |  | Pending |  |  |  |  | IHS_STR_007M
1575 | T0273 | IHS_STR_008M | Rottie Board | 25.8779 | -17.8339 | Southern | 1.5 | SOUTHERN | LIVINGSTONE | No | No | No | Urban | 2G 3G | P3 | BTS | Hub | On air | Grid-Gen | Green Field | 36 | Outdoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | MPI | MPI | 10 | perkins | GK65597R | Leroy Sommer | LSA 40M5 J 6/4 | 600 | Delta | DPS 2400B-48-5 | 250 | Agisson | 400 | 2 | 400 | 24 | N/A | N/A | N/A | NA | N/A | 42 |  | 1 | MTN | T0273 | 0 | Yes |  |  | Palisade | Inala | 2022-08-05 | Yes | No |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_008M
812 | T0104 | IHS_STR_009M | Libuyu | 25.885 | -17.8478 | Southern | 1.8 | SOUTHERN | LIVINGSTONE | No | No | No | Urban | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Outdoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | FG wilson | FG wilson | 15 | perkins | GU51794U | Leroy Sommer | LSA 40M5 J 6/4 | 600 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | NA | N/A | 172 |  | 2 | MTNAirtel | T0104 | ZM0214 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_009M
1711 | T0284 | IHS_STR_010M | St. Raphaels | 25.8679 | -17.823 | Southern | 1.5 | SOUTHERN | LIVINGSTONE | No | No | No | Urban | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Elcos | Elcos | 13 | perkins | GU51794U | Mecc Alte | ECP 3-3L/4 | 600 | Delta | DPS 2400B-48-5 | 250 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | NA | N/A | 90 |  | 2 | MTNAirtel | T0284 | ZM6768 | Yes |  |  | Palisade | Inala | 2022-08-05 | Yes | No |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_010M
293 | T0257 | IHS_STR_011M | Choma Secondary | 25.8472 | -17.8897 | Southern | 1.5 | SOUTHERN | LIVINGSTONE | Yes | No | No | Urban | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Pramac | Pramac | 15 | perkins | 3TNV76-GPGE | LINZ | TAL 040F J 6S/4 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 84 |  | 2 | MTNAirtel | T0257 | ZM0220 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | yes |  |  | Pending | n/a |  | Pending |  |  |  |  | IHS_STR_011M
324 | T0056 | IHS_STR_012M | Dambo North | 25.8141 | -17.8529 | Southern | 2.5 | SOUTHERN | LIVINGSTONE | Yes | No | No | Urban | 2G 3G | P4 | BTS | BB | On air | Grid-Gen | Green Field | 50 | Indoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GV51790U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | window/LG | window/LG | 18000 | 18000 | 2 | 100 |  | 2 | MTNAirtel | T0056 | ZM6770 | Yes |  |  | Palisade | Inala | 2022-08-05 | Yes | No |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_012M
831 | T0107 | IHS_STR_013M | Livingstone Airport | 25.819 | -17.8262 | Southern | NA | SOUTHERN | LIVINGSTONE | Yes | No | No | Urban | 2G 3G 4G | P4 | BTS | BTS | On air | Grid-Gen | Roof Top | RT | Outdoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | In House | NA | NA | NA | NA | NA | NA | NA | N/A | NA | NA | NA | NA | NA | NA | NA |  | N/A | N/A | N/A | NA | N/A | 64 |  | 2 | MTNLiquid Telecom | T0107 | 0 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_013M
1770 | T0049 | IHS_STR_014M | Victoria Falls | 25.8717 | -17.9236 | Southern | 1.8 | SOUTHERN | LIVINGSTONE | Yes | No | No | Urban | 2G 3G 4G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Lister pitter | LISTER PETTER | 15 | Lister petter | LPW4A07 | Leroy Sommer | 42 2S4 J 6/4 | 600 | Delta | DPS 2400B-48-5 | 250 | Amaron | 600 | 2 | 600 | 24 | window/LG | window/LG | 18000 | 18000 | 2 | 60 |  | 1 | MTN | T0049 | 0 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_014M
1656 | T0285 | IHS_STR_015M | Simoonga | 25.7188 | -17.8046 | Southern | 1.5 | SOUTHERN | LIVINGSTONE | Yes | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 70 | Outdoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | MPI | MPI | 10 | perkins | GK65597R | Leroy Sommer | LSA 40M5 J 6/4 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | NA | N/A | 42 |  | 2 | MTNINQ | T0285 | 0 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_015M
1603 | T0053 | IHS_STR_016M | Senkobo | 25.9788 | -17.6023 | Southern | 2.5 | SOUTHERN | LIVINGSTONE | Yes | No | No | Rural | 2G 3G | P4 | BB | BB | On air | Grid-Gen | Green Field | 46 | Indoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | IMG | IMG | 20 | perkins | GU51794U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | window/LG | window/LG | 18000 | 18000 | 2 | 40 |  | 1 | MTN | T0053 | 0 | Yes |  |  | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_016M
732 | T0057 | IHS_STR_017M | Katombola Kazungula | 25.5115 | -17.7783 | Southern | 2.5 | SOUTHERN | KAZUNGULA | Yes | No | No | Rural | 2G | P4 | BB | BTS | On air | Grid-Gen | Green Field | 70 | Indoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | IMG | IMG | 20 | perkins | GU51794U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | window/LG | window/LG | 18000 | 18000 | 2 | 90 |  | 2 | MTNAirtel | T0057 | ZM0171 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_017M
62 | T0065 | IHS_STR_018M | Camp site Livingstone | 26.0692 | -17.4739 | Southern | 1.5 | SOUTHERN | LIVINGSTONE | Yes | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Outdoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 13 | Yanmar | 4TNE88-G1A | Mecc Alte | ECO28-SN/4 | 600 | Delta | DPS 2400B-48-5 | 250 | Coslight | 400 | 2 | 400 | 24 | N/A | N/A | N/A | NA | N/A | 35 |  | 1 | MTN | T0065 | 0 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_018M
761 | T0048 | IHS_STR_019M | Kazungula | 25.286 | -17.7652 | Southern | 2.5 | SOUTHERN | KAZUNGULA | Yes | No | No | Rural | 2G 3G | P2 | BTS | BB | On air | Grid-Gen | Green Field | 46 | Indoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GU51790U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Delta | DPS 2400B-48-5 | 250 | Amaron | 600 | 2 | 600 | 24 | window/LG | window/LG | 18000 | 18000 | 2 | 89 |  | 2 | MTNParatus Telecom | T0048 | 0 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_019M
915 | T0141 | IHS_STR_020M | Lupani | 25.2633 | -17.7231 | Southern | 2 | SOUTHERN | KAZUNGULA | Yes | No | No | Rural | 2G | P4 | BB | BTS | On air | Grid-Gen | Green Field | 70 | Indoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 17.5 | Yanmar | 4TNE88-G1A | Mecc Alte | ECO28-SN/4 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | window/LG | window/LG | 18000 | 18000 | 2 | 70 |  | 1 | MTN | T0141 | 0 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_020M
1802 | T0055 | IHS_STR_021M | Zimba | 26.2367 | -17.3098 | Southern | 2.5 | SOUTHERN | KALOMO | Yes | No | No | Suburban | 2G 3G | P4 | BB | BB | On air | Grid-Gen | Green Field | 60 | Indoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | IMG | IMG | 20 | perkins | GU51794U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | window/LG | window/LG | 18000 | 18000 | 2 | 52 |  | 2 | MTNParatus Telecom | T0055 | 0 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_021M
1051 | T0110 | IHS_STR_022M | Mayoba Zimba | 26.2683 | -17.2278 | Southern | 1.8 | SOUTHERN | KALOMO | Yes | No | No | Rural | 2G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Outdoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | Yanmar | 3TNE88-G1A | Mecc Alte | ECO28-SN/4 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | NA | N/A | 74 |  | 2 | MTNAirtel | T0110 | ZM3588 | Yes |  |  | Palisade | Inala | 2022-08-05 | Yes | No |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_022M
559 | T0047 | IHS_STR_023M | Kalomo | 26.4823 | -17.027 | Southern | 5.5 | SOUTHERN | KALOMO | Yes | No | No | Suburban | 2G 3G | P3 | BB | BTS | On air | Grid-Gen | Green Field | 70 | Indoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 45 | perkins | 0 | Mecc Alte | ECO28-SN/4 | 1000 | Power cube | ICC330-H1_C1 | 600 | Lithium | 300 | 48 | 100 | 3 | window/LG | window/LG | 18000 | 18000 | 2 | 160 |  | 2 | MTNAirtel | T0047 | ZM0674 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | yes |  |  | yes | 30 |  | Pending |  |  |  |  | IHS_STR_023M
1230 | T0114 | IHS_STR_024M | Mukwela | 26.6547 | -17.0311 | Southern | 1.5 | SOUTHERN | CHOMA | Yes | No | No | Rural | 2G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Outdoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 13 | Yanmar | 3TNE88 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 63 |  | 2 | MTNAirtel | T0114 | ZM3799 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_STR_024M
1728 | T0158 | IHS_STR_025M | Tara | 26.7846 | -16.9552 | Southern | 2.5 | SOUTHERN | KALOMO | Yes | No | No | Rural | 2G | P4 | BB | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GV51790U | Leroy Sommer | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 28 |  | 1 | MTN | T0158 | 0 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_025M
936 | T0074 | IHS_STR_026M | Maamba | 27.2286 | -17.3401 | Southern | 1.5 | SOUTHERN | SINAZONGWE | Yes | No | No | Rural | 2G 3G 4G | P2 | BTS | Hub | On air | Grid-Gen | Green Field | 66 | Indoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 13 | Yanmar | 4TNE88 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 82 |  | 1 | MTN | T0074 | 0 | Yes |  |  | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | Done | 2019-06-06 | No | No | yes |  |  | Pending | n/a |  | Pending |  |  |  |  | IHS_STR_026M
294 | T0337 | IHS_STR_027M | Choma South | 26.9536 | -16.8322 | Southern | 2 | SOUTHERN | CHOMA | Yes | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | perkins | WP2_1D18E2 | Xingnou | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Shoto | 400 | 2 | 400 | 24 | N/A | N/A | N/A | 0 | N/A | 78 |  | 2 | MTNAirtel | T0337 | ZM0418 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | yes |  |  | Pending | n/a |  | Pending |  |  |  |  | IHS_STR_027M
288 | T0008 | IHS_STR_028M | Choma | 26.9818 | -16.8154 | Southern | 65 | SOUTHERN | CHOMA | Yes | Yes | No | Urban | 2G 3G | P2 | BB | BB | On air | Grid-Gen | Green Field | 70 | Indoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 65 | perkins | GU51798U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | Powercube | 400 | Lithium | 700 | 48 | 100 | 7 | LG | LG | 18000 | 18000 | 2 | 280 |  | 4 | MTNAirtelINQLiquid Telecom | T0008 | ZM3128 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | yes - Emergency | 45 | 43657 | closed |  |  |  |  | IHS_STR_028M
291 | T0336 | IHS_STR_029M | Choma North | 26.9921 | -16.7958 | Southern | 2.5 | SOUTHERN | CHOMA | Yes | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GV83540R | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 107 |  | 3 | MTNAirtelLiquid Telecom | T0336 | ZM0222 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | yes |  |  | Pending | n/a |  | Pending |  |  |  |  | IHS_STR_029M
1457 | T0077 | IHS_STR_030M | Njase | 26.9919 | -16.7733 | Southern | 2.5 | SOUTHERN | CHOMA | No | No | No | Urban | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GV51790V | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Delta | DPS 2400B-48-5 | 250 | Amaron | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 88 |  | 3 | MTNAirtelParatus Telecom | T0077 | ZM6889 | Yes |  |  | Palisade | Inala | 2022-08-05 | Yes | No |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_030M
1062 | T0097 | IHS_STR_031M | Mbabala | 26.9556 | -16.5526 | Southern | 1.5 | SOUTHERN | NAMWALA | No | No | No | Rural | 2G | P4 | BB | BTS | On air | Grid-Gen | Green Field | 66 | Outdoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 13 | Yanmar | 4TNE88 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Amaron | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 32 |  | 1 | MTN | T0097 | 0 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | yes |  |  | Pending | n/a |  | Pending |  |  |  |  | IHS_STR_031M
1660 | T0119 | IHS_STR_032M | Sinazeze | 27.41 | -17.15 | Southern | 1.5 | SOUTHERN | SINAZONGWE | Yes | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 66 | Outdoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Earth Technology | Earth technology | 10 | perkins | GU51794U | Leroy Sommer | 0 | 500 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 80 |  | 2 | MTNAirtel | T0119 | ZM0280 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_032M
1661 | T0054 | IHS_STR_033M | Sinazongwe | 27.4578 | -17.2618 | Southern | 2.5 | SOUTHERN | SINAZONGWE | No | No | No | Rural | 2G 3G | P4 | HUB | BB | On air | Grid-Gen | Green Field | 54 | Indoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GU51794U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 37 |  | 1 | MTN | T0054 | 0 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_033M
1615 | T0122 | IHS_STR_034M | Shamuleya Sinazongwe | 27.3129 | -16.9439 | Southern | 2.5 | SOUTHERN | SINAZONGWE | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Solar-Gen | Green Field | 70 | Outdoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Vitalgen | Vitalgen | 20 | perkins | GU51798U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | Powercube | 400 | Lithium | 500 | 48 | 100 | 5 | N/A | N/A | N/A | 0 | N/A | 95 |  | 2 | MTNAirtel | T0122 | ZM6587 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_034M
32 | T0064 | IHS_STR_035M | Batoka Choma | 27.2511 | -16.7686 | Southern | 2 | SOUTHERN | CHOMA | Yes | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Indoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Amaron | 600 | 2 | 600 | 24 | Gree | Gree | 18000 | 18000 | 2 | 25 |  | 1 | MTN | T0064 | 0 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_035M
1317 | T0391 | IHS_STR_036M | Muzoka Choma | 27.3132 | -16.6841 | Southern | 1.5 | SOUTHERN | CHOMA | Yes | No | No | Rural | 2G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | MPI | MPI | 10 | perkins | 0 | Leroy Sommer | TAL 040F J 6S/4 | 600 | Delta | DPS 2400B-48-5 | 250 | Agisson | 400 | 2 | 400 | 24 | N/A | N/A | N/A | 0 | N/A | 32 |  | 1 | MTN | T0391 | 0 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_036M
1012 | T0045 | IHS_STR_037M | Mapanza Namwala | 26.9083 | -16.2559 | Southern | 1.5 | SOUTHERN | NAMWALA | Yes | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 66 | Outdoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 13 | Yanmar | 4TNE88 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Amaron | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 34.8 |  | 1 | MTN | T0045 | 0 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_037M
1525 | T0052 | IHS_STR_038M | Pemba Choma | 27.3681 | -16.5154 | Southern | 2 | SOUTHERN | CHOMA | Yes | No | No | Rural | 2G 3G | P4 | BB | BTS | On air | Grid-Gen | Green Field | 70 | Indoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | Yanmar | 4TNE88 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Amaron | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 42 |  | 1 | MTN | T0052 | 0 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_038M
442 | T1009 | IHS_STR_039M | Ithezhi Thezhi | 26.0252 | -15.741 | Lusaka | 2 | SOUTHERN | ITHEZI-TEZHI | No | No | No | Rural | 2G 3G | P3 | BTS | BB | On air | Grid-Gen | Green Field | 50 | Indoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88-G1A | Mecc Alte | ECO28-1LN/4 | 600 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 58 |  | 1 | MTN | T1009 | 0 | YES |  | Working | Palisade | Inala | 2022-08-05 | Yes | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_039M
1327 | T0116 | IHS_STR_040M | Mwangwe | 26.9182 | -15.9878 | Southern | 2 | SOUTHERN | NAMWALA | No | No | No | Rural | 2G | P4 | BTS | BB/HUB | On air | Grid-Gen | Green Field | 80 | Indoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 81 |  | 2 | MTNAirtel | T0116 | ZM6586 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_040M
1747 | T0125 | IHS_STR_041M | Tuunga | 26.5719 | -15.8275 | Southern | 2 | SOUTHERN | NAMWALA | No | No | No | Rural | 2G | P4 | BTS | BB | On air | Grid-Gen | Green Field | 70 | Outdoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88 | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Amaron | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 65 |  | 2 | MTNAirtel | T0125 | ZM6588 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_041M
261 | T0089 | IHS_STR_042M | Chisekesi Monze | 27.4792 | -16.4292 | Southern | 2 | SOUTHERN | MONZE | Yes | No | No | Rural | 2G 3G | P4 | BB | BTS | On air | Grid-Gen | Green Field | 54 | Indoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | perkins | 0 | Mecc Alte | ECO28-SN/4 | 600 | Delta | DPS 2400B-48-5 | 250 | Lithium | 200 | 48 | 100 | 2 | LG | LG | 18000 | 18000 | 2 | 106 |  | 2 | MTNAirtel | T0089 | ZM3587 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_042M
1381 | T0051 | IHS_STR_043M | Namwala | 26.4359 | -15.7463 | Southern | 2.5 | SOUTHERN | NAMWALA | No | No | No | Suburban | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 46 | Indoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | IMG | Gen Logic | 20 | perkins | GV51790U | Leroy Sommer | TAL 040F J 6S/4 | 500 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | Gree | Gree | 18000 | 18000 | 2 | 46 |  | 1 | MTN | T0051 | 0 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_043M
395 | T0063 | IHS_STR_044M | Gwembe | 27.603 | -16.4977 | Southern | 2 | SOUTHERN | GWEMBE | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 66 | Indoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88 | Mecc Alte | ECO28-SN/4 | 600 | Delta | DPS 2400B-48-5 | 250 | Amaron | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 27 |  | 1 | MTN | T0063 | 0 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_044M
1580 | T0276 | IHS_STR_045M | Rusangu Monze | 27.5225 | -16.3801 | Southern | 1.8 | SOUTHERN | MONZE | Yes | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | IMG | Gen Logic | 15 | perkins | 3TNV76-GPGE | LINZ | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 50 |  | 1 | MTN | T0276 | 0 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_045M
478 | T0139 | IHS_STR_046M | Kabulamwanda | 26.8714 | -15.869 | Southern | 1.5 | SOUTHERN | NAMWALA | No | No | No | Rural | 2G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 42 | Outdoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Generator City | Generator City | 12 | Yanmar | 3TNE88-G1A | LINZ | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | Amaron | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 50 |  | 1 | MTN | T0139 | 0 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_046M
457 | T0242 | IHS_STR_047M | Kaanzwa | 26.079 | -15.6289 | Lusaka | 2.5 | SOUTHERN | ITHEZI-TEZHI | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Joseph Mulenga | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 403A-15 | Mecc Alte | ECP-28-M/4 | 1000 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 30 |  | 1 | MTN | T0242 | 0 | N0 |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_047M
1137 | T0339 | IHS_STR_048M | Monze south | 27.4731 | -16.2916 | Southern | 2.5 | SOUTHERN | MONZE | Yes | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GU51798U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | Powercube | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 120 |  | 2 | MTNAirtel | T0339 | ZM0481 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_STR_048M
1133 | T0016 | IHS_STR_049M | Monze | 27.4747 | -16.2694 | Southern | 4.5 | SOUTHERN | MONZE | Yes | No | No | Suburban | 2G 3G | P2 | BB | BB | On air | Grid-Gen | Green Field | 80 | Indoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | GV51790 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | Powercube | 400 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 118 |  | 1 | MTN | T0016 | 0 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_049M
837 | T0258 | IHS_STR_050M | Lochnivar/Blue Lagoon | 27.2312 | -15.8604 | Southern | 2 | SOUTHERN | MONZE | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88 | Mecc Alte | ECO28-SN/4 | 600 | Delta | DPS 2400B-48-5 | 250 | Amaron | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 26 |  | 1 | MTN | T0258 | 0 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | yes |  |  | Pending | n/a |  | Pending |  |  |  |  | IHS_STR_050M
948 | T0088 | IHS_STR_051M | Magoye Mazabuka | 27.605 | -16 | Southern | 4.5 | SOUTHERN | MAZABUKA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Himoisa | Himoisa | 30 | Yanmar | 4TNV98/B5576 | HIMOINSA | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 84 |  | 2 | MTNAirtel | T0088 | ZM3455 | 0 |  |  | Palisade | Inala | 2022-08-05 | Yes | No |  | 1 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_051M
1296 | T0046 | IHS_STR_053M | Musikili | 27.6409 | -15.8646 | Southern | 1.8 | SOUTHERN | MAZABUKA | No | No | No | Suburban | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Indoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Vitalgen | Vitalgen | 15 | perkins | GU51798U | Leroy Sommer | TAL 040F J 6/4 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 80 |  | 2 | MTNAirtel | T0046 | ZM9007 | 0 |  |  | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | Done | 2019-06-04 | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_053M
546 | T0202 | IHS_STR_054M | Kaleya | 27.6956 | -15.8811 | Southern | 2.5 | SOUTHERN | MAZABUKA | No | No | No | Suburban | 2G 3G | P3 | BTS | BB | On air | Grid-Gen | Green Field | 54 | Outdoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GU51798U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Delta | DPS 2400B-48-5 | 250 | Amaron | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 56.4 |  | 1 | MTN | T0202 | 0 | 0 |  |  | Palisade | Inala | 2022-08-05 | Yes | No |  |  |  |  | pending |  | No | No | yes |  |  | Pending | n/a |  | Pending |  |  |  |  | IHS_STR_054M
1055 | T0209 | IHS_STR_055M | Mazabuka BB | 27.7551 | -15.8846 | Southern | 2 | SOUTHERN | MAZABUKA | Yes | No | No | Urban | 2G 3G | P4 | BB | BTS | On air | Grid-Gen | Green Field | 70 | Indoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | GV51790U | Leroy Sommer | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 55 |  | 1 | MTN | T0209 | 0 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_055M
1060 | T0338 | IHS_STR_056M | Mazabuka Town Centre | 27.7511 | -15.8703 | Southern | 1.8 | SOUTHERN | MAZABUKA | Yes | No | No | Urban | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | 0 | 0 | 15 | perkins | GV51790R | Leroy Sommer | TAL 040F J 6S/4 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 105 |  | 2 | MTNAirtel | T0338 | ZM0226 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_056M
1054 | T0015 | IHS_STR_057M | Mazabuka | 27.7644 | -15.8647 | Southern | 4.5 | SOUTHERN | MAZABUKA | Yes | No | No | Urban | 2G 3G 4G | P2 | HUB | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | GN66044V | Mecc Alte | ECP28-1L/4 | 1000 | Delta | DPS 2400B-48-5 | 250 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 110 |  | 4 | MTNINQLiquid TelecomParatus Telecom | T0015 | 0 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | Done |  | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_057M
1270 | T0159 | IHS_STR_058M | Muninya | 28.0848 | -16.1614 | Southern | 2.5 | SOUTHERN | MAZABUKA | No | No | No | Suburban | 2G 3G | P4 | BB | BB | On air | Grid-Gen | Green Field | 70 | Indoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Vitalgen | Vitalgen | 20 | perkins | GU51798U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 46 |  | 1 | MTN | T0159 | 0 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_058M
165 | T0050 | IHS_STR_059M | Chikankata | 28.1437 | -16.229 | Southern | 1.8 | SOUTHERN | MAZABUKA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | GN65732V | Mecc Alte | 0 | 1000 | Delta | DPS 2400B-48-5 | 250 | Amaron | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 36 |  | 1 | MTN | T0050 | 0 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_059M
1259 | T0115 | IHS_STR_060M | Munali Hills | 28.01 | -16.0289 | Southern | 1.5 | SOUTHERN | MAZABUKA | Yes | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Outdoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | CK Works | CK Works | 13 | Yanmar | 3TNE88 | Leroy Sommer | ECO28-SN/4 | 600 | Delta | DPS 2400B-48-5 | 250 | Amaron | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 35 |  | 1 | MTN | T0115 | 0 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | yes |  |  | Pending | n/a |  | Pending |  |  |  |  | IHS_STR_060M
865 | T0194 | IHS_STR_061M | Lubombo | 27.8777 | -15.8642 | Southern | 2 | SOUTHERN | MAZABUKA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | perkins | 4TNE88 | Mecc Alte | 0 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 89 |  | 2 | MTNAirtel | T0194 | ZM6878 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_061M
1425 | T0315 | IHS_STR_063M | Neganega | 28.0226 | -15.832 | Southern | 1.8 | SOUTHERN | MAZABUKA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 70 | Outdoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | IMG | IMG | 15 | perkins | GU51794U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 84 |  | 2 | MTNAirtel | T0315 | ZM6790 | 0 |  |  | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 2 |  |  | Done | 2019-06-17 | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_063M
1642 | T0316 | IHS_STR_065M | Siavonga Uranium | 28.4983 | -16.3221 | Lusaka | 1.8 | SOUTHERN | SIAVONGA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Solar-Gen | Green Field | 70 | Outdoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Falcon | Falcon | 15 | perkins | 403A-15 | Leroy Sommer | LSA 40M5 C 6/4 | 600 | Power cube | Huawei | 200 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 51 |  | 1 | MTN | T0316 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  | Consolidated IHS_STR_259A | IHS_STR_065M
1638 | T0024 | IHS_STR_066M | Siavonga | 28.7144 | -16.5303 | Lusaka | 2 | SOUTHERN | SIAVONGA | No | No | No | Rural | 2G 3G | P4 | BB | BB | On air | Grid-Gen | Green Field | 36 | Indoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | LISTER PETTER | LISTER PETTER | 16 | Lister petter | LWP4 | Leroy Sommer | LSA 42.3VS2 J 6/4 | 600 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 89 |  | 1 | MTN | T0024 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_066M
1640 | T0200 | IHS_STR_067M | Siavonga Hajuma | 28.7336 | -16.4925 | Lusaka | 2 | SOUTHERN | SIAVONGA | No | No | No | Rural | 2G 3G | P4 | BB | BB | On air | Grid-Gen | Green Field | 25 | Indoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88-G1A | Mecc Alte | ECO28-1LN/4 | 1000 | IPT | DPR 2400B-48 | 250 | C&D True | 704 | 12 | 176 | 16 | GREE | GREE | 12000 | 12000 | 2 | 47 |  | 1 | MTN | T0200 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_067M
682 | T0102 | IHS_STR_068M | Kariba | 28.7583 | -16.5144 | Lusaka | 1.5 | SOUTHERN | SIAVONGA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 48 | Outdoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 13 | Yanmar | 4TNE88-G1A | Leroy Sommer | LSC 28S2 | 600 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 38 |  | 2 | MTNLiquid Telecom | T0102 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_068M
925 | T0109 | IHS_STR_069M | Lusitu | 28.7533 | -16.1853 | Lusaka | 1.8 | SOUTHERN | SIAVONGA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Outdoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | GNM | GNM | 15 | perkins | 403A-22 | Leroy Sommer | TAL 040 DJ 6S/4 | 600 | IPT | DPR 2400B-48 | 250 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | N/A | N/A | 91 |  | 2 | MTNAirtel | T0109 | ZM3584 | NO |  | Working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_069M
249 | T0007 | IHS_STR_070M | Chirundu | 28.8256 | -16.0358 | Lusaka | 2.5 | SOUTHERN | SIAVONGA | Yes | No | No | Rural | 2G 3G | P3 | BB | BB | On air | Grid-Gen | Green Field | 70 | Indoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Vitalgen | Vitalgen | 20 | perkins | 404D-22 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | CHIGO | CHIGO | 18000 | 18000 | 2 | 82 |  | 3 | MTNAirtelTop Star | T0007 | ZM0014 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_070M
251 | T0092 | IHS_STR_071M | Chirundu Border | 28.8506 | -16.0333 | Lusaka | 4.5 | SOUTHERN | SIAVONGA | Yes | No | No | Rural | 2G 3G | P1 | HUB | HUB | On air | Grid-Gen | Green Field | 54 | Outdoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | DPR 2400B-48 | 600 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 190 |  | 4 | MTNAirtelINQParatus Telecom | T0092 | ZM0432 | N0 |  | No working | Palisade | Inala | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | Yes | No | Yes |  |  | Pending | 30 |  | Pending |  |  |  |  | IHS_STR_071M
250 | T0261 | IHS_STR_072M | Chirundu | 28.8689 | -15.98 | Lusaka | 1.5 | SOUTHERN | SIAVONGA | Yes | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Samuel Mumba | SBC | SBC | MTN | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 13 | Yanmar | 4TNE88-G1A | Mecc Alte | ECO28-1LN/4 | 1000 | IPT | DPR 2400B-48 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 36 |  | 1 | MTN | T0261 | 0 | NO |  | No working | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_072M
988 | T0361 | IHS_STR_073M | MAMBOVA | 25.1962 | -17.7315 | Southern | 1.5 | SOUTHERN | KAZUNGULA | Yes | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Outdoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Generator city | Generator city | 12 | Yanmar | 3TNV88 | ALPHAGEN | SLG164 | 600 | Delta | DPS 2400B-48-5 | 250 | Amaron | 600 | 2 | 600 | 24 | N/A | N/A | N/A | NA | N/A | 35 |  | 1 | MTN | T0361 | 0 | No |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_073M
1454 | T0416 | IHS_STR_074M | Nico Girls | 26.9193 | -16.0893 | Southern | 1.5 | SOUTHERN | NAMWALA | No | No | No | Rural | 2G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 55 | Outdoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | MPI | MPI | 10 | perkins | GK65597R | Leroy Sommer | TAL 040F J 6S/4 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 32 |  | 1 | MTN | T0416 | 0 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_074M
1276 | T0432 | IHS_STR_075M | Munyumbwe | 27.7833 | -16.65 | Southern | 1.8 | SOUTHERN | GWEMBE | No | No | No | Rural | 2G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 75 | Outdoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | MPL | MPL | 15 | perkins | MPLS13S-1NS | Leroy Sommer | TAL 040F J 6S/4 | 600 | Delta | DPS 2400B-48-5 | 250 | Amaron | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 76 |  | 2 | MTNAirtel | T0432 | ZM0275 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_075M
1277 | T0434 | IHS_STR_076M | Munyumbwe RPT | 27.6288 | -16.5202 | Southern | 1.5 | WESTERN | MONGU | No | No | No | Rural | 2G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 75 | Outdoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | MPI | MPI | 10 | perkins | GK65597R | Leroy Sommer | TAL 040F J 6S/4 | 600 | Delta | DPS 2400B-48-5 | 250 | Wolong | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 25 |  | 1 | MTN | T0434 | 0 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_076M
733 | T0423 | IHS_STR_077M | Katombora Prison | 25.3937 | -17.8355 | Southern | 1.8 | SOUTHERN | KAZUNGULA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 55 | Outdoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | IMG | IMG | 15 | perkins | GU51790U | Leroy Sommer | LSA 40M5 J 6/4 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | NA | N/A | 62 |  | 2 | MTNAirtel | T0423 | ZM0103 | No |  |  | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | Done | 2019-06-04 | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_077M
1635 | T0415 | IHS_STR_079M | Siankaba Islands | 25.5742 | -17.8355 | Southern | 1.5 | SOUTHERN | KAZUNGULA | No | No | No | Rural | 2G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 55 | Outdoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | MPI | MPI | 10 | perkins | GK65597R | Leroy Sommer | LSA 40M5 J 6/4 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | NA | N/A | 34 |  | 1 | MTN | T0415 | 0 | Yes |  |  | Palisade | Inala | 2022-08-05 | Yes | No |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_079M
699 | T0425 | IHS_STR_080M | Kasenga Girls School | 26.8 | -15.8667 | Southern | 2 | SOUTHERN | NAMWALA | No | No | No | Urban | 2G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 55 | Outdoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | perkins | GV51790U | Mecc Alte | ECP28-1L/4 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 23.5 |  | 1 | MTN | T0425 | 0 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_080M
1135 | T1181 | IHS_STR_081M | Monze Overspill | 27.461 | -16.2867 | Southern | 2.5 | SOUTHERN | Monze | No | No | No | Urban | P4 | P4 | BTS | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GV83540U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | Powercube | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 46 |  | 1 | MTN | T1181 | 0 | 0 |  |  | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_081M
938 | T0326 | IHS_STR_084M | Maamba Town 2 | 27.2144 | -17.3582 | Southern | 2.5 | SOUTHERN | Mamba | Yes | No | No | Urban | P4 | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GV83540U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | Powercube | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 27 |  | 1 | MTN | T1186 | 0 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_084M
296 | T1193 | IHS_STR_088M | Choma WT Airtel Share | 26.9891 | -16.8038 | Southern | 2.5 | SOUTHERN | Choma | Yes | No | No | Urban | P4 | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Aaron Ikenda | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GV83540U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | Powercube | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 89 |  | 2 | MTNAirtel | T1193 | ZM0016 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_088M
649 | ZM0034 | IHS_STR_201A | Kanyemeza | 26.5707 | -17.0509 | Southern | 2 | SOUTHERN | Kalomo | Yes | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 64 | Indoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | perkins | GV51790V | Mecc Alte | ECP28-1L/4 | 1000 | Power cube | Powercube | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 84 |  | 1 | Airtel | 0 | ZM0034 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_201A
832 | ZM0047 | IHS_STR_202A | Livingstone Airport | 25.819 | -17.8261 | Southern | 2.5 | SOUTHERN | Livingstone | Yes | No | No | Urban | Gold | Gold | BTS | BTS | On air | Grid-Gen | Roof Top | RT | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GV51790U | Mecc Alte | ECP 28-M/4 | 1000 | Power cube | ICC330-H1_C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | 0 | NA | 0 | 90 |  | 1 | Airtel | 0 | ZM0047 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_202A
834 | ZM0048 | IHS_STR_203A | Livingstone Sun | 25.8699 | -17.9189 | Southern | 2.5 | SOUTHERN | Livingstone | Yes | No | No | Urban | Gold | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 35 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GV51790U | Mecc Alte | ECP 28-M/4 | 1000 | Power cube | ICC330-H1_C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | 0 | NA | 0 | 45 |  | 1 | Airtel | 0 | ZM0048 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_203A
1063 | ZM0054 | IHS_STR_204A | Mbabala (Choma Backbone) | 26.9154 | -16.8202 | Southern | 5.5 | SOUTHERN | Choma | No | No | No | Urban | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 66 | Indoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 45 | perkins | DK32037 | Leroy Sommer | TAL042F | 600 | Power cube | Powercube | 400 | Lithium | 800 | 48 | 100 | 8 | LG | LG | 18000 | 18000 | 2 | 240 |  | 2 | MTNAirtel | T0226 | ZM0054 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_204A
1057 | ZM0057 | IHS_STR_205A | Mazabuka BB | 27.7549 | -15.8853 | Southern | 4.5 | SOUTHERN | Mazabuka | No | No | No | Urban | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 70 | Indoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | DJ51434 | Leroy Sommer | 0 | 600 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 106.3 |  | 1 | Airtel | 0 | ZM0057 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_205A
1136 | ZM0060 | IHS_STR_206A | Monze Silo | 27.4757 | -16.2656 | Southern | 1.5 | SOUTHERN | Monze | Yes | No | No | Suburban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Roof Top | RT | Indoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 10 | perkins | GV51790U | Mecc Alte | ECP28-M/4 | 1000 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 87 |  | 1 | Airtel | 0 | ZM0060 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_206A
1524 | ZM0072 | IHS_STR_207A | Pemba | 27.3691 | -16.5147 | Southern | 4.5 | SOUTHERN | Choma | Yes | No | No | Suburban | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 64 | Indoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | DJ51434 | Mecc Alte | TAL 040F J 6S/4 | 1000 | Power cube | PowerCube | 400 | Lithium | 200 | 48 | 100 | 2 | LG | LG | 18000 | 18000 | 2 | 89 |  | 1 | Airtel | 0 | ZM0072 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_207A
1776 | ZM0077 | IHS_STR_208A | SIAVONGA | 28.7156 | -16.5318 | Lusaka | 4.5 | SOUTHERN | Siavonga | No | No | No | Rural | Silver | Silver | HUB | HUB | On air | Grid-Gen | Green Field | 50 | Indoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 68 |  | 2 | AirtelLiquid( Former Hai) | 0 | ZM0077 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_208A
1803 | ZM0083 | IHS_STR_209A | Zimba | 26.247 | -17.3302 | Southern | 2.5 | SOUTHERN | Kazungula | Yes | No | No | Rural | Silver | Silver | BB | BTS | On air | Grid-Gen | Green Field | 64 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Vitalgen | Vitalgen | 20 | perkins | GV51790U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | ICC330-H1_C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 18000 | N/A | 52 |  | 1 | Airtel | 0 | ZM0083 | Yes |  |  | Mesh | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_209A
762 | ZM0102 | IHS_STR_210A | Kazungula | 25.2691 | -17.7865 | Southern | 4.5 | SOUTHERN | Kazungula | Yes | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Indoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | GV51790U | 0 | 0 | 1000 | Power cube | ICC330-H1_C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | window/LG | window/LG | 18000 | 18000 | 2 | 75 |  | 2 | MTNAirtel | T1188 | ZM0102 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_210A
523 | ZM0104 | IHS_STR_211A | KAFUE MAZABUKA | 28.0529 | -16.0274 | Southern | 1.8 | SOUTHERN | Mazabuka | Yes | No | No | Suburban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 70 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | IMG | IMG | 15 | perkins | GU51794U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 80 |  | 2 | MTNAirtel | T0428 | ZM0104 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_211A
833 | ZM0121 | IHS_STR_212A | Livingstone Relief | 25.8556 | -17.8488 | Southern | 2 | SOUTHERN | Livingstone | Yes | No | No | Urban | Gold | Gold | BTS | BTS | On air | Grid-Gen | Roof Top | RT | Indoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Up Time | Up Time | 16 | Lister petter | LPW4 A27 | Marelli | MJB 160 MA4 | 600 | Power cube | TP48200A | 200 | NARADA | 600 | 2 | 600 | 24 | window/LG | window/LG | 18000 | 18000 | 2 | 80 |  | 1 | Airtel | 0 | ZM0121 | yes |  |  | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | pending |  | Yes | No | yes |  |  | Pending | n/a |  | Pending |  |  |  |  | IHS_STR_212A
166 | ZM0150 | IHS_STR_213A | CHIKANKATA | 28.1438 | -16.2327 | Southern | 1.8 | SOUTHERN | Siavonga | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | 0 | 0 | 15 | perkins | GU51784V | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 44 |  | 1 | Airtel | 0 | ZM0150 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_213A
342 | ZM0151 | IHS_STR_214A | DUNDU | 28.0849 | -16.1627 | Southern | 2.5 | SOUTHERN | Mazabuka | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 70 | Indoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | MPI | MPI | 20 | perkins | GU51790R | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | star energy | star energy | 25000 | 25000 | 2 | 64 |  | 1 | Airtel | 0 | ZM0151 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_214A
937 | ZM0154 | IHS_STR_215A | Maamba | 27.2285 | -17.3419 | Southern | 1.8 | SOUTHERN | Sinazongwe | Yes | No | No | Urban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 56 | Indoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | IMG | IMG | 15 | perkins | GU51794U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | Powercube | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 76 |  | 1 | Airtel | 0 | ZM0154 | Yes |  |  | Palisade | Inala | 2022-08-05 | Yes | No |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_215A
1662 | ZM0160 | IHS_STR_216A | Sinazongwe | 27.458 | -17.2626 | Southern | 2.5 | SOUTHERN | Sinazongwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Vitalgen | Vitalgen | 20 | perkins | GU51798U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Emerson | 0 | 250 | NARADA | 600 | 2 | 600 | 24 | star energy | star energy | 25000 | 25000 | 2 | 70 |  | 1 | Airtel | 0 | ZM0160 | Yes |  |  | Palisade | Inala | 2022-08-05 | Yes | No |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_216A
441 | ZM0181 | IHS_STR_217A | Itezhitezhi | 26.0319 | -15.7326 | Southern | 1.8 | SOUTHERN | Namwala | No | No | No | Rural | Silver | Silver | HUB | HUB | On air | Grid-Gen | Green Field | 50 | Indoor | John Banda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Earth Technology | Earth technology | 15 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 600 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 84 |  | 1 | Airtel | 0 | ZM0181 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_217A
1382 | ZM0201 | IHS_STR_218A | Namwala | 26.4251 | -15.7656 | Southern | 1.8 | SOUTHERN | Namwala | No | No | No | Suburban | Silver | Silver | BB | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | IMG | IMG | 15 | perkins | GU51794U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | star energy | star energy | 25000 | 25000 | 2 | 67 |  | 1 | Airtel | 0 | ZM0201 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_218A
172 | ZM0212 | IHS_STR_219A | Chikuni | 27.5466 | -16.4252 | Southern | 1.8 | SOUTHERN | Choma | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | IMG | IMG | 15 | perkins | GU51794U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 65 |  | 2 | MTNAirtel | T0188 | ZM0212 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_219A
935 | ZM0234 | IHS_STR_220A | Maala | 26.7483 | -15.7414 | Southern | 1.8 | SOUTHERN | Itezhi-Tezhi | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 80 | Indoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | 0 | 0 | 15 | perkins | GN83012V | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 74 |  | 2 | MTNAirtel | T0187 | ZM0234 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_220A
1637 | ZM0520 | IHS_STR_222A | Siaskabole (Sinazeze West) | 27.0467 | -17.1217 | Southern | 2 | SOUTHERN | Choma | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 48 | Indoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | perkins | GV51790U | Leroy Sommer | 0 | 1000 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 69 |  | 2 | MTNAirtel | T0466 | ZM0520 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_222A
1667 | ZM0529 | IHS_STR_223A | Sipatunyana | 26.5863 | -17.1875 | Southern | 2.5 | SOUTHERN | Kalomo | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 52 | Indoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GV51790U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | TP48200A | 200 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 79 |  | 2 | MTNAirtel | T0464 | ZM0529 | no |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_223A
1035 | ZM0592 | IHS_STR_224A | Masuku | 27.0935 | -17.2749 | Southern | 1.8 | SOUTHERN | Choma | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 60 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | 0 | 0 | 15 | perkins | GU51794U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 18000 | N/A | 68 |  | 2 | MTNAirtel | T0457 | ZM0592 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_224A
1240 | ZM0594 | IHS_STR_225A | Mulobezi Road | 25.1093 | -17.1198 | Southern | 2.5 | SOUTHERN | Kazungula | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Solar-Gen | Green Field | 80 | Indoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GU51790U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | TP48300/A 100A | 300 | Lithium | 200 | 48 | 100 | 2 | LG | LG | 18000 | 18000 | 2 | 32 |  | 1 | Airtel | 0 | ZM0594 | NO |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | yes |  |  | Pending | n/a |  | Pending |  |  |  |  | IHS_STR_225A
396 | ZM0618 | IHS_STR_226A | Gwembe | 27.61 | -16.5058 | Southern | 1.8 | SOUTHERN | Choma | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | IMG | IMG | 15 | perkins | GU51794U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 46 |  | 1 | Airtel | 0 | ZM0618 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_226A
1138 | ZM0623 | IHS_STR_227A | Monze South | 27.4949 | -16.3181 | Southern | 2.5 | SOUTHERN | Monze | No | No | No | Suburban | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 80 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Vitalgen | Vitalgen | 30 | perkins | 0 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 18000 | N/A | 120 |  | 2 | MTNAirtel | T1180 | ZM0623 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_227A
547 | ZM0685 | IHS_STR_229A | Kaleya | 27.6725 | -15.869 | Southern | 1.8 | SOUTHERN | Mazabuka | No | No | No | Suburban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Vitalgen | Vitalgen | 15 | perkins | GU51798U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 47 |  | 1 | Airtel | 0 | ZM0685 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_229A
279 | ZM0695 | IHS_STR_230A | Chitongo | 26.936 | -16.0391 | Southern | 4.5 | SOUTHERN | Itezhi-Tezhi | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 80 | Indoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | DJ51434 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 73 |  | 2 | AirtelTop Star | 0 | ZM0695 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_230A
1013 | ZM0696 | IHS_STR_231A | Mapatizya Mine | 26.897 | -17.7024 | Southern | 2.5 | SOUTHERN | Sinazongwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 80 | Indoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GK65597R | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ICC330-H1_C1 | 600 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 67 |  | 2 | MTNAirtel | T0248 | ZM0696 | No |  |  | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_231A
1350 | ZM0713 | IHS_STR_232A | Nakambala | 27.752 | -15.8532 | Southern | 1.8 | SOUTHERN | Mazabuka | Yes | No | No | Urban | Silver | Silver | HUB | BTS | On air | Grid-Gen | Green Field | 30 | Indoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | IMG | IMG | 15 | perkins | GU51794U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | star energy | star energy | 25000 | 25000 | 2 | 159 |  | 2 | MTNAirtel | T0314 | ZM0713 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_232A
1225 | ZM0725 | IHS_STR_233A | Mukuni | 25.9395 | -17.9054 | Southern | 2.5 | SOUTHERN | Kazungula | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Vitalgen | Vitalgen | 20 | perkins | GV51790U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | ICC330-H1_C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | window/LG | window/LG | 18000 | 18000 | 2 | 71 |  | 2 | MTNAirtel | T0189 | ZM0725 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_233A
535 | ZM0728 | IHS_STR_234A | Kala Ranch (Mapatiziya North) | 26.8666 | -17.32 | Southern | 1.8 | SOUTHERN | Kalomo | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 52 | Indoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Earth Technology | Earth technology | 15 | perkins | GV51790U | Leroy Sommer | LSA 40M5 J 6/4 | 600 | Power cube | ICC330-H1_C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | window/LG | window/LG | 18000 | 18000 | 2 | 60 |  | 2 | MTNAirtel | T0463 | ZM0728 | no |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_234A
1064 | ZM0768 | IHS_STR_235A | Mbabala Town | 26.955 | -16.5628 | Southern | 1.8 | SOUTHERN | Choma | No | No | No | Suburban | Silver | Silver | BB | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | Lister petter | 0 | Leroy Sommer | LSA 42.2S4J6/4 | 600 | Power cube | PowerCube | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 46 |  | 1 | Airtel | 0 | ZM0768 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_235A
295 | ZM0773 | IHS_STR_236A | Choma Town | 26.9641 | -16.8197 | Southern | 2.5 | SOUTHERN | Choma | Yes | No | No | Urban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GU51794U | Mecc Alte | TAL 040F J 6S/4 | 1000 | Power cube | PowerCube | 400 | Agisson | 600 | 2 | 600 | 24 | star energy | star energy | 25000 | 25000 | 2 | 136 |  | 2 | MTNAirtel | T1191 | ZM0773 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_236A
31 | ZM0776 | IHS_STR_237A | Batoka | 27.2483 | -16.7737 | Southern | 1.8 | SOUTHERN | Choma | No | No | No | Suburban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | Lister petter | 0 | Leroy Sommer | LSA 42.2S4J6/4 | 600 | Power cube | PowerCube | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 78 |  | 1 | Airtel | 0 | ZM0776 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | yes |  |  | Pending | n/a |  | Pending |  |  |  |  | IHS_STR_237A
1020 | ZM0806 | IHS_STR_238A | Maramba | 25.8697 | -17.8473 | Southern | 2.5 | SOUTHERN | Livingstone | Yes | No | No | Urban | Gold | Gold | HUB | BTS | On air | Grid-Gen | Green Field | 36 | Indoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Vitalgen | Vitalgen | 20 | perkins | GV51790U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | ICC330-H1_C1 | 400 | Lithium | 200 | 48 | 100 | 2 | window/LG and sumsung | window/LG and sumsung | 18000 | 18000 | 2 | 90 |  | 1 | Airtel | 0 | ZM0806 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_238A
824 | ZM0807 | IHS_STR_239A | Linda | 25.8541 | -17.8698 | Southern | 2.5 | SOUTHERN | Livingstone | Yes | No | No | Urban | Gold | Gold | HUB | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GV51790U | Mecc Alte | ECP 28-M/4 | 1000 | Power cube | ICC330-H1_C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 18000 | N/A | 67 |  | 2 | AirtelLiquid Telecom | 0 | ZM0807 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_239A
940 | ZM0827 | IHS_STR_240A | Macha Mission | 26.7981 | -16.3975 | Southern | 2 | SOUTHERN | Choma | No | No | No | Rural | Silver | Silver | BB | BTS | On air | Grid-Gen | Green Field | 80 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88 | Leroy Sommer | 0 | 600 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 76 |  | 2 | MTNAirtel | T0191 | ZM0827 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_240A
1636 | ZM0828 | IHS_STR_241A | Siansowa | 27.3725 | -17.4553 | Southern | 1.8 | SOUTHERN | Sinazongwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | IMG | IMG | 15 | perkins | GU51794U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 78 |  | 2 | MTNAirtel | T0286 | ZM0828 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_241A
751 | ZM0859 | IHS_STR_242A | Kawama Southern | 27.7899 | -15.8135 | Southern | 1.8 | SOUTHERN | Mazabuka | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | IMG | IMG | 15 | perkins | GU51794U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | star energy | star energy | 25000 | 25000 | 2 | 82 |  | 2 | MTNAirtel | T0186 | ZM0859 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_242A
1011 | ZM0872 | IHS_STR_243A | Mapanza | 26.9027 | -16.2435 | Southern | 1.8 | SOUTHERN | Choma | No | No | No | Rural | Silver | Silver | BB | BTS | On air | Grid-Gen | Green Field | 70 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | IMG | IMG | 15 | perkins | GU51794U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | PowerCube | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 52 |  | 1 | Airtel | 0 | ZM0872 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_243A
1783 | ZM0879 | IHS_STR_244A | KAFUE RIVERSIDE | 28.2573 | -15.8289 | Lusaka | 2.5 | SOUTHERN | Mazabuka | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | MPMC | MPMC | 20 | perkins | 403D-15T | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 63 |  | 1 | Airtel | 0 | ZM0879 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_244A
448 | ZM3129 | IHS_STR_246A | Jembo | 27.4703 | -16.6022 | Southern | 1.8 | SOUTHERN | Choma | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Vitalgen | Vitalgen | 15 | perkins | GU51798U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 45 |  | 1 | Airtel | 0 | ZM3129 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_246A
1804 | ZM3164 | IHS_STR_247A | Zimba Town | 26.2003 | -17.3176 | Southern | 2.5 | SOUTHERN | Kazungula | Yes | No | No | Suburban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 40 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GU51790U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ICC330-H1_C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | NA | N/A | 60 |  | 2 | MTNAirtel | T0368 | ZM3164 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_STR_247A
1655 | ZM3217 | IHS_STR_248A | Simonga | 25.6291 | -17.7866 | Southern | 2.5 | SOUTHERN | Livingstone | Yes | No | No | Rural | Silver | Silver | BTS | BB/HUB | On air | Grid-Gen | Green Field | 60 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GV51790U | Mecc Alte | ECP 28-M/4 | 1000 | Power cube | ICC330-H1_C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 18000 | N/A | 85 |  | 2 | MTNAirtel | T0192 | ZM3217 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_248A
1261 | ZM3218 | IHS_STR_249A | MUNALI NICKEL | 28.0454 | -15.9194 | Southern | 2.5 | SOUTHERN | Mazabuka | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | 0 | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 78 |  | 2 | MTNAirtel | T0115 | ZM3218 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_249A
1134 | ZM3340 | IHS_STR_250A | Monze Barclays | 27.4795 | -16.2765 | Southern | 4.5 | SOUTHERN | Monze | Yes | No | No | Suburban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | IMG | Vitalgen | 30 | perkins | GU51794U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 160 |  | 3 | MTNAirtelLiquid Telecom | T0215 | ZM3340 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_250A
1481 | ZM3343 | IHS_STR_251A | Nottie Broadie | 25.8688 | -17.842 | Southern | 2.5 | SOUTHERN | Livingstone | No | No | No | Urban | Gold | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GU51790U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ICC330-H1_C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | window/LG | window/LG | 18000 | 18000 | 2 | 122 |  | 2 | MTNAirtel | T1187 | ZM3343 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | yes |  |  | Pending | n/a |  | Pending |  |  |  |  | IHS_STR_251A
830 | ZM3346 | IHS_STR_252A | Livingstone 217 | 25.8542 | -17.8596 | Southern | 2.5 | SOUTHERN | Livingstone | Yes | No | No | Urban | Gold | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GU51790U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ICC330-H1_C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 18000 | N/A | 110 |  | 2 | MTNAirtel | T0256 | ZM3346 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | yes |  |  | Pending | n/a |  | Pending |  |  |  |  | IHS_STR_252A
916 | ZM3357 | IHS_STR_253A | Lupani | 25.2631 | -17.7219 | Southern | 2.5 | SOUTHERN | Kazungula | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 80 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | IMG | IMG | 20 | perkins | GV51790U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | ICC330-H1_C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | NA | N/A | 70 |  | 1 | Airtel | 0 | ZM3357 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_253A
1383 | ZM3408 | IHS_STR_254A | NANGA FAMRS | 27.9129 | -15.7861 | Southern | 1.8 | SOUTHERN | Mazabuka | No | No | No | Rural | Silver | Silver | BB | BTS | On air | Grid-Gen | Green Field | 40 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | IMG | IMG | 15 | perkins | GU51794U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 68 |  | 2 | MTNAirtel | T0267 | ZM3408 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_254A
1710 | ZM3410 | IHS_STR_255A | St. Raphaels | 25.8794 | -17.8316 | Southern | 2 | SOUTHERN | Livingstone | No | No | No | Urban | Gold | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 42 | Indoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88-G1A | Leroy Sommer | LSC 28S2 | 600 | Power cube | ICC330-H1_C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | window/LG | window/LG | 18000 | 18000 | 2 | 65 |  | 1 | Airtel | 0 | ZM3410 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_255A
328 | ZM3415 | IHS_STR_256A | Dambwa North | 25.842 | -17.8625 | Southern | 2.5 | SOUTHERN | Livingstone | Yes | No | No | Urban | Gold | Gold | HUB | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | IMG | IMG | 20 | perkins | GV51790U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | ICC330-H1_C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | window/LG | window/LG | 18000 | 18000 | 2 | 120 |  | 2 | MTNAirtel | T0352 | ZM3415 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_256A
326 | ZM3416 | IHS_STR_257A | Dambwa Central | 25.8414 | -17.8489 | Southern | 2.5 | SOUTHERN | Livingstone | Yes | No | No | Urban | Gold | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GU51790U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ICC330-H1_C1 | 400 | Agisson | 600 | 2 | 600 | 24 | window/LG | window/LG | 18000 | 18000 | 2 | 138 |  | 3 | MTNAirtelLiquid Telecom | T0353 | ZM3416 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | yes |  |  | Pending | n/a |  | Pending |  |  |  |  | IHS_STR_257A
674 | ZM3417 | IHS_STR_258A | Kapufi | 27.7397 | -15.8574 | Southern | 4.5 | SOUTHERN | Mazabuka | Yes | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | MPI | CK works | 30 | perkins | GK65597R | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 25000 | N/A | 130 |  | 2 | MTNAirtel | T0494 | ZM3417 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_258A
1784 | ZM3433 | IHS_STR_259A | SIAVONGA URANIUM MINE | 28.4944 | -16.3222 | Lusaka | 2.5 | SOUTHERN | Siavonga | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 70 | Outdoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-16 | Leroy Sommer | ECP-28-M/4 | 1000 | MPPT | MPPT | 225 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 51.2 |  | 1 | Airtel | 0 | ZM3433 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_STR_259A
1316 | ZM3434 | IHS_STR_260A | Muzoka | 27.3132 | -16.6839 | Southern | 2.5 | SOUTHERN | Choma | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 70 | Indoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Vitalgen | Vitalgen | 20 | perkins | GU51798U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 72 |  | 1 | Airtel | 0 | ZM3434 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_260A
331 | ZM3435 | IHS_STR_261A | David Livingstone hotel | 25.8483 | -17.8902 | Southern | 2.5 | SOUTHERN | Livingstone | Yes | No | No | Urban | Gold | Gold | BTS | BTS | On air | Solar-Gen | Green Field | 20 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GV51790U | Mecc Alte | ECP 28-M/4 | 1000 | Power cube | ICC330-H1_C1 | 600 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | NA | N/A | 90 |  | 2 | MTNAirtel | T0441 | ZM3435 | yes |  |  | Palisade | Inala | 2022-08-05 | Yes | No |  |  |  |  | pending |  | No | No | yes |  |  | Pending | n/a |  | Pending |  |  |  |  | IHS_STR_261A
972 | ZM3511 | IHS_STR_262A | MAKOLI | 26.089 | -17.4177 | Southern | 1.5 | SOUTHERN | Livingstone | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 80 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 11.5 | perkins | 3TNE88-G1A | Mecc Alte | ECO28-SN/4 | 600 | Power cube | ICC330-H1_C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | NA | N/A | 28 |  | 1 | Airtel | 0 | ZM3511 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_262A
1729 | ZM3512 | IHS_STR_263A | Tara Tuya Farms | 26.783 | -16.9619 | Southern | 4.5 | SOUTHERN | Kalomo | Yes | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 60 | Indoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | GV51790U | Mecc Alte | ECP28-1L/4 | 1000 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 70 |  | 1 | Airtel | 0 | ZM3512 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_263A
1799 | ZM3559 | IHS_STR_264A | Kaanzwa | 26.0803 | -15.6292 | Lusaka | 2.5 | SOUTHERN | Namwala | No | No | No | Rural | Silver | Silver | HUB | HUB | On air | Grid-Gen | Green Field | 60 | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 93 |  | 1 | Airtel | 0 | ZM3559 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_264A
282 | ZM3560 | IHS_STR_265A | Chivuna | 27.8263 | -16.184 | Southern | 1.8 | SOUTHERN | Monze | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Vitalgen | Vitalgen | 15 | Yanmar | GU51798U | Leroy Sommer | 0 | 600 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 81 |  | 2 | MTNAirtel | T0334 | ZM3560 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_265A
1476 | ZM3577 | IHS_STR_266A | No Name Camp | 25.7277 | -17.827 | Southern | 1.8 | SOUTHERN | Livingstone | Yes | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 48 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Generator city | Generator city | 15 | perkins | GU51790U | Mecc Alte | ECO28-SN/4 | 600 | Power cube | ICC330-H1_C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | NA | N/A | 45 |  | 1 | Airtel | 0 | ZM3577 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | yes |  |  | Pending | n/a |  | Pending |  |  |  |  | IHS_STR_266A
1351 | ZM3592 | IHS_STR_267A | NAKAMBALA SUGAR | 27.769 | -15.8424 | Southern | 1.8 | SOUTHERN | Mazabuka | Yes | No | No | Urban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Green Power | Green Power | 15 | perkins | 0 | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | PowerCube | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 25000 | N/A | 130 |  | 3 | MTNAirtelLiquid Telecom | T0490 | ZM3592 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_267A
393 | ZM3733 | IHS_STR_268A | GREEN SOLUTION | 27.0463 | -16.7301 | Southern | 2 | SOUTHERN | Choma | No | No | No | Urban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 48 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | Yanmar | 4TNE88 | Mecc Alte | ECO28-SN/4 | 1000 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 45.2 |  | 1 | Airtel | 0 | ZM3733 | 0 |  |  | Mesh | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_268A
1453 | ZM3734 | IHS_STR_269A | NGWEZI RANCH | 26.344 | -17.0341 | Southern | 1.8 | SOUTHERN | Kalomo | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | Yanmar | 3TNE88-G1A | Mecc Alte | ECP 28-M/4 | 1000 | Power cube | ICC330-H1_C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | NA | N/A | 57.2 |  | 2 | MTNAirtel | T0459 | ZM3734 | no |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_269A
813 | ZM3791 | IHS_STR_270A | LIBUYU | 25.882 | -17.8542 | Southern | 1.8 | SOUTHERN | Livingstone | No | No | No | Urban | Gold | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 40 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | GK65597U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ICC330-H1_C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | NA | N/A | 40 |  | 1 | Airtel | 0 | ZM3791 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_270A
1800 | ZM3792 | IHS_STR_271A | SIAVONGA_1 | 28.7144 | -16.5303 | Lusaka | 1.5 | SOUTHERN | Siavonga | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 48 | Outdoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 10 | perkins | 404A-22 | Mecc Alte | ECP-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 23 |  | 1 | Airtel | 0 | ZM3792 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_271A
479 | ZM3793 | IHS_STR_272A | KABULAMWANDA | 26.8736 | -15.8652 | Southern | 2 | SOUTHERN | Itezhi-Tezhi | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 54 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Metco | Metco | 16 | perkins | GK65597U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 66 |  | 1 | Airtel | 0 | ZM3793 | 0 |  |  | Mesh | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_272A
1658 | ZM3794 | IHS_STR_273A | SIMWATA CHELA | 26.7597 | -17.5287 | Southern | 2.5 | SOUTHERN | Kalomo | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Solar-Gen | Green Field | 52 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GU51790U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | TP48200A | 200 | NARADA | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | NA | N/A | 52 |  | 1 | Airtel | 0 | ZM3794 | yes |  |  | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_273A
289 | ZM3795 | IHS_STR_274A | Choma Biofuels | 26.8277 | -16.8725 | Southern | 1.5 | SOUTHERN | Choma | No | No | No | Urban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 48 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | MPI | MPI | 20 | perkins | GK65597R | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | PowerCube | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 60 |  | 2 | MTNAirtel | T1190 | ZM3795 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_274A
1806 | ZM3796 | IHS_STR_275A | Kariba 47 | 28.2934 | -16.3957 | Lusaka | 2.5 | SOUTHERN | Siavonga | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | metico-perkins | metico-perkins | 20 | perkins | 404A-22 | Zanardi | AL 3/4 | 1000 | Emerson | N/A | 400 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 39.5 |  | 1 | Airtel | 0 | ZM3796 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | Yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_STR_275A
977 | ZM3797 | IHS_STR_276A | Makunka Settlement | 25.65 | -17.533 | Southern | 2.5 | SOUTHERN | Kazungula | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen-solar | Green Field | 40 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | IMG | IMG | 20 | perkins | GV51790U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | ICC330-H1_C1 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | NA | N/A | 64 |  | 2 | MTNAirtel | T0420 | ZM3797 | yes |  |  | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_276A
1647 | ZM3798 | IHS_STR_277A | SIKALONGO | 27.2357 | -16.9705 | Southern | 1.8 | SOUTHERN | Choma | No | No | No | Rural | Silver | Silver | BB | BTS | On air | Grid-Gen | Green Field | 70 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | 0 | 0 | 15 | perkins | GU51794U | Leroy Sommer | 0 | 600 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 62 |  | 2 | MTNAirtel | T1195 | ZM3798 | 0 |  |  | Mesh | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_277A
1061 | ZM3801 | IHS_STR_278A | MAZABUKA_KAFUE | 27.9399 | -16.0158 | Southern | 1.8 | SOUTHERN | Mazabuka | Yes | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Indoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | IMG | IMG | 15 | perkins | GU51794U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 72 |  | 2 | MTNAirtel | T0205 | ZM3801 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_278A
1260 | ZM3802 | IHS_STR_279A | Munali Hills Riverside | 28.158 | -15.937 | Southern | 1.8 | SOUTHERN | Mazabuka | Yes | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | IMG | IMG | 15 | perkins | GU51794U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 50 |  | 1 | Airtel | 0 | ZM3802 | 0 |  |  | Mesh | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_279A
1526 | ZM3803 | IHS_STR_280A | PEMBA MUZOKA | 27.3382 | -16.6032 | Southern | 2.5 | SOUTHERN | Choma | Yes | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 54 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GU51794U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Emerson | N/A | 400 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | 0 | N/A | 78 |  | 2 | MTNAirtel | T0309 | ZM3803 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_280A
397 | ZM3804 | IHS_STR_281A | Harmony | 27.0872 | -16.7771 | Southern | 1.5 | SOUTHERN | Choma | Yes | No | No | Urban | Silver | Silver | BB | BTS | On air | Grid-Gen | Green Field | 54 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | MPI | MPI | 10 | perkins | GK65597R | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | Power2000 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 78 |  | 2 | MTNAirtel | T1184 | ZM3804 | 0 |  |  | Mesh | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_281A
3 | ZM3805 | IHS_STR_282A | After Zimba Kananga | 25.8799 | -14.1502 | Southern | 1.8 | SOUTHERN | Livingstone | Yes | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 40 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | GV51790U | Mecc Alte | ECP 28-M/4 | 1000 | Power cube | ICC330-H1_C1 | 600 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | NA | N/A | 56 |  | 2 | MTNAirtel | T1194 | ZM3805 | yes |  |  | Palisade | Netco | 2022-08-05 | Yes | Yes |  |  |  |  | pending |  | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_282A
1579 | ZM3867 | IHS_STR_283A | Rusangu Mission | 27.5227 | -16.3801 | Southern | 1.8 | SOUTHERN | Monze | Yes | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Green Power | Green Power | 15 | perkins | GU51794U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 55 |  | 1 | Airtel | 0 | ZM3867 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_283A
560 | ZM3969 | IHS_STR_284A | Kalomo Boma | 26.4972 | -16.9897 | Southern | 2.5 | SOUTHERN | Kalomo | Yes | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 40 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Vitalgen | Vitalgen | 20 | perkins | GV51790U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | ICC330-H1_C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | NA | N/A | 50 |  | 2 | MTNAirtel | T1185 | ZM3969 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_284A
1372 | ZM3970 | IHS_STR_285A | Namiyanga | 26.5034 | -17.0758 | Southern | 1.8 | SOUTHERN | Kalomo | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 56 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | GV51790U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ICC330-H1_C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | NA | N/A | 50 |  | 2 | MTNAirtel | T0271 | ZM3970 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_285A
939 | ZM3972 | IHS_STR_286A | Maamba Town1 | 27.334 | -17.2855 | Southern | 2 | SOUTHERN | Sinazongwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 65 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Vitalgen | Vitalgen | 15 | perkins | GU51798U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 37 |  | 1 | Airtel | T0449 | ZM3972 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_286A
59 | ZM3994 | IHS_STR_287A | Bweengwa | 27.1292 | -16.1003 | Southern | 2.5 | SOUTHERN | Monze | No | No | No | Urban | Silver | Silver | BB | BB | On air | Grid-Gen-solar | Green Field | 50 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | 0 | 0 | 15 | perkins | GV51790R | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | Power2000 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 75 |  | 2 | MTNAirtel | T0468 | ZM3994 | Yes |  |  | Palisade | Netco | 2022-08-05 | Yes | No |  |  |  |  | pending |  | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_287A
1634 | ZM4012 | IHS_STR_288A | SIACHITEMA | 26.73 | -16.7509 | Southern | 1.8 | SOUTHERN | Kalomo | No | No | No | Suburban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | RID | RID | 20 | Mitsubishi | 0 | Leroy Sommer | 0 | 600 | Power cube | Power2000 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 60 |  | 2 | MTNAirtel | T0414 | ZM4012 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_288A
1822 | ZM6000 | IHS_STR_289A | Ngoma | 25.9558 | -15.9105 | Lusaka | 2 | SOUTHERN | Namwala | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Joseph Mulenga | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 16 | perkins | 404D-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 54 |  | 1 | Airtel | T0465 | ZM6000 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_289A
1072 | ZM6002 | IHS_STR_290A | Mbila | 26.3182 | -16.181 | Southern | 2.5 | SOUTHERN | Namwala | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | MPMC | CK works | 20 | perkins | 0 | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | Power2000 | 250 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | 0 | N/A | 45 |  | 1 | Airtel | 0 | ZM6002 | 0 |  |  | Mesh | Netco | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_290A
1059 | ZM6010 | IHS_STR_291A | Mazabuka Town | 27.7636 | -15.8603 | Southern | 1.5 | SOUTHERN | Mazabuka | Yes | No | No | Urban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GV51790U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Emerson | Netsure | 250 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | 0 | N/A | 119 |  | 1 | Airtel | 0 | ZM6010 | 0 |  |  | Mesh | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_291A
158 | ZM6066 | IHS_STR_292A | Chief Nyawa | 25.9 | -17.1833 | Southern | 1.8 | SOUTHERN | Kazungula | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 70 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Rid | Mitsubishi | 15 | Mitsubishi | Mitsubishi S 4L2 | Zanardi | Zanadi AL3/4 | 600 | NA | NA | NA | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | NA | N/A | 30 |  | 1 | Airtel | 0 | ZM6066 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_292A
941 | ZM6069 | IHS_STR_293A | Machipapa | 25.1426 | -11.8296 | Southern | 1.8 | SOUTHERN | Choma | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | IMG | IMG | 15 | perkins | GU51794U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 71 |  | 2 | MTNAirtel | T0419 | ZM6069 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_293A
1659 | ZM6071 | IHS_STR_294A | Simwata chela (Luyaba) | 26.6632 | -17.2948 | Southern | 2.5 | SOUTHERN | Kalomo | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GV51790U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ICC330-H1_C1 | 600 | Lithium | 500 | 48 | 100 | 5 | N/A | N/A | N/A | NA | N/A | 70 |  | 2 | MTNAirtel | T0467 | ZM6071 | yes |  |  | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_294A
1653 | ZM6073 | IHS_STR_295A | Simaubi | 26.8332 | -16.2577 | Southern | 2 | SOUTHERN | Choma | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | perkins | GV51790U | Mecc Alte | ECP28-M/4 | 1000 | Power cube | Power2000 | 250 | Lithium | 500 | 48 | 100 | 5 | N/A | N/A | N/A | 0 | N/A | 62 |  | 1 | Airtel | 0 | ZM6073 | 0 |  |  | Palisade | Netco | 2022-08-05 | No | No |  |  |  |  | Done |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_295A
1310 | ZM6074 | IHS_STR_296A | Muyobe | 26.8932 | -16.4122 | Southern | 1.8 | SOUTHERN | Choma | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 70 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | IMG | IMG | 15 | perkins | GU51794U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | Power2000 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 46 |  | 1 | Airtel | 0 | ZM6074 | 0 |  |  | Palisade | Netco | 2022-08-05 | Yes | No |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_296A
1364 | ZM6075 | IHS_STR_297A | Nalube | 27.6663 | -16.0974 | Southern | 1.5 | SOUTHERN | Monze | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 10 | perkins | GK65597R | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Delta | IPT | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 43 |  | 1 | Airtel | 0 | ZM6075 | 0 |  |  | Mesh | Inala | 2022-08-05 | Yes | No |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_297A
1616 | ZM6076 | IHS_STR_298A | Shanbwato | 26.9263 | -16.1319 | Southern | 1.8 | SOUTHERN | Choma | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | MPMC | MPMC | 15 | perkins | MPLS13S-INS | Leroy Sommer | 0 | 600 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 48 |  | 1 | Airtel | T0451 | ZM6076 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_298A
7 | ZM6104 | IHS_STR_299A | Airtel_ZM0215 | 26.5828 | -13.5051 | Southern | 1.8 | SOUTHERN | Itezhi-Tezhi | No | No | No | Rural | Silver | Silver | HUB | BTS | On air | Solar-Gen | Green Field | 70 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Vitalgen | Vitalgen | 15 | perkins | GU51798U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | Power2000 | 250 | Wolong | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 59 |  | 2 | MTNAirtel | T0455 | ZM6104 | 0 |  |  | Mesh | Netco | 2022-08-05 | Yes | No |  |  |  |  | pending |  | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_299A
763 | ZM6175 | IHS_STR_300A | Kemba Basic School | 27.3742 | -16.0549 | Southern | 1.5 | SOUTHERN | Monze | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 10 | perkins | GN6644V | Leroy Sommer | 0 | 1000 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 66 |  | 2 | MTNAirtel | T0422 | ZM6175 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_300A
11 | ZM6185 | IHS_STR_301A | APOSTOLIC_3_Rlf | 25.8353 | -14.2537 | Southern | 1.8 | SOUTHERN | Livingstone | Yes | No | No | Urban | Gold | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 40 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | GN66044U | Mecc Alte | ECP 28-M/4 | 1000 | Power cube | ICC330-H1_C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | NA | N/A | 45 |  | 1 | Airtel | 0 | ZM6185 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_301A
1022 | ZM6186 | IHS_STR_302A | MARAMBA_2_Rlf | 25.8738 | -17.8514 | Southern | 2.5 | SOUTHERN | Livingstone | Yes | No | No | Urban | Gold | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 40 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Ghadder | Ghadder | 20 | perkins | GV51790U | Leroy Sommer | TAL 049F J 6S/4 | 750 | Power cube | ICC330-H1_C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | NA | N/A | 45 |  | 1 | Airtel | 0 | ZM6186 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_302A
145 | ZM6321 | IHS_STR_304A | Chibozu | 27.2936 | -16.3024 | Southern | 1.5 | SOUTHERN | Monze | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | MPI | MPI | 10 | perkins | GK65597R | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | PowerCube | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 35 |  | 1 | Airtel | 0 | ZM6321 | 0 |  |  | Palisade | Netco | 2022-08-05 | Yes | No |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_304A
998 | ZM6363 | IHS_STR_305A | Mangunza | 27.0372 | -16.3534 | Southern | 1.8 | SOUTHERN | Choma | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 70 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Vitalgen | Vitalgen | 20 | perkins | GU51798U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | Power2000 | 250 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | 0 | N/A | 45.5 |  | 1 | Airtel | 0 | ZM6363 | 0 |  |  | Palisade | Netco | 2022-08-05 | No | No |  |  |  |  | Done |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_305A
1139 | ZM6364 | IHS_STR_306A | Moobola | 26.6968 | -16.2462 | Southern | 2.5 | SOUTHERN | Choma | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 70 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GU51794U | Leroy Sommer | 0 | 1000 | Power cube | PowerCube | 12 | Lithium | 500 | 48 | 100 | 5 | N/A | N/A | N/A | 0 | N/A | 62 |  | 2 | MTNAirtel | T0370 | ZM6364 | 0 |  |  | Palisade | Netco | 2022-08-05 | No | No |  |  |  |  | Done |  | No | No | yes |  |  | Pending | n/a |  | Pending |  |  |  |  | IHS_STR_306A
1468 | ZM6377 | IHS_STR_307A | Nkonkola high school | 27.8836 | -16.2281 | Southern | 1.8 | SOUTHERN | Monze | No | No | No | Urban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | 0 | 0 | 15 | perkins | GU51794U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 50.4 |  | 1 | Airtel | 0 | ZM6377 | 0 |  |  | Mesh | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_307A
47 | ZM6407 | IHS_STR_308A | Buleya Malima | 27.5064 | -17.1114 | Southern | 1.5 | SOUTHERN | Sinazongwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Generator City | Generator City | 13 | Yanmar | 3TNV88-GGEP | LINZ | 0 | 600 | Power cube | Power2000 | 250 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 61.3 |  | 2 | MTNAirtel | T1196 | ZM6407 | 0 |  |  | Palisade | Netco | 2022-08-05 | Yes | No |  |  |  |  | pending |  | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_308A
8 | ZM6438 | IHS_STR_309A | ALEXSWILL FARM | 26.7949 | -14.0406 | Southern | 2.5 | SOUTHERN | Kalomo | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 70 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GU51798U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | Power2000 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 46 |  | 1 | Airtel | 0 | ZM6438 | 0 |  |  | Palisade | Netco | 2022-08-05 | Yes | No |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_309A
1492 | ZM6447 | IHS_STR_310A | NTEME BASIC SCHOOL | 27.3961 | -16.1683 | Southern | 1.8 | SOUTHERN | Monze | No | No | No | Urban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 70 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | MPI | MPI | 15 | perkins | GK65597 | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | PowerCube | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 50.6 |  | 1 | Airtel | 0 | ZM6447 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_310A
194 | ZM6452 | IHS_STR_311A | Chilindi Basic | 27.7474 | -16.1234 | Southern | 2.5 | SOUTHERN | Mazabuka | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GV51790V | Mecc Alte | TAL 040F J 6S/4 | 1000 | Power cube | DCDU400 | 400 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | 0 | N/A | 42 |  | 1 | Airtel | 0 | ZM6452 | 0 |  |  | Palisade | Netco | 2022-08-05 | No | No |  |  |  |  | Done |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_311A
917 | ZM6463 | IHS_STR_312A | LUPANIMWNDIHOP1 | 25.1102 | -17.4752 | Southern | 2.5 | SOUTHERN | Kazungula | Yes | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 60 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GV51790U | Leroy Sommer | TAL 049F J 6S/4 | 1000 | Power cube | ICC330-H1_C1 | 600 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | NA | N/A | 63 |  | 2 | MTNAirtel | T0461 | ZM6463 | yes |  |  | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_312A
1021 | ZM6769 | IHS_STR_313A | Maramba 3G | 25.8931 | -17.8495 | Southern | 1.8 | SOUTHERN | Livingstone | Yes | No | No | Urban | Gold | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | falcon | falcon | 15 | perkins | GV51790U | Mecc Alte | ECP 28-M/4 | 600 | Power cube | ICC330-H1_C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | NA | N/A | 50 |  | 1 | Airtel | 0 | ZM6769 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_313A
245 | ZM0169 | IHS_STR_314A | CHIPEPO | 27.8597 | -16.8041 | Southern | 2.5 | SOUTHERN | Munyumbwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 80 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GV83540U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | Powercube | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | 0 | N/A | 64 |  | 2 | MTNAirtel | T0327 | ZM0169 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_314A
1058 | ZM3800 | IHS_STR_315A | Mazabuka Monze | 27.5517 | -16.116 | Southern | 2 | SOUTHERN | Mazabuka | No | No | No | Suburban | Silver | Silver | BTS | BB/HUB | On air | Grid-Gen | Green Field | 60 | Indoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | perkins | 0 | Leroy Sommer | 0 | 1000 | Emerson | Netsure | 300 | BSB | 1500 | 2 | 1500 | 24 | LG | LG | 18000 | 18000 | 2 | 80 |  | 2 | AirtelZambia Railways | 0 | ZM3800 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_315A
1278 | ZM0216 | IHS_STR_316A | MUNYUMBWE RPT 2 (Simwami) | 27.6219 | -16.8415 | Southern | 2.5 | SOUTHERN | Munyumbwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 80 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GV83540U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | Powercube | 400 | Lithium | 500 | 48 | 100 | 5 | N/A | N/A | N/A | 0 | N/A | 73 |  | 2 | MTNAirtel | T1197 | ZM0216 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_316A
1823 | ZM0207 | IHS_STR_317A | SIAVONGA ROAD | 28.3719 | -15.9307 | Lusaka | 2.5 | SOUTHERN | Siavonga | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ECC500 | 50 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 46 |  | 1 | Airtel | 0 | ZM0207 | 0 |  |  | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_STR_317A
290 | ZM0466 | IHS_STR_318A | Choma CBD | 26.9844 | -16.8083 | Southern | 2.5 | SOUTHERN | Choma | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GV51790U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | Powercube | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 94 |  | 1 | Airtel | 0 | ZM0466 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_STR_318A
1834 | ZM0554 | IHS_STR_319A | Chirundu High Cost | 28.8497 | -16.0224 | Lusaka | 2.5 | Lusaka | Chirundu | No | No | No | Suburban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 404A-22 | Leroy Sommer | ECO-28-M/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 68 |  | 1 | Airtel | 0 | ZM0554 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_STR_319A
1861 | ZM1476 | IHS_STR_320A | Chirundu Gabon | 28.8406 | -16.03 | Lusaka | 2.5 | Lusaka | Chirundu | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Samuel Mumba | SBC | SBC | Airtel | Evans Ngonga | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 83 |  | 1 | Airtel | 0 | ZM1476 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_STR_320A
292 | ZM0562 | IHS_STR_322A | Choma Overspill | 26.9786 | -16.8269 | Southern | 2.5 | SOUTHERN | Southern | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GV51790U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Emerson | Netsure | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 76 |  | 1 | Airtel | 0 | ZM0562 | NO |  | N/A | Palisade | Inala | 2022-08-05 | [21 empty] | IHS_STR_322A
1143 | ZM1477 | IHS_STR_324A | Mount Gomali | 26.9937 | -16.8131 | Southern | 2.5 | Southern | Choma | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS |  |  | 20 | perkins |  |  |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 150 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 95 |  | 1 | Airtel | ZM1477 | ZM1477 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_STR_324A
1436 | ZM1496 | IHS_STR_325A | New Kazungula | 25.2805 | -17.7859 | Southern | 2.5 | Southern | Kazungula | No | No | No | Urban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | perkins | CK Works | 20 | perkins |  |  |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 89 |  | 1 | Airtel | ZM1496 | ZM1496 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_STR_325A
327 | ZM1506 | IHS_STR_326A | Dambwa Extension | 25.8309 | -15.8603 | Southern | 2.5 | Southern | Livingstone | No | No | No | Urban |  | Gold | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 130 |  | 1 | Airtel | ZM1506 | ZM1506 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_STR_326A
655 | ZM1511 | IHS_STR_327A | Kaonga | 27.7695 | -15.8492 | Southern | 2.5 | Southern | Mazabuka | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 150 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 96 |  | 1 | Airtel | ZM1511 | ZM1511 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_STR_327A
406 | ZM1510 | IHS_STR_328A | Hill Side | 27.7397 | -15.8711 | Southern | 2.5 | Southern | Mazabuka | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | perkins | CK Works | 20 | perkins |  |  |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 150 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 97 |  | 1 | Airtel | 0 | ZM1510 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_STR_328A
1056 | ZM1512 | IHS_STR_329A | Mazabuka Airstrip | 27.7455 | -8.8446 | Southern | 2.5 | Southern | Mazabuka | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Aaron Ikenda | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 150 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 98 |  | 1 | Airtel | ZM1512 | ZM1512 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_STR_329A
1856 | ZM1367 | IHS_STR_330A | Siantente Basic School | 26.6123 | -16.4735 | Southern | 4.5 | Southern | Kalomo | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Solar-Gen | Green Field | 70 | Outdoor | Aaron Ikenda | N/A | N/A | Airtel | Joseph Banda | CCS | CCS | perkins |  | 30 |  |  |  |  | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_STR_330A
1835 | ZM1290 | IHS_STR_331A | Syamuyala Basic school | 27.4776 | -17.1971 | Southern | 4.5 | Southern | Sinazongwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 60 | Outdoor | Aaron Ikenda | N/A | N/A | Airtel | Joseph Banda | CCS | CCS | perkins | [6 empty] | 1000 |  |  |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_STR_331A
1836 | ZM1371 | IHS_STR_332A | Nkandanzovu Clinic | 26.2017 | -16.5726 | Southern | 4.5 | Southern | Kalomo | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Solar-Gen | Green Field | 60 | Outdoor | Aaron Ikenda | N/A | N/A | Airtel | Joseph Banda | CCS | CCS | perkins | [6 empty] | 1000 |  |  |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_STR_332A
1837 | ZM0954 | IHS_STR_333A | Simanansa Basic School | 27.1886 | -16.2711 | Southern | 4.5 | Southern | Monze | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Solar-Gen | Green Field | 60 | Outdoor | Aaron Ikenda | N/A | N/A | Airtel | Joseph Banda | CCS | CCS | perkins | [6 empty] | 1000 |  |  |  | Lithium | 200 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_STR_333A
1838 | ZM0972 | IHS_STR_334A | Mubanga Primary School | 26.4657 | -16.7304 | Southern | 4.5 | Southern | Kalomo | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Solar-Gen | Green Field | 60 | Outdoor | Aaron Ikenda | N/A | N/A | Airtel | Joseph Banda | CCS | CCS | perkins | [6 empty] | 1000 |  |  |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_STR_334A
1839 | ZM0980 | IHS_STR_335A | Nakabanga Primary School | 26.7432 | -16.7251 | Southern | 4.5 | Southern | Kalomo | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Solar-Gen | Green Field | 60 | Outdoor | Aaron Ikenda | N/A | N/A | Airtel | Joseph Banda | CCS | CCS | perkins | [6 empty] | 1000 |  |  |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_STR_335A
1840 | ZM1030 | IHS_STR_336A | Nameembo Basic School | 28.1207 | -16.098 | Southern | 4.5 | Southern | Chikankanta | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Solar-Gen | Green Field | 60 | Outdoor | Aaron Ikenda | N/A | N/A | Airtel | Joseph Banda | CCS | CCS | perkins | [6 empty] | 1000 |  |  |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_STR_336A
1857 | ZM1049 | IHS_STR_337A | Chipembele Basic School | 27.609 | -16.3639 | Southern | 4.5 | Southern | Monze | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Solar-Gen | Green Field | 70 | Outdoor | Aaron Ikenda | N/A | N/A | Airtel | Joseph Banda | CCS | CCS | perkins |  | 30 |  |  |  |  | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_STR_337A
1858 | ZM1410 | IHS_STR_338A | Itapa Clinic | 26.5261 | -16.1197 | Southern | 4.5 | Southern | Namwala | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Solar-Gen | Green Field | 80 | Outdoor | Aaron Ikenda | N/A | N/A | Airtel | Joseph Banda | CCS | CCS | perkins |  | 30 |  |  |  |  | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_STR_338A
1859 | ZM1413 | IHS_STR_339A | Chikanta Basic School | 26.6168 | -16.3653 | Southern | 4.5 | Southern | Kalomo | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Gen Only | Green Field | 80 | Outdoor | Aaron Ikenda | N/A | N/A | Airtel | Joseph Banda | CCS | CCS | perkins |  | 30 | perkins |  |  |  | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_STR_339A
1860 | ZM1369 | IHS_STR_340A | Sinamalima Basic School | 27.5526 | -17.0614 | Southern | 4.5 | Southern | Sinazongwe | No | No | No | Rural | Silver | Silver | BTS | BTS | On Air | Grid-Gen | Green Field | 70 | Outdoor | Aaron Ikenda | N/A | N/A | Airtel | Joseph Banda | CCS | CCS | perkins |  | 30 |  |  |  |  | 1000 | Power cube |  |  | Lithium | 100 | 48 | 100 | 2 | N/A | N/A | N/A | N/A | N/A | 105 | [32 empty] | IHS_STR_340A
1128 | T1090 | IHS_WST_001M | Mongu Central | 23.136 | -15.2695 | Southern | 2.5 | WESTERN | MONGU | No | No | No | Urban | 2G 3G 4G | P2 | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Kelvin Simpasa | SBC | SBC | MTN | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GN83537R | Leroy Sommer | TAL-A40-F J 6/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 156 |  | 3 | MTNLiquid TelecomSmartnet | T1090 | 0 | Yes |  |  | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 2 |  |  | Done | 2019-07-04 | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_001M
1130 | T1111 | IHS_WST_002M | Mongu East | 23.1578 | -15.2717 | Southern | 4.5 | WESTERN | MONGU | Yes | No | No | Urban | 2G 3G | P3 | BTS | BTS | On air | Grid-Gen | Green Field | 36 | Outdoor | Kelvin Simpasa | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 0 | Leroy Sommer | TAL-A40-F J 6/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 154 |  | 4 | MTNAirtelINQLiquid Telecom | T1111 | ZM6844 | Yes |  |  | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | Done | 2019-07-04 | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_002M
734 | T1037 | IHS_WST_003M | Katongo | 23.1524 | -15.3015 | Southern | 2.5 | WESTERN | MONGU | No | No | No | Rural | 2G 3G | P3 | BB | BB | On air | Grid-Gen | Green Field | 66 | Indoor | Kelvin Simpasa | SBC | SBC | MTN | Joseph Banda | CCS | CCS | CK Works | CK Works | 30 | perkins | GN83537R | Leroy Sommer | TAL-A40-F J 6/4 | 1000 | Delta | DPS 2400B-48-5 | 250 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 124 |  | 2 | MTNAirtel | T1037 | ZM6885 | YES |  |  | Palisade | Inala | 2022-08-05 | Yes | No |  |  |  |  | pending |  | No | No | yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_WST_003M
982 | T1043 | IHS_WST_004M | Malengwa | 23.1537 | -15.2274 | Southern | 2.5 | WESTERN | MONGU | Yes | No | No | Suburban | 2G 3G | P4 | BTS | BB | On air | Grid-Gen | Green Field | 36 | Outdoor | Kelvin Simpasa | SBC | SBC | MTN | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GN83537R | Leroy Sommer | TAL-A40-F J 6/4 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 105 |  | 2 | MTNAirtel | T1043 | ZM6796 | YES |  |  | Palisade | Inala | 2022-08-05 | Yes | No |  | 2 |  |  | Done | 2019-05-20 | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_004M
820 | T1004 | IHS_WST_005M | Limulunga | 23.1482 | -15.1308 | Southern | 2.5 | WESTERN | MONGU | No | No | No | Suburban | 2G 3G | P4 | BB | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Kelvin Simpasa | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GV51790U | Mecc Alte | ECP 28-M/4 | 1000 | Delta | DPS 2400B-48-5 | 250 | Lithium | 200 | 48 | 100 | 2 | LG | LG | 18000 | 18000 | 2 | 39.7 |  | 1 | MTN | T1004 | 0 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_005M
722 | T1036 | IHS_WST_006M | Kataba MTN | 23.2327 | -15.4427 | Southern | 1.5 | WESTERN | MONGU | No | No | No | Suburban | 2G 3G | P4 | BB | BTS | On air | Grid-Gen | Green Field | 42 | Outdoor | Kelvin Simpasa | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Yanmar | Yanmar | 13 | Yanmar | 3TNE88-G1A | Mecc Alte | ECO28-SN4 | 600 | Delta | DPS 2400B-48-5 | 250 | Wolong | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 30 |  | 1 | MTN | T1036 | 0 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_006M
1334 | T1050 | IHS_WST_007M | Mweeke | 23.3464 | -15.2347 | Southern | 2.5 | WESTERN | MONGU | No | No | No | Rural | 2G | P4 | BB | BB | On air | Grid-Gen | Green Field | 66 | Outdoor | Kelvin Simpasa | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GV51790U | Mecc Alte | ECP 28-M/4 | 1000 | Power cube | AMP30H | 90 | Wolong | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 67.2 |  | 2 | MTNAirtel | T1050 | ZM3807 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_007M
1765 | T1057 | IHS_WST_008M | Ushaa | 23.2327 | -14.9735 | Southern | N/A | WESTERN | MONGU | No | No | No | Rural | 2G | P4 | BB | BTS | On air | Solar-Gen | Green Field | 70 | Outdoor | Kelvin Simpasa | SBC | SBC | MTN | Joseph Banda | CCS | CCS | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Power cube | AMP30H | 90 | ROLLS | 1410 | 4 | 1460 | 12 | N/A | N/A | N/A | N/A | N/A | 38.3 |  | 1 | MTN | T1057 | 0 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  | Consolidated on IHS_WST_209A | IHS_WST_008M
1388 | T1064 | IHS_WST_009M | Nanjucha | 23.2986 | -15.7041 | Southern | 2.5 | WESTERN | SENANGA | No | No | No | Rural | 2G | P4 | BB | BTS | On air | Grid-Gen | Green Field | 80 | Outdoor | Kelvin Simpasa | SBC | SBC | MTN | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GV51794U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ICC330-HA1-C10 | 600 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 89 |  | 2 | MTNAirtel | T1064 | ZM6881 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_009M
536 | T1010 | IHS_WST_010M | Kalabo | 22.6803 | -14.9972 | Southern | 2 | WESTERN | KALABO | No | No | No | Suburban | 2G 3G | P3 | BTS | BB | On air | Grid-Gen | Green Field | 70 | Indoor | Kelvin Simpasa | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 16 | perkins | 921931V | Mecc Alte | EC0 28-VL/4 | 1000 | Delta | DPS 2400B-48-5 | 250 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 111 |  | 3 | MTNAirtelTop Star | T1010 | ZM0141 | YES |  |  | Palisade | Inala | 2022-08-05 | Yes | No |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_010M
1757 | T1019 | IHS_WST_011M | Uka | 22.614 | -14.9858 | Southern | 1.8 | WESTERN | KALABO | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 42 | Outdoor | Kelvin Simpasa | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | GV51794U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 75 |  | 2 | MTNAirtel | T1019 | ZM6797 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_011M
676 | T1034 | IHS_WST_012M | Kapungu | 23.2204 | -14.6082 | Southern | N/A | WESTERN | LUKULU | No | No | No | Rural | 2G | P4 | BB | BTS | On air | Solar-Gen | Green Field | 70 | Outdoor | Kelvin Simpasa | SBC | SBC | MTN | Joseph Banda | CCS | CCS | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Emerson | R48-3200W | 400 | ROLLS | 1410 | 4 | 1460 | 12 | N/A | N/A | N/A | N/A | N/A | 28.8 |  | 1 | MTN | T1034 | 0 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  | Consolidated on IHS_WST_216A Kapungu | IHS_WST_012M
1597 | T1006 | IHS_WST_013M | Senanga | 23.2939 | -16.1094 | Southern | 4.5 | WESTERN | SENANGA | No | No | No | Suburban | 2G 3G | P2 | BB | BB | On air | Grid-Gen | Green Field | 66 | Indoor | Kelvin Simpasa | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 4TNE88-G1A | Leroy Sommer | EC0 28-1LN/4 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 109.34 |  | 2 | MTNTop Star | T1006 | 0 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_013M
886 | T1042 | IHS_WST_014M | Lukulu B | 23.2477 | -14.3926 | Southern | 1.8 | WESTERN | LUKULU | No | No | No | Suburban | 2G 3G | P3 | BB | BB | On air | Grid-Gen | Green Field | 80 | Indoor | Kelvin Simpasa | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Yanmar | Yanmar | 15 | Yanmar | 4TNE88-G1A | Leroy Sommer | LS 28S2 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 89 |  | 2 | MTNTop Star | T1042 | 0 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_WST_014M
1386 | T1065 | IHS_WST_015M | Nangweshi | 23.3208 | -16.3989 | Southern | 2.5 | WESTERN | SESHEKE | No | No | No | Rural | 2G 3G | P4 | BB | BTS | On air | Solar-Gen | Green Field | 80 | Indoor | Kelvin Simpasa | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Ghaddar | Ghaddar | 30 | perkins | GV51790U | Leroy Sommer | LSA 40M5J6/4 | 1000 | Cordex | Shelf 19' Cordex 3.6kw | 400 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 54 |  | 1 | MTN | T1065 | 0 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | yes |  |  | Pending | n/a |  | Pending |  |  |  |  | IHS_WST_015M
592 | T1029 | IHS_WST_016M | Kamilende | 23.4398 | -14.1557 | Southern | 2.5 | WESTERN | LUKULU | No | No | No | Rural | Silver | P4 | BB | BB | On air | Solar-Gen | Green Field | 70 | Indoor | Kelvin Simpasa | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GV51790U | Mecc Alte | ECP 28-M/4 | 1000 | Emerson | Shelf 19' Cordex 3.6kw | 400 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 25 |  | 1 | MTN | T1029 | 0 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_016M
1665 | T1023 | IHS_WST_018M | Sioma | 23.499 | -16.6053 | Southern | 1.8 | WESTERN | SESHEKE | No | No | No | Suburban | 2G 3G | P4 | BB | BTS | On air | Grid-Gen | Green Field | 66 | Outdoor | Kelvin Simpasa | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Elcose | Elcos | 15 | perkins | GU51794U | Mecc Alte | ECP 3-3L/4 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 67 |  | 1 | MTN | T1023 | 0 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_018M
1343 | T1051 | IHS_WST_019M | Mwetete | 24.4912 | -14.9186 | Southern | 2.5 | WESTERN | KAOMA | No | No | No | Rural | 2G | P4 | BB | BB | On air | Solar-Gen | Green Field | 66 | Outdoor | Kelvin Simpasa | SBC | SBC | MTN | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GN83537R | Leroy Sommer | TAL-A40-F J 6/4 | 1000 | Cordex | Shelf 19' Cordex 3.6kw | 400 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | 18000 | N/A | 30.3 |  | 1 | MTN | T1051 | 0 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_019M
1464 | T1060 | IHS_WST_020M | Nkhale | 23.75 | -16.7966 | Southern | NA | WESTERN | SESHEKE | No | No | No | Rural | 2G | P4 | BB | BTS | On air | Solar-Gen | Green Field | 70 | Outdoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | NA | NA | NA | NA | NA | NA | NA | N/A | Power cube | ICC330-H1_C1 | 600 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | NA | N/A | 40 |  | 1 | MTN | T1060 | 0 | yes |  |  | Palisade | Inala | 2022-08-05 | Yes | Yes |  | 1 |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  | Consolidated at IHS_WST_212A | IHS_WST_020M
827 | T1040 | IHS_WST_021M | Litiya A | 24.7673 | -14.8334 | Southern | 1.8 | WESTERN | KAOMA | No | No | No | Suburban | 2G 3G | P4 | BB | BTS | On air | Grid-Gen | Green Field | 60 | Indoor | Kelvin Simpasa | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Yanmar | Yanmar | 15 | Yanmar | 4TNE88-G1A | Leroy Sommer | LS 28S2 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 54 |  | 1 | MTN | T1040 | 0 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_021M
650 | T1003 | IHS_WST_022M | Kaoma | 24.806 | -14.8038 | Southern | 1.8 | WESTERN | KAOMA | No | No | No | Suburban | 2G 3G | P2 | BB | BTS | On air | Grid-Gen | Green Field | 46 | Indoor | Kelvin Simpasa | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Elcose | Elcos | 15 | perkins | GU51794U | Leroy Sommer | ECP 3-3L/4 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 55 |  | 1 | MTN | T1003 | 0 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | yes |  |  | Pending | n/a |  | Pending |  |  |  |  | IHS_WST_022M
1052 | T1089 | IHS_WST_023M | Mayukwayukwa | 24.7877 | -14.6697 | Southern | 2.5 | WESTERN | KAOMA | No | No | No | Rural | 2G 3G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 70 | Outdoor | Kelvin Simpasa | SBC | SBC | MTN | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GN83537R | Leroy Sommer | TAL-A40-F J 6/4 | 1000 | Eltek | FP2 48V 8+6KW 400V+N BD LD | 166 | NARADA | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 38.3 |  | 1 | MTN | T1089 | 0 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_023M
554 | T1059 | IHS_WST_024M | Kalobolelwa | 23.9774 | -17.0315 | Southern | 2.5 | WESTERN | SESHEKE | No | No | No | Rural | 2G | P4 | BB | BTS | On air | Solar-Gen | Green Field | 80 | Outdoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | 0 | 0 | 0 | 0 | 1000 | Power cube | ICC330-H1_C1 | 600 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | NA | N/A | 38 |  | 1 | MTN | T1059 | 0 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_024M
627 | T1032 | IHS_WST_025M | KanKwanda | 25.1217 | -14.8389 | Southern | 1.8 | WESTERN | KAOMA | No | No | No | Rural | 2G 3G | P3 | BB | BTS | On air | Grid-Gen | Green Field | 66 | Indoor | Kelvin Simpasa | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | GV51794U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 54.3 |  | 1 | MTN | T1032 | 0 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_025M
426 | T1058 | IHS_WST_026M | Imbwae | 24.1338 | -17.2817 | Southern | NA | WESTERN | SESHEKE | No | No | No | Rural | 2G | P4 | BB | BB | On air | Solar-Gen | Green Field | 70 | Outdoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | NA | NA | NA | NA | NA | NA | NA | N/A | Emerson | 0 | 250 | ROLLS | 1410 | 4 | 1460 | 12 | N/A | N/A | N/A | NA | N/A | 34 |  | 1 | MTN | T1058 | 0 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  | consolidated on IHS_WST_210A | IHS_WST_026M
1239 | T1093 | IHS_WST_027M | Mulobezi Road | 24.9619 | -16.9369 | Southern | 1.8 | WESTERN | SESHEKE | No | No | No | Rural | 2G | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 70 | Outdoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | GK65597R | Leroy Sommer | TAL 040F J 6S/4 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | NA | N/A | 30 |  | 1 | MTN | T1093 | 0 | no |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_027M
1610 | T1007 | IHS_WST_028M | Sesheke | 24.2854 | -17.4616 | Southern | 4.5 | WESTERN | SESHEKE | No | No | No | Suburban | 2G 3G | P2 | BB | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | GU51790U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ICC330-H1_C1 | 600 | Lithium | 400 | 48 | 100 | 4 | window/LG | window/LG | 18000 | 18000 | 2 | 55 |  | 2 | MTNParatus Telecom | T1007 | 0 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_028M
1291 | T1062 | IHS_WST_030M | Mushimbo | 24.5231 | -17.415 | Southern | NA | WESTERN | SESHEKE | No | No | No | Rural | 2G | P4 | BB | BTS | On air | Solar-Gen | Green Field | 42 | Outdoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | NA | NA | NA | NA | NA | NA | NA | N/A | Power cube | ICC330-H1_C1 | 600 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | NA | N/A | 35 |  | 1 | MTN | T1062 | 0 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  | Consolidated at IHS_WST_226A | IHS_WST_030M
1586 | T1055 | IHS_WST_031M | Sakankolonga | 24.8958 | -17.2706 | Southern | 1.8 | WESTERN | SESHEKE | No | No | No | Rural | 2G | P4 | BTS | BB | On air | Solar-Gen | Green Field | 70 | Outdoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | GU51790U | Leroy Sommer | LSA 40M5 J 6/4 | 600 | Power cube | ICC330-H1_C1 | 600 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | NA | N/A | 32 |  | 1 | MTN | T1055 | 0 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_031M
1326 | T1063 | IHS_WST_032M | Mwandi MTN | 24.8251 | -17.5108 | Southern | 1.8 | WESTERN | SESHEKE | No | No | No | Suburban | 2G 3G | P4 | BB | BB | On air | Grid-Gen | Green Field | 80 | Outdoor | Mwamba Kalilo | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | Yanmar | 4TNE88-G1A | Mecc Alte | ECP 28-M/4 | 600 | Delta | DPS 2400B-48-5 | 250 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | NA | N/A | 53 |  | 1 | MTN | T1063 | 0 | 0 |  |  | Palisade | Inala | 2022-08-05 | Yes | No |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_032M
928 | T1130 | IHS_WST_033M | LUVUZI VILLAGE | 23.9624 | -14.387 | Southern | 1.8 | WESTERN | LUKULU | No | No | No | Rural | 2G | P4 | BTS | BTS | On air | Solar-Gen | Green Field | 55 | Outdoor | Kelvin Simpasa | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Rid | Mitsubishi | 20 | Mitsubishi | 0 | Zanardi | 0 | 200 | N/A | N/A | 0 | Agisson | 1600 | 2 | 800 | 48 | N/A | N/A | N/A | N/A | N/A | 25 |  | 1 | MTN | T1130 | 0 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_033M
825 | T1133 | IHS_WST_034M | Lishiwa Repeater | 23.511 | -14.3838 | Southern | 1.8 | WESTERN | LUKULU | No | No | No | Rural | 2G | P4 | BTS | BTS | On air | Solar-Gen | Green Field | 55 | Outdoor | Kelvin Simpasa | SBC | SBC | MTN | Joseph Banda | CCS | CCS | Rid | Mitsubishi | 15 | Mitsubishi | 0 | Zanardi | 0 | 200 | N/A | N/A | 0 | Amaron | 600 | 4 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 18 |  | 1 | MTN | T1133 | 0 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_034M
652 | T1166 | IHS_WST_036M | Kaoma Town | 24.7949 | -14.7966 | Southern | 2.5 | WESTERN | Kaoma | No | No | No | Urban | P4 | P4 | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Kelvin Simpasa | SBC | SBC | MTN | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GN83537R | Leroy Sommer | TAL-A40-F J 6/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 36 |  | 1 | MTN | T1166 | 0 | No |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_036M
1126 | ZM0059 | IHS_WST_201A | Mongu | 23.1392 | -15.2713 | Southern | 5.5 | WESTERN | Mongu | No | No | No | Urban | Silver | Silver | HUB | BSC | On air | Grid-Gen | Green Field | 54 | Indoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 45 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 500 | 48 | 100 | 5 | LG | LG | 18000 | 18000 | 2 | 245 |  | 1 | Airtel | 0 | ZM0059 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_201A
1325 | ZM0129 | IHS_WST_202A | Mwandi | 24.8239 | -17.5122 | Southern | 2.5 | WESTERN | Sesheke | No | No | No | Suburban | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 80 | Indoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GV51790U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ICC330-H1C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | window/LG | window/LG | 18000 | 18000 | 2 | 50 |  | 2 | AirtelTop Star | 0 | ZM0129 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_WST_202A
1611 | ZM0137 | IHS_WST_203A | Sesheke | 24.2849 | -17.4617 | Southern | 2.5 | WESTERN | Sesheke | No | No | No | Urban | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 80 | Indoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GV51790U | Mecc Alte | TAL 040F J 6S/4 | 1000 | Power cube | ICC330-H1C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | window/LG | window/LG | 18000 | 18000 | 2 | 69 |  | 1 | Airtel | 0 | ZM0137 | yes |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_203A
651 | ZM0182 | IHS_WST_204A | Kaoma | 24.8055 | -14.8037 | Southern | 1.8 | WESTERN | Kaoma | No | No | No | Urban | Silver | Silver | BB | BTS | On air | Grid-Gen | Green Field | 48 | Indoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Earth Technology | Earth technology | 15 | perkins | GU51798U | Leroy Sommer | TAL 040F J 6S/4 | 400 | Power cube | ICC330-H1-C1 | 400 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 86 |  | 2 | AirtelTop Star | 0 | ZM0182 | YES |  |  | Palisade | Inala | 2022-08-05 | Yes | No |  |  |  |  | pending |  | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_204A
1238 | ZM0198 | IHS_WST_205A | Mulobezi | 25.1753 | -16.7777 | Southern | 2.5 | WESTERN | Sesheke | No | No | No | Rural | Silver | Silver | BTS | BB | On air | Grid-Gen | Green Field | 80 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | IMG | IMG | 20 | perkins | GV51790U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | ICC330-H1C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | 0 | N/A | 50 |  | 2 | MTNAirtel | T1092 | ZM0198 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_205A
1617 | ZM0205 | IHS_WST_206A | Shangombo | 22.0973 | -16.3179 | Southern | 2.5 | WESTERN | Shangombo | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GN83537R | Leroy Sommer | TAL-A40-F J 6/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | Chigo | Chigo | 18000 | 18000 | 2 | 87 |  | 3 | MTNAirtelTop Star | T1070 | ZM0205 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_206A
1387 | ZM0266 | IHS_WST_207A | Nangweshi | 23.3228 | -16.3969 | Southern | N/A | WESTERN | Senanga | No | No | No | Rural | Silver | Silver | BB | BTS | On air | Solar-Gen | Green Field | 50 | Indoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | CK Works | CK Works | N/A | N/A | N/A | N/A | N/A | N/A | Power cube | ICC330-HA1-C10 | 600 | Lithium | 300 | 48 | 100 | 3 | LG | LG | 18000 | 18000 | 2 | 67 |  | 1 | Airtel | 0 | ZM0266 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | Done | 2019-05-19 | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  | Consolidated on IHS_WST_015M Nangweshi | IHS_WST_207A
1666 | ZM0279 | IHS_WST_208A | Sioma | 23.4996 | -16.6053 | Southern | 2.5 | WESTERN | Shangombo | No | No | No | Suburban | Silver | Silver | BB | BTS | On air | Grid-Gen | Green Field | 58 | Indoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GV51790U | Mecc Alte | ECP 28-M/4 | 1000 | Power cube | TP48300/A-100A | 300 | NARADA | 600 | 2 | 600 | 24 | Chigo | Chigo | 18000 | 18000 | 2 | 71 |  | 1 | Airtel | 0 | ZM0279 | YES |  |  | Palisade | Netco | 2022-08-05 | Yes | No |  |  |  |  | pending |  | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_208A
1766 | ZM0550 | IHS_WST_209A | Ushaa | 23.2328 | -14.9704 | Southern | 4.5 | WESTERN | Mongu | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 80 | Indoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | CK Works | CK Works | 30 | perkins | GN83537R | Leroy Sommer | TAL-A40-F J 6/4 | 1000 | Power cube | ICC900-HD2 | 300 | Lithium | 400 | 48 | 100 | 4 | LG | LG | 18000 | 18000 | 2 | 78 |  | 1 | Airtel | 0 | ZM0550 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | Done | 2019-05-19 | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_209A
427 | ZM0763 | IHS_WST_210A | Imbwae | 24.1357 | -17.2819 | Southern | 4.5 | WESTERN | Sesheke | No | No | No | Rural | Silver | Silver | BB | BTS | On air | Solar-Gen | Green Field | 70 | Indoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | GN83537R | Leroy Sommer | TAL-A40-F J 6/4 | 1000 | Power cube | TP48300/A 100A | 300 | Wolong | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 47 |  | 1 | Airtel | 0 | ZM0763 | yes |  |  | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_210A
420 | ZM0764 | IHS_WST_211A | Illwendo | 23.9897 | -17.0729 | Southern | 2.5 | WESTERN | Sesheke | No | No | No | Rural | Silver | Silver | BB | BTS | On air | Solar-Gen | Green Field | 80 | Indoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | IMG | IMG | 20 | perkins | GV51790U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | TP48300/A 100A | 300 | Wolong | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 40 |  | 1 | Airtel | 0 | ZM0764 | yes |  |  | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_211A
1074 | ZM0766 | IHS_WST_212A | Mbowe | 23.7512 | -16.7969 | Southern | 4.5 | WESTERN | Sesheke | No | No | No | Rural | Silver | Silver | BB | BTS | On air | Solar-Gen | Green Field | 80 | Indoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | CK Works | CK Works | 30 | perkins | GN83537R | Leroy Sommer | TAL-A40-F J 6/4 | 1000 | Power cube | ICC330-H1_C1 | 400 | Wolong | 1200 | 2 | 600 | 48 | LG | LG | 18000 | 18000 | 2 | 45 |  | 1 | Airtel | 0 | ZM0766 | yes |  |  | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_212A
1378 | ZM0825 | IHS_WST_213A | Namushakende | 23.2326 | -15.4434 | Southern | 1.5 | WESTERN | Senanga | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 70 | Indoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 11 | perkins | GK66045U | Mecc Alte | ECP 28-1L/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 52 |  | 1 | Airtel | 0 | ZM0825 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | yes |  |  | Pending | n/a |  | Pending |  |  |  |  | IHS_WST_213A
821 | ZM0863 | IHS_WST_214A | Limulunga | 23.1479 | -15.1314 | Southern | 1.8 | WESTERN | Mongu | No | No | No | Suburban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Indoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Earth Technology | Earth technology | 15 | perkins | GU51798U | Leroy Sommer | TAL 040F J 6S/4 | 400 | Power cube | ICC330-H1-C1 | 400 | Amaron | 600 | 2 | 600 | 24 | star energy | star energy | 25000 | 25000 | 2 | 58 |  | 1 | Airtel | 0 | ZM0863 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_214A
1780 | ZM3345 | IHS_WST_215A | Winela | 23.1396 | -15.2603 | Southern | 4.5 | WESTERN | Mongu | No | No | No | Urban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 52 | Indoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | star energy | star energy | 25000 | 25000 | 2 | 122 |  | 2 | MTNAirtel | T1052 | ZM3345 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_215A
677 | ZM3358 | IHS_WST_216A | Kapungu | 23.2199 | -14.6084 | Southern | 4.5 | WESTERN | Lukulu | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 70 | Outdoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | CK Works | CK Works | 30 | perkins | 0 | Leroy Sommer | 0 | 1000 | Power cube | TP48200A | 200 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | N/A | N/A | 69 |  | 1 | Airtel | 0 | ZM3358 | YES |  |  | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | Yes | yes |  |  | Pending | n/a |  | Pending |  |  |  |  | IHS_WST_216A
1345 | ZM3411 | IHS_WST_217A | Mwilwe | 23.4852 | -15.1803 | Southern | 2.5 | WESTERN | Mongu | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 80 | Outdoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | GN83537R | Leroy Sommer | ECP 28-M/4 | 1000 | Power cube | ICC300-H1 | 400 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | N/A | N/A | 104 |  | 2 | MTNAirtel | T1120 | ZM3411 | YES |  |  | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_WST_217A
1366 | ZM3412 | IHS_WST_218A | Nalwei | 23.8635 | -15.0769 | Southern | 2.5 | WESTERN | Mongu | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 80 | Outdoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GN83537R | Leroy Sommer | TAL-A40-F J 6/4 | 1000 | Power cube | ICC300-H1-C1 | 400 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | N/A | N/A | 102 |  | 2 | MTNAirtel | T1097 | ZM3412 | YES |  |  | Palisade | Netco | 2022-08-05 | No | No |  |  |  |  | Done |  | No | No | yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_WST_218A
879 | ZM3413 | IHS_WST_219A | Luiikuta | 24.2107 | -15.0094 | Southern | 4.5 | WESTERN | Kaoma | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 80 | Outdoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 30 | perkins | 999395X | Mecc Alte | ECP 28-M/4 | 1000 | Power cube | TP48200A | 200 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | N/A | N/A | 74 |  | 2 | MTNAirtel | TX | ZM3413 | YES |  |  | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_219A
1367 | ZM3414 | IHS_WST_220A | Namasheshe | 24.6144 | -14.8723 | Southern | 2.5 | WESTERN | Kaoma | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 80 | Outdoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | EU20050608 | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | TP48200A | 200 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | N/A | N/A | 70 |  | 1 | Airtel | 0 | ZM3414 | YES |  |  | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_220A
1645 | ZM3513 | IHS_WST_221A | SICHILI | 24.9534 | -16.7118 | Southern | 2.5 | WESTERN | Sesheke | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | IMG | IMG | 20 | perkins | GV51790U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | ICC330-H1_C1 | 600 | Lithium | 200 | 48 | 100 | 2 | N/A | N/A | N/A | NA | N/A | 55 |  | 2 | MTNAirtel | T1123 | ZM3513 | no |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | Yes | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_221A
1140 | ZM3579 | IHS_WST_222A | MOOKA | 24.3798 | -17.4669 | Southern | 2.5 | WESTERN | Sesheke | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 48 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | IMG | IMG | 20 | perkins | Gu51790U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | NA | N/A | 50 |  | 2 | MTNAirtel | T0243 | ZM3579 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | yes |  |  | Pending | n/a |  | Pending |  |  |  |  | IHS_WST_222A
840 | ZM3581 | IHS_WST_223A | LUAMPA MISSION | 24.4456 | -15.0566 | Southern | 2.5 | WESTERN | Kaoma | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Vitalgen | Vitalgen | 20 | perkins | GV51790U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | TP48200A | 200 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 72 |  | 2 | MTNAirtel | T1088 | ZM3581 | YES |  |  | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_223A
1657 | ZM3605 | IHS_WST_224A | Simungoma | 24.6507 | -17.4136 | Southern | 2.5 | WESTERN | Sesheke | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen | Green Field | 60 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | IMG | IMG | 20 | perkins | GV5190U | Leroy Sommer | TAL 040F J 6S/4 | 600 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | NA | N/A | 65 |  | 2 | MTNAirtel | T0426 | ZM3605 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_224A
628 | ZM3735 | IHS_WST_225A | KANKWANDA | 25.1218 | -14.8403 | Southern | 2.5 | WESTERN | Kaoma | No | No | No | Rural | Silver | Silver | BB | BTS | On air | Grid-Gen | Green Field | 80 | Outdoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GV83540R | Leroy Sommer | TAL-A40-F J 6/4 | 1000 | Power cube | ICC330-HA1-C10 | 600 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | N/A | N/A | 71 |  | 1 | Airtel | 0 | ZM3735 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_225A
1292 | ZM3736 | IHS_WST_226A | Mushimbo | 24.5228 | -17.4147 | Southern | 4.5 | WESTERN | Sesheke | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 70 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | CK Works | CK Works | 30 | perkins | GV51790U | Mecc Alte | ECP 28-M/4 | 1000 | Power cube | ICC330-H1_C1 | 400 | Lithium | 500 | 48 | 100 | 5 | N/A | N/A | 0 | NA | 0 | 60 |  | 1 | Airtel | 0 | ZM3736 | no |  |  | Palisade | Netco | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_226A
1595 | ZM3806 | IHS_WST_227A | SEFULA | 23.1915 | -15.3789 | Southern | 1.8 | WESTERN | Mongu | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 54 | Outdoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Yanmar | Yanmar | 15 | Yanmar | 4TNE88-G1A | Leroy Sommer | LS 28S2 | 600 | Power cube | ICC330-H1-CI | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 95.6 |  | 2 | MTNAirtel | T1163 | ZM3806 | YES |  |  | Mesh | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_227A
1335 | ZM3808 | IHS_WST_229A | MWEETWE | 24.3439 | -14.955 | Southern | 1.8 | WESTERN | Kaoma | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 54 | Outdoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Green Power | Green Power | 15 | perkins | 51794V | Leroy Sommer | LSA 42.3VS2J6/4 | 600 | Power cube | TP48200A | 200 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 50.5 |  | 2 | MTNAirtel | T1132 | ZM3808 | YES |  |  | Palisade | Netco | 2022-08-05 | No | No |  |  |  |  | Done |  | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_229A
1392 | ZM3839 | IHS_WST_230A | Natukoma | 22.759 | -16.3554 | Southern | 2.5 | WESTERN | Shangombo | No | No | No | Rural | Silver | Silver | BTS | BB | On air | Solar-Gen | Green Field | 80 | Outdoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GV83540R | Leroy Sommer | TAL-A40-F J 6/4 | 1000 | Power cube | TP48200A | 200 | Lithium | 400 | 48 | 100 | 4 | N/A | N/A | N/A | N/A | N/A | 67 |  | 2 | MTNAirtel | T1128 | ZM3839 | YES |  |  | Mesh | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_230A
1379 | ZM3843 | IHS_WST_231A | Namusheshe | 24.0278 | -15.3225 | Southern | 2.5 | WESTERN | Kalabo | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 80 | Outdoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GN83537R | Leroy Sommer | TAL-A40-F J 6/4 | 1000 | Power cube | TP48200A | 200 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | N/A | N/A | 55.2 |  | 1 | Airtel | 0 | ZM3843 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No |  |  |  |  | Done |  | No | No | yes |  |  | Pending | n/a |  | Pending |  |  |  |  | IHS_WST_231A
811 | ZM3855 | IHS_WST_232A | Libonda | 22.9501 | -14.9863 | Southern | 1.8 | WESTERN | Kalabo | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | GN66044U | Mecc Alte | ECO 28-VL/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 60 |  | 2 | MTNAirtel | T1149 | ZM3855 | YES |  |  | Mesh | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_232A
1231 | ZM3863 | IHS_WST_233A | Mulambwa harbour | 23.1211 | -15.2727 | Southern | 1.8 | WESTERN | Mongu | No | No | No | Urban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 42 | Outdoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Earth Technology | Earth technology | 15 | perkins | GU51794 | Leroy Sommer | TAL 040F J 6S/4 | 400 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 98 |  | 2 | MTNAirtel | T1110 | ZM3863 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_233A
997 | ZM3865 | IHS_WST_234A | Mangango Mission | 24.5196 | -14.6513 | Southern | 2.5 | WESTERN | Kaoma | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen-solar | Green Field | 50 | Indoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GN83537R | Leroy Sommer | TAL-A40-F J 6/4 | 1000 | Emerson | A48701z-1 | 335 | NARADA | 600 | 2 | 600 | 24 | LG | LG | 18000 | 18000 | 2 | 73 |  | 2 | MTNAirtel | T1079 | ZM3865 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | yes |  |  | Pending | n/a |  | Pending |  |  |  |  | IHS_WST_234A
653 | ZM3971 | IHS_WST_235A | Kaoma Town1 | 24.8471 | -14.822 | Southern | 2.5 | WESTERN | Kaoma | No | No | No | Suburban | Silver | Silver | BB | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 20 | perkins | 998599X | Mecc Alte | ECP 28M4 | 1000 | Power cube | ICC300-H1-C1 | 400 | NARADA | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 100 |  | 2 | MTNAirtel | T1121 | ZM3971 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_235A
1053 | ZM3996 | IHS_WST_236A | MAYUKWAYUKWA_3 | 24.192 | -14.5676 | Southern | 2.5 | WESTERN | Kaoma | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GN83537R | Leroy Sommer | TAL-A40-F J 6/4 | 1000 | Emerson | ICC300-H1-C1 | 400 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | N/A | N/A | 78 |  | 2 | MTNAirtel | T1154 | ZM3996 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_236A
1073 | ZM4014 | IHS_WST_237A | Mbopuma Rpt | 22.9646 | -16.3946 | Southern | 2.5 | WESTERN | Shangombo | No | No | No | Rural | Silver | Silver | BB | BB | On air | Solar-Gen | Green Field | 70 | Outdoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GV83540R | Leroy Sommer | TAL-A40-F J 6/4 | 1000 | Power cube | TP48200A | 200 | Agisson | 1200 | 2 | 600 | 48 | N/A | N/A | N/A | N/A | N/A | 57 |  | 2 | MTNAirtel | T1134 | ZM4014 | YES |  |  | Mesh | Inala | 2022-08-05 | No | No | [6 empty] | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_237A
1279 | ZM6062 | IHS_WST_239A | Muoyo | 23.2574 | -15.5766 | Southern | 1.8 | WESTERN | Senanga | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 60 | Outdoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Yanmar | Yanmar | 15 | perkins | 4TNE88-G1A | Mecc Alte | ECO 28-VL/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 75.74 |  | 2 | MTNAirtel | T1124 | ZM6062 | YES |  |  | Mesh | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_239A
1380 | ZM6065 | IHS_WST_240A | Namuzingu Mulobezi Plantation | 24.8667 | -17.05 | Southern | 2.5 | WESTERN | Sesheke | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 70 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GU51790U | Leroy Sommer | TAL 040F J 6S/4 | 1000 | Power cube | ICC330-H1_C1 | 600 | Lithium | 300 | 48 | 100 | 3 | N/A | N/A | N/A | NA | N/A | 40 |  | 1 | Airtel | 0 | ZM6065 | 0 |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_240A
1127 | ZM6194 | IHS_WST_241A | Mongu 1 Rfl | 23.14 | -15.2648 | Southern | 1.8 | WESTERN | Mongu | No | No | No | Urban | Silver | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 40 | Outdoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Gen Logic | Gen Logic | 15 | perkins | GN66044U | Mecc Alte | EC0 28-VL/4 | 1000 | Power cube | ICC330-H1-C1 | 400 | Agisson | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 80.57 |  | 1 | Airtel | 0 | ZM6194 | YES |  |  | Mesh | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_241A
1354 | ZM6301 | IHS_WST_243A | Nakanyaa | 23.6513 | -15.4833 | Southern | 2.5 | WESTERN | Mongu | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 80 | Outdoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | CK Works | CK Works | 20 | perkins | GN83537R | Leroy Sommer | TAL-A40-F J 6/4 | 1000 | N/A | EPC 48200/2900-HC1 | 200 | BSB | 1500 | 2 | 1500 | 24 | N/A | N/A | N/A | N/A | N/A | 42.3 |  | 1 | Airtel | 0 | ZM6301 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | yes |  |  | yes | 20 |  | Pending |  |  |  |  | IHS_WST_243A
1116 | ZM6323 | IHS_WST_244A | Mishulundu | 22.8086 | -14.7797 | Southern | 1.8 | WESTERN | Kalabo | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 60 | Outdoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Rid | Mitsubishi | 20 | Mitsubishi | Mitsubishi | Zanardi | AL3/4 | 600 | N/A | 0 | 0 | Amaron | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 35 |  | 1 | MTN | T1142 | 0 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | No | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_244A
1652 | ZM6357 | IHS_WST_245A | Simaa | 23.6205 | -14.8528 | Southern | 1.8 | WESTERN | Mongu | No | No | No | Rural | Silver | Silver | BTS | BTS | On air | Solar-Gen | Green Field | 50 | Outdoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Earth Technology | Earth technology | 15 | perkins | GU51794 | Leroy Sommer | TAL 040F J 6S/4 | 400 | Power cube | TP48200A | 200 | Lithium | 500 | 48 | 100 | 5 | N/A | N/A | N/A | N/A | N/A | 42.4 |  | 1 | Airtel | 0 | ZM6357 | YES |  |  | Palisade | Netco | 2022-08-05 | No | No |  |  |  |  | Done |  | No | Yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_245A
1598 | ZM6462 | IHS_WST_246A | senenga-lyendela Hop Breaker | 23.3208 | -15.8719 | Southern | 1.8 | WESTERN | Senanga | No | No | No | Rural | Silver | Silver | BB | BB | On air | Grid-Gen-solar | Green Field | 52 | Outdoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | Rid | Mitsubishi | 15 | Mitsubishi | Mitsubishi | Zanardi | AL3/4 | 600 | Emerson | Netsure 701 | 400 | NARADA | 600 | 2 | 600 | 24 | N/A | N/A | N/A | N/A | N/A | 70.9 |  | 2 | MTNAirtel | T1129 | ZM6462 | YES |  |  | Palisade | Inala | 2022-08-05 | No | No | [6 empty] | No | yes | No |  |  | n/a | n/a |  | n/a |  |  |  |  | IHS_WST_246A
1612 | ZM1532 | IHS_WST_247A | Sesheke CBD | 24.2952 | -17.4809 | Southern | 2.5 | Southern | Sesheke | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 102 |  | 1 | Airtel | ZM1532 | ZM1532 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_WST_247A
1613 | ZM1376 | IHS_WST_248A | Sesheke Nakatindi | 24.3074 | -12.1881 | Southern | 2.5 | Southern | Sesheke | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Mwamba Kalilo | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 76 |  | 1 | Airtel | ZM1376 | ZM1376 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_WST_248A
1129 | ZM1515 | IHS_WST_249A | Mongu District Hospital | 23.1578 | -9.3281 | Southern | 2.5 | Southern | Mongu | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS | perkins | CK Works | 20 | perkins |  | Leroy Sommer |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 94 |  | 1 | Airtel | ZM1515 | ZM1515 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_WST_249A
1131 | ZM1516 | IHS_WST_250A | Mongu SDA HQ | 23.1406 | -15.2579 | Southern | 2.5 | WESTERN | Mongu | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS |  |  | 20 | perkins |  |  |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 103 |  | 1 | Airtel | ZM1516 | ZM1516 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_WST_250A
1232 | ZM1489 | IHS_WST_251A | Mulambwa Kaoma | 24.7978 | -14.817 | Southern | 2.5 | WESTERN | Kaoma | No | No | No | Urban |  | Silver | BTS | BTS | On air | Grid-Gen | Green Field | 50 | Outdoor | Kelvin Simpasa | SBC | SBC | Airtel | Joseph Banda | CCS | CCS |  |  | 20 | perkins |  |  |  | 1000 | Power cube | ICC330-H1-C1 |  | Lithium | 300 | 48 | 150 | 2 | N/A | N/A | N/A | N/A | N/A | 85 |  | 1 | Airtel | 0 | ZM1489 |  |  |  |  | Inala | 2022-08-05 | [21 empty] | IHS_WST_251A
IHS_EST_021M
IHS_EST_027M
IHS_EST_205A
IHS_EST_211A
IHS_EST_273A
Note on D1255: Simon Sinkala: Replaced Kawambwa Tea Estate Site

## MS CAPTURE
2325
SITE ID | SITE NAME | SBC | NAME OF TECHNICIAN | REGION | CURRENT VISIT DATE | LAST VISIT DATE | TYPE OF VISIT | DG SERIAL NUMBER | DG BRAND | AC / DC | DG KVA | DG REPLACEMENT DATE | PREVIOUS DG RUN HOURS | CURRENT DG RUN HOURS | RUNING HOURS | MAX RH | RH TEST | Last servicing | CURRENT SERVICING | NEXT SERVICE PLANED | DG serviced Hour | PREVIOUS DIESEL LEVEL | FUEL FOUND | FUEL ADDED | FUEL LEFT ON SITE | FUEL CONSUMED | CPH | Expected CPH | CPH Test | CPH Deductions | ZESCO METER S/NO | PHASE TYPE | CURRENT GRID METER READING | PREVIOUS GRID METER READING | GRID CONSUMPTION (kWh) | N-PH1 VOLTAGE | N-PH2 VOLTAGE | N-PH3 VOLTAGE | LOAD 1 (A) | LOAD 2 (A) | LOAD 3 (A) | DC LOAD (A)
T3223 | CHISOKONE | CCS | FACKSON | COPPERBELT | 2025-09-23 | [7 empty] | 0 | 0 | [8 empty] | 0 | 200
T3223 | CHISOKONE | CCS | FACKSON | COPPERBELT | 2025-09-27 | [7 empty] | 0 | 47 | [8 empty] | 0 | 200
T3223 | CHISOKONE | CCS | FACKSON | COPPERBELT | 2025-09-30 | [7 empty] | 47 | 77 | [8 empty] | 112 | 200
T3223 | CHISOKONE | CCS | FACKSON | COPPERBELT | 2025-10-04 | [7 empty] | 77 | 145 | [8 empty] | 49 | 200
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | 2025-09-23 | [7 empty] | FAULTY | 5017 | [8 empty] | 5 | 50
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | 2025-09-24 | [7 empty] | 5017 | 5039 | [8 empty] | 5 | 50
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | 2025-09-26 | [7 empty] | 5039 | 5059 | [8 empty] | 5 | 50
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | 2025-09-27 | [7 empty] | 5059 | 5082 | [8 empty] | 5 | 50
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | 2025-09-28 | [7 empty] | 5082 | 5100 | [8 empty] | 5 | 50
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | 2025-09-29 | [7 empty] | 5100 | 5117 | [8 empty] | 10 | 40
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | 2025-09-30 | [7 empty] | 5117 | 5133 | [8 empty] | 5 | 50
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | 2025-10-01 | [7 empty] | 5133 | 5148 | [8 empty] | 16 | 40
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | 2025-10-03 | [7 empty] | 5168 | 5182 | [8 empty] | 17 | 40
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | 2025-10-04 | [7 empty] | 5182 | 5192 | [8 empty] | 10 | 40
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | 2025-10-05 | [7 empty] | 5198 | 5215 | [8 empty] | 5 | 50
T3007 | KAMFINSA HILL | CCS | FACKSON | Copperbelt | 2025-09-16 | [7 empty] | 16280 | 16317 | [8 empty] | 76 | 200
T3007 | KAMFINSA HILL | CCS | FACKSON | Copperbelt | 2025-09-20 | [7 empty] | 16317 | 16355 | [8 empty] | 136 | 200
T3007 | KAMFINSA HILL | CCS | FACKSON | Copperbelt | 2025-10-02 | [7 empty] | 16355 | 16446 | [8 empty] | 10 | 200
T3265 | KITWE INDUSTRIES | CCS | JAULA | COPPERBELT | 2025-09-10 | [7 empty] | 3352 | 3439 | [8 empty] | 30 | 50
T3265 | KITWE INDUSTRIES | CCS | JAULA | COPPERBELT | 2025-09-12 | [7 empty] | 3470 | 3442 | [8 empty] | 70 | 100
T3265 | KITWE INDUSTRIES | CCS | JAULA | COPPERBELT | 2025-09-14 | [7 empty] | 3470 | 3512 | [8 empty] | 168 | 200
T3265 | KITWE INDUSTRIES | CCS | JAULA | COPPERBELT | 2025-09-18 | [7 empty] | 3512 | 3606 | [8 empty] | 114 | 200
T3265 | KITWE INDUSTRIES | CCS | JAULA | COPPERBELT | 2025-09-22 | [7 empty] | 3606 | 3710 | [8 empty] | 36 | 200
T3265 | KITWE INDUSTRIES | CCS | FACKSON | COPPERBELT | 2025-09-24 | [7 empty] | 3710 | 3748 | [8 empty] | 105 | 100
T3265 | KITWE INDUSTRIES | CCS | FACKSON | COPPERBELT | 2025-09-28 | [7 empty] | 3801 | 3848 | [8 empty] | 5 | 200
T3265 | KITWE INDUSTRIES | CCS | FACKSON | COPPERBELT | 2025-09-30 | [7 empty] | 3848 | 3814 | [8 empty] | 51 | 100
T3265 | KITWE INDUSTRIES | CCS | FACKSON | COPPERBELT | 2025-09-26 | [7 empty] | 3748 | 3801 | [8 empty] | 33 | 100
T3265 | KITWE INDUSTRIES | CCS | FACKSON | COPPERBELT | 2025-10-01 | [7 empty] | 3894 | 3922 | [8 empty] | 56 | 150
T3265 | KITWE INDUSTRIES | CCS | FACKSON | COPPERBELT | 2025-10-05 | [7 empty] | 3922 | 4001 | [8 empty] | 5 | 150
T3340 | KITWE TBN | CCS | JAULA | COPPERBELT | 2025-09-13 | [7 empty] | 3389 | 3389 | [8 empty] | 21 | 300
T3340 | KITWE TBN | CCS | JAULA | COPPERBELT | 2025-09-18 | [7 empty] | 3438 | 3438 | [8 empty] | 148 | 300
T3340 | KITWE TBN | CCS | JAULA | COPPERBELT | 2025-09-23 | [7 empty] | 3514 | 3514 | [8 empty] | 206 | 100
T3340 | KITWE TBN | CCS | JAULA | COPPERBELT | 2025-09-27 | [7 empty] | 3573 | 3573 | [8 empty] | 127 | 100
T3340 | KITWE TBN | CCS | FACKSON | COPPERBELT | 2025-09-29 | [7 empty] | 3646 | 3646 | [8 empty] | 16 | 150
T3340 | KITWE TBN | CCS | FACKSON | COPPERBELT | 2025-10-04 | [7 empty] | 3663 | 3663 | [8 empty] | 104 | 200
T3246 | RIVERSIDE EXTENTION | CCS | JAULA | Copperbelt | 2025-09-10 | [7 empty] | 4550 | 4576 | [8 empty] | 10 | 200
T3246 | RIVERSIDE EXTENTION | CCS | JAULA | Copperbelt | 2025-09-13 | [7 empty] | 4576 | 4637 | [8 empty] | 10 | 300
T3246 | RIVERSIDE EXTENTION | CCS | FACKSON | Copperbelt | 2025-09-17 | [7 empty] | 4637 | 4732 | [8 empty] | 5 | 200
T3246 | RIVERSIDE EXTENTION | CCS | JAULA | COPPERBELT | 2025-09-18 | [7 empty] | 4732 | 4750 | [8 empty] | 142 | 300
T3246 | RIVERSIDE EXTENTION | CCS | JAULA | COPPERBELT | 2025-09-23 | [7 empty] | 4750 | 4870 | [8 empty] | 76 | 150
T3246 | RIVERSIDE EXTENTION | CCS | JAULA | COPPERBELT | 2025-09-26 | [7 empty] | 4870 | 4939 | [8 empty] | 5 | 100
T3246 | RIVERSIDE EXTENTION | CCS | JAULA | COPPERBELT | 2025-09-27 | [7 empty] | 4939 | 4966 | [8 empty] | 16 | 150
T3246 | RIVERSIDE EXTENTION | CCS | JAULA | COPPERBELT | 2025-09-28 | [7 empty] | 4966 | 4989 | [8 empty] | 99 | 200
T3246 | RIVERSIDE EXTENTION | CCS | JAULA | COPPERBELT | 2025-09-30 | [7 empty] | 4989 | 5036 | [8 empty] | 126 | 100
T3246 | RIVERSIDE EXTENTION | CCS | JAULA | COPPERBELT | 2025-10-02 | [7 empty] | 5036 | 5082 | [8 empty] | 61 | 150
T3246 | RIVERSIDE EXTENTION | CCS | JAULA | COPPERBELT | 2025-10-05 | [7 empty] | 5082 | 5148 | [8 empty] | 5 | 100
T3340 | KITWE TBN | CCS | JAULA | COPPERBELT | [9 empty] | 3746 | [8 empty] | 25 | 200
T3007 | KAMFINSA HILL | CCS | FACKSON | Copperbelt | 2025-09-13 | [8 empty] | 16280 | [8 empty] | 10 | 200
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | [9 empty] | FAULTY | [9 empty] | 50
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | [9 empty] | 5168 | [9 empty] | 100
T3265 | KITWE INDUSTRIES | CCS | JAULA | COPPERBELT | [9 empty] | 3470 | [8 empty] | 76 | 200
T3223 | CHISOKONE | CCS | FACKSON | COPPERBELT | 2025-10-09 | [7 empty] | 145 | 197 | [8 empty] | 5 | 200
T3223 | CHISOKONE | CCS | SAMUEL | COPPERBELT | 2025-10-12 | [7 empty] | 197 | 233 | [8 empty] | 87 | 200
T3223 | CHISOKONE | CCS | FACKSON | COPPERBELT | 2025-10-15 | [7 empty] | 233 | 279 | [8 empty] | 82 | 300
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | 2025-10-14 | [8 empty] | 5320 | [8 empty] | 5 | 50
T3007 | KAMFINSA HILL | CCS | FACKSON | COPPERBELT | 2025-10-09 | [7 empty] | 16446 | 16501 | [8 empty] | 15 | 100
T3007 | KAMFINSA HILL |  | FACKSON | COPPERBELT | 2025-10-15 | [7 empty] | 16501 | 16532 | [8 empty] | 10 | 200
T3265 | KITWE INDUSTRIES | CCS | SAMUEL | COPPERBELT | 2025-10-11 | [7 empty] | 4047 | 4113 | [8 empty] | 79 | 250
T3265 | KITWE INDUSTRIES | CCS | FACKSON | COPPERBELT | 2025-10-14 | [7 empty] | 4113 | 4188 | [8 empty] | 65 | 250
T3265 | KITWE INDUSTRIES | CCS | FACKSON | COPPERBELT | 2025-10-08 | [8 empty] | 4047 | [8 empty] | 10 | 300
T3246 | RIVERSIDE EXTENTION | CCS | JAULA | COPPERBELT | 2025-10-05 | [7 empty] | 5212 | 5312 | [8 empty] | 21 | 300
T3340 | KITWE TBN | CCS | FACKSON | COPPERBELT | 2025-10-09 | [7 empty] | 3746 | 3822 | [8 empty] | 5 | 200
T3340 | KITWE TBN | CCS | SAMUEL | COPPERBELT | 2025-10-12 | [7 empty] | 3822 | 3853 | [8 empty] | 118 | 250
T3246 | RIVERSIDE EXTENTION | CCS | JAULA | COPPERBELT | 2025-10-09 | [7 empty] | 5148 | 5176 | [8 empty] | 5 | 150
T3246 | RIVERSIDE EXTENTION | CCS | JAULA | COPPERBELT | 2025-10-10 | [7 empty] | 5176 | 5192 | [8 empty] | 103 | 300
T3246 | RIVERSIDE EXTENTION | CCS | JAULA | COPPERBELT | 2025-10-14 | [8 empty] | 5312 | [8 empty] | 21 | 300
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | 2025-10-16 | [7 empty] | 5320 | 5349 | [8 empty] | 5 | 50
T3265 | KITWE INDUSTRIES | CCS | FACKSON | COPPERBELT | 2025-10-17 | [7 empty] | 4188 | 4261 | [8 empty] | 62 | 300
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | 2025-10-17 | [7 empty] | 5349 | 5363 | [8 empty] | 18 | 50
T3223 | CHISOKONE | CCS | FACKSON | COPPERBELT | 2025-10-19 | [7 empty] | 279 | 332 | [8 empty] | 149 | 300
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | 2025-10-18 | [7 empty] | 5363 | 5385 | [8 empty] | 5 | 50
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | 2025-10-19 | [7 empty] | 5385 | 5402 | [8 empty] | 9 | 50
T3007 | KAMFINSA HILL | CCS | FACKSON | COPPERBELT | 2025-10-19 | [7 empty] | 16532 | 16579 | [8 empty] | 41 | 100
T3246 | RIVERSIDE EXTENTION | CCS | JAULA | COPPERBELT | 2025-10-19 | [7 empty] | 5312 | 5419 | [8 empty] | 5 | 200
T3340 | KITWE TBN | CCS | FACKSON | COPPERBELT | 2025-10-20 | [7 empty] | 3853 | 3963 | [8 empty] | 12 | 200
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | 2025-10-17 | [7 empty] | 5402 | 5416 | [8 empty] | 21 | 30
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | 2025-10-22 | [7 empty] | 5416 | 5445 | [8 empty] | 5 | 50
T3246 | RIVERSIDE EXTENTION | CCS | SAMUEL | COPPERBELT | 2025-10-22 | [7 empty] | 5419 | 5484 | [8 empty] | 5 | 100
T3265 | KITWE INDUSTRIES | CCS | JAULA | COPPERBELT | 2025-10-22 | [7 empty] | 4261 | 4382 | [8 empty] | 17 | 100
T3246 | RIVERSIDE EXTENTION | CCS | JAULA | COPPERBELT | 2025-10-23 | [7 empty] | 5484 | 5512 | [8 empty] | 5 | 100
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | 2025-10-24 | [7 empty] | 5445 | 5468 | [8 empty] | 5 | 50
T3007 | KAMFINSA HILL |  | FACKSON | COPPERBELT | 2025-10-24 | [7 empty] | 16579 | 16617 | [8 empty] | 10 | 200
T3246 | RIVERSIDE EXTENTION | CCS | JAULA | COPPERBELT | 2025-10-25 | [7 empty] | 5512 | 5537 | [8 empty] | 12 | 200
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | 2025-10-25 | [7 empty] | 5468 | 5488 | [8 empty] | 5 | 50
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | 2025-10-25 | [7 empty] | 5488 | 5506 | [8 empty] | 5 | 50
T3223 | CHACHACHA |  | FACKSON | COPPERBELT | 2025-10-26 | [7 empty] | 1635 | 1737 | [8 empty] | 52 | 300
T3223 | CHISOKONE | CCS | FACKSON | COPPERBELT | 2025-10-26 | [7 empty] | 332 | 413 | [8 empty] | 117 | 300
T3340 | KITWE TBN | CCS | FACKSON | COPPERBELT | 2025-10-25 | [7 empty] | 3963 | 4024 | [8 empty] | 29 | 100
T3265 | KITWE INDUSTRIES | CCS | JAULA | COPPERBELT | 2025-10-27 | [7 empty] | 4024 | 4061 | [8 empty] | 10 | 200
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | 2025-10-27 | [7 empty] | 5506 | 5525 | [8 empty] | 5 | 50
T3246 | RIVERSIDE EXTENTION | CCS | JAULA | COPPERBELT | 2025-10-27 | [7 empty] | 5537 | 5589 | [8 empty] | 30 | 300
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | 2025-10-27 | [7 empty] | 5525 | 5542 | [8 empty] | 5 | 50
T3007 | KAMFINSA HILL | CCS | FACKSON | COPPERBELT | 2025-10-29 | [7 empty] | 16617 | 16653 | [8 empty] | 78 | 200
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | 2025-10-29 | [7 empty] | 5542 | 5565 | [8 empty] | 5 | 50
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | 2025-10-30 | [7 empty] | 5565 | 5819 | [8 empty] | 16 | 40
T3246 | RIVERSIDE EXTENTION | CCS | JAULA | COPPERBELT | 2025-10-30 | [7 empty] | 5589 | 5661 | [8 empty] | 92 | 300
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | 2025-10-31 | [7 empty] | 5565 | 5578 | [8 empty] | 16 | 40
T3265 | KITWE INDUSTRIES | CCS | FACKSON | COPPERBELT | 2025-10-31 | [7 empty] | 4415 | 4491 | [8 empty] | 21 | 300
T3265 | KITWE INDUSTRIES | CCS | FACKSON | COPPERBELT | 2025-10-31 | [7 empty] | 4061 | 4105 | [8 empty] | 57 | 300
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | 2025-11-03 | [7 empty] | 5607 | 5629 | [8 empty] | 5 | 50
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | 2025-11-03 | [7 empty] | 5629 | 5648 | [8 empty] | 5 | 50
T3246 | RIVERSIDE EXTENTION | CCS | JAULA | COPPERBELT | 2025-11-04 | [7 empty] | 5661 | 5778 | [8 empty] | 5 | 200
T3007 | KAMFINSA HILL | CCS | FACKSON | COPPERBELT | 2025-11-04 | [7 empty] | 16653 | 16715 | [8 empty] | 33 | 100
T3246 | RIVERSIDE EXTENTION | CCS | JAULA | COPPERBELT | 2025-11-07 | [7 empty] | 5778 | 5841 | [8 empty] | 5 | 200
T3265 | KITWE INDUSTRIES | CCS | FACKSON | COPPERBELT | 2025-11-07 | [7 empty] | 4491 | 4611 | [8 empty] | 5 | 350
T3423 | KABUSHI WEST | CCS | KASOMA | COPPERBELT | 2025-11-08 | [7 empty] | 5648 | 5697 | [8 empty] | 5 | 50
T3340 | KITWE TBN | CCS | FACKSON | COPPERBELT | 2025-11-11 | [7 empty] | 4243 | 4257 | [8 empty] | 5 | 250
T3265 | KITWE INDUSTRIES | CCS | FACKSON | COPPERBELT | 2025-11-12 | [7 empty] | 4611 | 4733 | [8 empty] | 25 | 300
T3223 | CHISOKONE | CCS | FACKSON | COPPERBELT11-12 | 2025-11-12 | [7 empty] | 413 | 524 | [8 empty] | 20 | 400
T3246 | RIVERSIDE EXTENTION | CCS | JAULA | COPPERBELT | 2025-11-13 | [7 empty] | 5864 | 5971 | [8 empty] | 5 | 200
T3246 | RIVERSIDE EXTENTION | CCS | JAULA | COPPERBELT | 2025-11-14 | [7 empty] | 5971 | 6011 | [8 empty] | 54 | 100
T3340 | KITWE TBN | CCS | FACKSON | COPPERBELT | 2025-11-15 | [7 empty] | 4257 | 4290 | [8 empty] | 143 | 200
T3007 | KAMFINSA HILL | CCS | FACKSON | COPPERBELT11-16 | 2025-11-16 | [7 empty] | 16715 | 16748 | [8 empty] | 10 | 150
T3423 | KABUSHI WEST | CCS | ROYD | COPPERBELT | 2025-11-16 | [8 empty] | 5779 | [8 empty] | 10 | 50
T3246 | RIVERSIDE EXTENTION | CCS | JAULA | COPPERBELT | 2025-11-17 | [7 empty] | 6011 | 6056 | [8 empty] | 5 | 50
T3265 | KITWE INDUSTRIES | CCS | FACKSON | COPPERBELT | 2025-11-17 | [7 empty] | 4733 | 4835 | [8 empty] | 5 | 25